## Control Dependencies
ID | Layer | Kinetics dependency / normalized need | Kinetics source point / register | How Kinetics controller uses it | New source | Elecod / Lineage mapping | Function / access | Mapping class | Required implementation change | Commissioning / vendor validation | Source basis
B01 | BMS | Emergency-stop blocker | external_fault_state @0x1001 bit6 | Hard blocker before energisation and during runtime | Lineage System Alarm | Emergency stop, Unit 1, discrete input 1 | FC02 RO | DIRECT | Map to normalized bms.emergency_stop. No architectural change. | Verify active polarity on hardware. | Kinetics bms_pcs_control.py; Lineage System Alarm
B02 | BMS | System / critical fault blocker | 0x1004, 0x1007, 0x100C, 0x100D + rack critical words | Any documented detailed critical fault blocks start/charge/discharge | Lineage System + Rack Alarm | Battery system state reg 1 + Rack Alarm FC02 points, especially BMS fault 73, comm faults 66/67, acquisition faults 68-70, contactor faults 78-83, pre-charge abnormal 114 | FC04 + FC02 RO | ADAPT | Replace Kinetics packed fault words with Lineage discrete-alarm aggregation and severity policy. | Freeze which Lineage warning/alarm/protection points are hard blockers vs derating only. | Kinetics control code; Lineage System Data/Rack Alarm
B03 | BMS | Charge prohibited | system_full bit + selected rack current limit | Blocks charge when critical fault or selected rack charge limit unavailable | Lineage Rack Data | Rack state reg 1 (NoChg) + max rack charge power reg 111 + max charge current reg 115 | FC04 RO FLOAT/U16 | DIRECT+BETTER | Use explicit Lineage NoChg state and direct kW/A limits instead of calculating power from V*I only. | Confirm whether Warn state still permits charge; confirm zero limit semantics. | Lineage Rack Data
B04 | BMS | Discharge prohibited | system_empty bit + selected rack current limit | Blocks discharge when critical fault or selected rack discharge limit unavailable | Lineage Rack Data | Rack state reg 1 (NoDchg) + max rack discharge power reg 113 + max discharge current reg 117 | FC04 RO FLOAT/U16 | DIRECT+BETTER | Use explicit NoDchg and direct kW/A limits. | Confirm Warn state behavior and zero limit semantics. | Lineage Rack Data
B05 | BMS | Rack voltage | vrack @561, 0.1 V | Readiness voltage window and BMS power-limit calculation | Lineage Rack Data | Rack total voltage reg 51, FLOAT, V | FC04 RO | DIRECT | Driver maps FLOAT to normalized rack_voltage_v. | Confirm FLOAT byte/word order and address base. | Lineage Rack Data
B06 | BMS | Rack charge current limit | irack_chg_limit @549, 0.1 A | Direction permission + dynamic power calculation | Lineage Rack Data | Max rack charging current reg 115 FLOAT A | FC04 RO | DIRECT | Map directly. Keep minimum current availability check. | Confirm current limit always non-negative. | Lineage Rack Data
B07 | BMS | Rack discharge current limit | irack_dsg_limit @550, 0.1 A | Direction permission + dynamic power calculation | Lineage Rack Data | Max rack discharging current reg 117 FLOAT A | FC04 RO | DIRECT | Map directly. | Confirm current limit always non-negative. | Lineage Rack Data
B08 | BMS | Dynamic charge power limit | Derived V*I | Enforced in precheck and runtime monitor | Lineage Rack Data | Max rack charging power reg 111 FLOAT kW (system-level alternative reg 95) | FC04 RO | DIRECT+BETTER | Use direct rack kW limit as pair limit; retain system-level 95 as plant ceiling/cross-check. | Confirm rack limit is authoritative for each pair. | Lineage System Data/Rack Data
B09 | BMS | Dynamic discharge power limit | Derived V*I | Enforced in precheck and runtime monitor | Lineage Rack Data | Max rack discharging power reg 113 FLOAT kW (system-level alternative reg 97) | FC04 RO | DIRECT+BETTER | Use direct rack kW limit; system-level 97 as plant ceiling/cross-check. | Confirm rack limit is authoritative for each pair. | Lineage System Data/Rack Data
B10 | BMS | Positive main contactor feedback | contactor_state bit0 | Required ready/start/runtime interlock | Lineage Rack Data | Digital input 1 / reg 18 = Positive DC contactor state feedback | FC04 RO U16 | DIRECT | Normalize positive_contactor_closed. | Verify polarity: workbook says 1 close / 0 open. | Lineage Rack Data row 18
B11 | BMS | Negative main contactor feedback | contactor_state bit2 | Required ready/start/runtime interlock | Lineage Rack Data | Digital input 2 / reg 19 = Negative DC contactor state feedback | FC04 RO U16 | DIRECT | Normalize negative_contactor_closed. | Verify polarity on hardware. | Lineage Rack Data row 19
B12 | BMS | MCB / fuse feedback | Not a primary Kinetics pair-control input | Additional safety diagnostics | Lineage Rack Data | Reg 20 MCB state feedback; reg 21 Fuse feedback | FC04 RO U16 | NEW | Add to normalized rack diagnostics and alarm/UI. Optionally make MCB/fuse unsafe states blockers after commissioning. | Confirm normal polarity and whether open is expected during standby. | Lineage Rack Data
B13 | BMS | Positive/negative insulation | ir_pos @568; ir_neg @569 | Observed before precharge; available for diagnostics | Lineage Rack Data | Positive insulation reg 61 FLOAT MOhm; negative insulation reg 63 FLOAT MOhm | FC04 RO | DIRECT | Convert units to common normalized unit (prefer kohm internally or expose MOhm explicitly). | Confirm acceptable thresholds with battery vendor; protocol provides measurements but no acceptance threshold. | Lineage Rack Data
B14 | BMS | Total insulation / insulation command | ir + start_insulation_sampleing | Kinetics retained API; command disabled after vendor said BMS automatic | Lineage | No total IR command/state; only positive/negative IR and alarm/protection points | RO only for measurements | NO DIRECT COMMAND | Preserve API for compatibility but return capability=automatic/not_supported for start-insulation; verify-insulation remains read-only. | None for command; threshold still vendor-defined. | Kinetics source; Lineage Rack Data/Rack Alarm
B15 | BMS | Precharge command | auto_onnected / start_pre_chg_operate | Automatic startup explicitly commands BMS precharge/connect | Lineage | No normal EMS precharge/connect command documented. Only forced + and - contactor writes; no precharge-contactor command. | Holding writes exist only for main contactors; write FC unspecified | GAP | Introduce battery.prepare_for_operation() capability. For Lineage default to observe/handshake mode; do NOT emulate precharge by forcing main contactors. | BLOCKER: vendor must define who initiates precharge/contactor close (BMS automatic, PCS-BMS handshake, or EMS sequence). | Lineage Setting + Rack Alarm
B16 | BMS | Precharge state = success | pre_charge_state @24 == 3 | Required before PCS start | Lineage | No direct precharge-state register. Available evidence: main contactors regs 18/19, rack state reg 1/2, pre-charge abnormal/fault points 80/83/114, rack voltage | FC04/FC02 RO | DERIVED / GAP | Create normalized battery_ready_for_pcs only after vendor-approved rule. Likely contactors closed + no precharge fault + voltage valid, but source does not define this equivalence. | BLOCKER: vendor confirmation required. | Lineage Rack Data/Rack Alarm
B17 | BMS | Rack enable bitmap | rack_enable_state_l16 @0x102A | Diagnostics / rack enabled feedback | Lineage System Data | Operate-rack bitmap reg 4, Unit 1 | FC04 RO U16 | DIRECT | Map bit N to rack operating state. | Confirm bit order; workbook says bit0 rack1 ... bit15 rack16. | Lineage System Data
B18 | BMS | Rack run state | bcu_run_state @25 | Readiness / diagnostics | Lineage Rack Data | Rack state reg 1 + charge/discharge state reg 2 | FC04 RO U16 | DIRECT+BETTER | Normalize permission_state and operating_direction separately. | Confirm mapping of Open/Standby/Charge/Discharge and transition behavior. | Lineage Rack Data
B19 | BMS | BMS fault reset | Kinetics recovery pulse to BMS control point | Clears latched BMS fault from safe state | Lineage Setting | System Holding reg 11 = 1 “clean fault” | Holding RW; FC not stated | DIRECT SEMANTICS | Implement fault_reset() behind same internal confirmation and safe-state checks. | Confirm write function (FC06/FC16) and whether value auto-resets. | Lineage Setting
B20 | BMS | Open selected battery during safe-stop | BAU auto_onnected=disconnect | After zero power + PCS stopped, opens selected rack | Lineage Setting | Rack holding reg 1 positive contactor; reg 2 negative contactor; 2 = EMS forced open | Holding RW; FC not stated | PARTIAL / SAFETY GAP | Do not make forced-open normal path until vendor confirms sequencing and per-rack addressing. Preserve safe-stop: zero P -> stop PCS; battery disconnect step capability-gated. | BLOCKER for exact parity: confirm write FC, unit addressing for racks 1-4, forced-open sequence, precharge behavior. | Lineage Setting
B21 | BMS | Close/enable selected battery | BAU connect command | Used during startup before PCS start | Lineage Setting | Main contactor forced close value 1 exists, but no precharge contactor command and note says “EMS forced close (no alarm)” | Holding RW; FC not stated | NOT SAFE AS SUBSTITUTE | Keep disabled in production path. Only expose as internal commissioning capability after vendor approval. | BLOCKER: safe precharge sequence not specified. | Lineage Setting
B22 | BMS | Battery SOC/SOH | Available in Kinetics telemetry but not pair-control core | UI/history/analytics | Lineage System + Rack Data | System SOC 55, SOH 57; Rack SOC 55, SOH 57 FLOAT | FC04 RO | DIRECT | Add standardized system and rack telemetry. | Confirm FLOAT ordering. | Lineage System Data/Rack Data
P01 | PCS | PCS actual active power | grid_active_power @4365 | Zero-power verification, tracking, runtime monitor | Elecod PCS | Total active power reg 1060, INT16, 0.1 kW | FC03/04 RO | DIRECT | Map to normalized pcs_actual_power_kw. | Commission sign convention under charge/discharge. | Elecod protocol §4.2.1
P02 | PCS | PCS active-power command in kW | active_power_setpoint @0x1409, 0.1 kW | Charge/discharge setpoint and ramp | Elecod PCS | Total active power reg 3050, INT16, -1200..1200 = -120%..120% | FC06/16 RW | ADAPT | Expose same normalized set_active_power_kw(); driver converts kW <-> percent using configured/read rated power (e.g. model 215 kW, reg 3146 scale 0.1 kW). | Commission +P/-P direction and verify rated-power basis. | Elecod §4.5.1, §4.5.4
P03 | PCS | PCS battery/DC input voltage | battery_voltage @4354 | Verify BMS rack voltage is present at PCS input | Elecod PCS | DC voltage reg 1063, UINT16, 0.1 V | FC03/04 RO | DIRECT | Map to pcs_battery_voltage_v. | Confirm whether 1063 is battery terminal voltage in actual product topology. | Elecod §4.2.1
P04 | PCS | PCS DC bus voltage | dc_bus_voltage @4352 | Readiness window and input-vs-bus comparison | Elecod PCS | Busbar voltage reg 1066, UINT16, 0.1 V | FC03/04 RO | DIRECT | Map to pcs_dc_bus_voltage_v. | Confirm “Busbar voltage” is intended DC link/bus used for readiness. | Elecod §4.2.1
P05 | PCS | Operating state | operating_state @0x1200 bit-coded | Stopped/ready/fault state machine | Elecod PCS | Status word reg 2057: bit6 Run, bit7 Fault, bit10 Standby, bit11 Shutdown, bit12 EPO | FC03/04 RO | DERIVED | Implement Elecod-specific state decoder returning normalized STOPPED/STANDBY/RUNNING/FAULT/EPO instead of copying old numeric masks. | Validate state transitions during start/stop. | Elecod §4.4.1
P06 | PCS | Remote feedback | status_word_1 bit0 | Kinetics configure_pcs requires Remote feedback | Elecod PCS | No local/remote feedback register documented | — | CAPABILITY DIFFERENCE | Make remote-feedback check capability-based. For Elecod, successful Modbus control + command readback/status is used; do not invent remote bit. | Ask vendor whether local/remote control source exists elsewhere. | Elecod protocol: no documented local/remote point
P07 | PCS | Authorization feedback | status_word_1 bit1 | Diagnostics/readiness support | Elecod PCS | No equivalent documented | — | CAPABILITY DIFFERENCE | Do not require for Elecod; capability=false. | None unless vendor exposes private register. | Elecod protocol
P08 | PCS | DC breaker/relay closed feedback | status_word_2 bit6 + reg_1210 bit7 | Required ready/start/runtime interlock | Elecod PCS | 2057 bit2 DC Relay connected; bit0 DC Pre-Charge connected | FC03/04 RO | ADAPT | Normalize pcs_dc_path_ready from vendor-specific relay/precharge bits. Do not call it breaker in Elecod driver. | Validate which bit best represents safe DC path during run. | Elecod §4.4.1
P09 | PCS | DC soft-start fault | reg_121A bits2/3 | Abort startup / runtime safety | Elecod PCS | Alarm 2053 bit0 DC Precharge Fault; additional relay faults in 2053 bits2/3 are DC Relay short/open | FC03/04 RO | DIRECT+ADAPT | Map relevant Elecod precharge/DC relay faults to normalized pcs_dc_start_fault. | Confirm fault clearing behavior. | Elecod §4.3.4
P10 | PCS | PCS start/stop command | remote_on_off_command @0x1400; start FF00, stop 00FF | Start after battery ready; stop during safe-stop | Elecod PCS | 5050: FF00 Power On; 0000 Power Off | FC05 or FC06 per section; V2.7 history creates FC05 ambiguity | DIRECT SEMANTICS | Use FC06 initially in driver; vendor-specific stop value is 0000, not Kinetics 00FF. | Validate FC06 on hardware; clarify V2.7 FC05 wording. | Elecod §4.7 + revision history
P11 | PCS | Standby/shutdown command | No equivalent primary Kinetics write in final automatic path | Optional lifecycle state | Elecod PCS | 5051: FF00 Standby; 0000 Shutdown | FC05/06 | NEW | Add capability and API internally without changing existing endpoints. Useful for vendor-specific safe lifecycle. | Validate desired use in startup/shutdown sequence. | Elecod §4.7
P12 | PCS | Remote/local selection | remote_local_mode @0x1402 | configure_pcs writes Remote | Elecod PCS | No equivalent documented | — | NO DIRECT MATCH | Remove from generic core requirement; execute only if driver capability supports it. | Vendor clarification optional. | Elecod protocol
P13 | PCS | PQ product mode | product_run_mode @0x1406 = 1 | configure_pcs selects PQ | Elecod PCS | 3157=0 On-grid + 3159=0 PQ | FC06/16 RW | DIRECT VIA TWO POINTS | Elecod driver prepare_pq_mode() writes/validates vendor-specific mode points. | Confirm mode changes allowed while stopped and whether reboot/standby needed. | Elecod §4.5.1
P14 | PCS | Constant-power work mode | pq_work_mode @0x1407 = 0 | configure_pcs selects constant P | Elecod PCS | No separate constant-power selector needed/documented; active P command 3050 under PQ mode | — | SEMANTIC COLLAPSE | Generic prepare() should not require a separate work-mode register when capability absent. | Validate that 3050 is honored in PQ mode without further selector. | Elecod §4.5.1
P15 | PCS | Reactive power / PF control | Not core pair start sequence | Existing/future EMS functions | Elecod PCS | 3051 reactive P; 3052 PF; 3152 reactive mode | FC06/16 RW | NEW / DIRECT | Add normalized reactive/PF capabilities without altering pair active-power sequence. | Commission sign convention for kvar/PF if used. | Elecod §4.5.1
P16 | PCS | On-grid / off-grid mode | Kinetics product_run_mode has VSG/voltage-source options | Application extension | Elecod PCS | 3157 on/off-grid; 3159 on-grid PQ/MPPT/CV/VSG; 3160 off-grid VSG/VF | FC06/16 RW | DIRECT CAPABILITY | Expose generic grid_mode/control_mode capabilities. Keep transfer sequence separate from normal charge/discharge until validated. | Vendor must define safe transition / STS-contactor sequence. | Elecod §4.5.1
P17 | PCS | PCS/BMS/EMS communication faults | Kinetics status/fault words | Runtime safety / alarms | Elecod PCS | 2056 bit1 EMS comm fail, bit2 BMS comm fail, bit3 BMS fault; 2050-2055 other faults | FC03/04 RO | DIRECT+RICHER | Map to normalized alarms and hard blockers according to severity. | Define which alarm bits are hard-stop vs warning. | Elecod §4.3
P18 | PCS | Charge/discharge direction feedback | Inferred mainly from signed power in Kinetics | Verification / UI | Elecod PCS | 2057 bit5: 0 Discharging, 1 Charging | FC03/04 RO | NEW / DIRECT | Cross-check actual power sign with explicit direction bit during commissioning/runtime. | Validate bit behavior at zero power / standby. | Elecod §4.4.1
P19 | PCS | E-stop feedback | Fault words in Kinetics | Hard blocker | Elecod PCS | 2057 bit12 EPO | FC03/04 RO | DIRECT | Normalize as PCS EPO; combine with Lineage system E-stop in hard-blocker logic. | Verify active polarity. | Elecod §4.4.1

## Feature Parity
Feature | Kinetics baseline behavior | Elecod+Lineage feasibility | Status | Required adaptation | Blocking validation
4 logical PCS-BMS pairs | pair_1..pair_4 map one PCS to one rack | Same logical pairing is supported; transport/addressing becomes configuration | KEEP | Config maps Elecod PCS endpoint/unit to Lineage rack unit | Actual Elecod 4-PCS network topology
Read telemetry | Multi-rate BMS + PCS polling | Full PCS + system/rack/cell/auxiliary BMS telemetry available | KEEP + EXPAND | Generate new catalogs; add FC02 and FLOAT handling where needed | Lineage FLOAT word order/address base
Pair precheck | Voltage, contactors, precharge, faults, PCS readiness, dynamic BMS limit | Most checks available; precharge-success semantics not directly available | ADAPT | Vendor-neutral readiness interface with capability-specific checks | Lineage precharge/contactor ownership
Configure PCS | Stop, Remote, PQ, constant P, zero setpoint | Elecod: zero setpoint + on-grid/PQ; no Remote/local and no separate constant-P selector | ADAPT | Driver capability methods | Mode-write sequencing
Start battery / precharge | Explicit Kinetics BAU connect/precharge command and success state | No normal EMS precharge command/state documented | GAP | Observe vendor-managed precharge or PCS-BMS handshake; do not force main contactors as substitute | Vendor startup sequence
Start PCS | Write start after BMS readiness; verify DC path/soft-start | 5050 Power On + 2057 run/relay/precharge + faults | KEEP | Vendor-specific status decoder and values | FC06 validation and readiness bits
Charge/discharge setpoint | Signed kW, + discharge / - charge | 3050 signed percentage setpoint; sign strongly inferred but needs test | KEEP via adapter | kW<->percent conversion in driver | Sign and rated-power basis
Dynamic BMS limiting | Selected rack I limit -> derived kW; runtime enforcement | Direct rack P and I limits available | KEEP + IMPROVE | Use regs 111/113 and 115/117; system limits as plant ceiling | Limit semantics
Power ramp | 10 kW steps with interval | Can remain identical at normalized kW layer | KEEP | Driver converts each kW step to percent | PCS response/ramp behavior
Power tracking | Compare setpoint and actual kW | Actual 1060 + normalized command readback | KEEP | Convert 3050 readback to kW | Sign and tolerances
Runtime monitor | Faults, contactors, DC path, BMS limits, comm health | Equivalent/richer signals exist | KEEP | Replace Kinetics point set with normalized capabilities | Hard-blocker severity table
Safe stop | Zero P -> verify -> PCS stop -> BMS open -> verify contactors | Zero P and PCS stop are clear; BMS open command is only forced contactor override | PARTIAL | Capability-gate battery disconnect step | Vendor-approved rack disconnect sequence
Safe-stop-all | Independent safe stop each pair | Same once pair safe-stop is adapted | KEEP | No architecture change | Same battery-disconnect gap
BMS fault reset | Safe-state recovery pulse | Lineage fault reset holding reg 11 | KEEP | Lineage write implementation | Write FC and reset behavior
Alarms/history | Normalized alarms + SQLite lifecycle/history | Both protocols have extensive faults/alarms | KEEP + EXPAND | New alarm catalogs/severity mapping | Severity policy
Cell/rack details | Kinetics bulk arrays | Lineage offers cell voltage/temp/SOC/balance, pack V/temp | KEEP + EXPAND | Slow/bulk polling classes | FLOAT word order, temperature physical mapping
Environment/HVAC | Kinetics power/environment asset | Lineage has chiller, T/H, water, dehumidifier + FSS summary signals | EXPAND | Add normalized auxiliary assets under same GatewayService | Aux device Unit IDs starting 101 allocation
REST/WebSocket/History APIs | Existing stable API surface | Can remain stable; new fields/assets additive | KEEP | Preserve route contracts | Frontend schema regression testing
Security/write gates | Internal role + explicit confirmation + write-enable gates | Independent of vendor | KEEP EXACT | No device-specific change | None
Storage/audit/exports | SQLite WAL, telemetry, alarms, commands, events, CSV | Independent of vendor | KEEP EXACT | No device-specific change | None

## Validation Gaps
Priority | Open item | Why it matters | Source-supported fact | What must be confirmed | Code strategy until confirmed
P0 | Lineage precharge / main-contactor ownership | Exact automatic startup and battery disconnect parity depends on it | EMS protocol has contactor feedback and forced main-contactor writes, but no normal precharge command/state | Does BMS auto-precharge? Does Elecod PCS request it over direct BMS link? Is there another Lineage command/protocol? | Keep battery.prepare_for_operation() capability unresolved; do not force-close in automatic production flow.
P0 | Lineage FLOAT word/byte order | System/rack/cell telemetry is mostly FLOAT | Workbook states FLOAT spans 2 registers but does not specify word order | ABCD/CDAB/BADC/DCBA and address-base behavior | Make word_order configurable; commission with known SOC/voltage.
P0 | Lineage rack contactor write semantics | Safe-stop battery opening depends on it | Holding regs 1/2 at “Modbus address 2” support 0 auto,1 forced close,2 forced open | Whether same map applies to rack units 2..5/17; write FC; safe order; precharge impact | Keep forced contactor control internal/disabled by default.
P0 | Elecod active-power sign | Charge/discharge correctness | Charging P-U limits are negative and discharge P-U limits positive, strongly implying -charge/+discharge | Confirm low-power +/− command behavior | Commission at small setpoints before enabling full automatic mode.
P0 | Elecod 5050 write function | Start/stop command must be reliable | Section 4.7 says FC05 or FC06, while V2.7 revision notes FC05 removed from remote adjustment | Vendor-recommended FC for 5050/5051 on shipped firmware | Implement FC06 first, capability-configurable.
P1 | Elecod rated-power basis for 3050 conversion | 3050 is percentage, core API is kW | 3050 is ±120%; model spec says 215 kW; reg 3146 reports rated power configuration | Whether use 3146, 3165 authorized capacity, or fixed nameplate for conversion | Configure rated_kw and cross-check 3146 at startup.
P1 | Elecod DC voltage semantics | Readiness compares BMS rack voltage with PCS input/DC bus | 1063 is “DC voltage”; 1066 is “Busbar voltage” | Which is battery terminal and which is internal DC link on Monet hardware | Map provisionally but keep role configurable until commissioning.
P1 | Lineage current sign | Telemetry/history and direction cross-check | System/rack current is FLOAT A; sign convention not stated | Positive charge or discharge | Use rack operating state reg2 to validate sign during commissioning.
P1 | Lineage warning/alarm/protection severity policy | Runtime hard blockers must be correct | Rack Alarm exposes 115 discrete warning/alarm/protection/fault points | Which warning/alarm levels permit continued operation/derating vs require stop | Catalog severity map configurable; protections/faults hard-block by default only after vendor review.
P1 | Auxiliary device unit-ID allocation | Chiller/T&H/water/dehumidifier polling endpoints | Workbook says Modbus addresses starting from 101, but no full per-device allocation table | Exact Unit IDs and count at site | Make endpoint list configuration-driven.
P2 | Cell temperature physical mapping | Detailed UI/analytics | Workbook has separate “actually” and “show” mappings and many reserved rows | Final sensor-to-cell mapping | Expose raw channel index first; add physical mapping config later.
P2 | On-grid/off-grid transition sequence | Future grid-forming feature safety | 3157/3159/3160 provide modes but protocol does not define full transfer sequencing | Required stop/standby/STS/contactor timing | Keep grid-mode control capability disabled until site sequence is validated.

## Architecture Freeze
Frozen layer | Baseline module(s) | Freeze decision | Extension rule
Configuration | app/core/config.py + /etc config | Keep config-driven assets, pairs, polling, safety thresholds | Add vendor-specific endpoint/capability fields; do not hard-code site topology
Protocol catalog | app/core/catalog.py + generated_protocols | Keep protocol data separate from drivers | Generate lineage_bms_catalog.json and elecod_pcs_catalog.json
Transport | app/protocols/* | Keep Modbus TCP/RTU planner/codec abstraction | Extend FC02/discrete handling and per-protocol FLOAT word order if required
Asset drivers | app/assets/* | Generalize to vendor-capability adapters | Kinetics, Lineage, Elecod and future vendors implement same normalized methods
Gateway service | app/services/gateway_service.py | Keep caching, polling, asset aggregation, telemetry/history feed | Add new asset classes without rewriting core service
Pair controller | app/services/bms_pcs_control.py | Keep state machine, write gates, ramp, monitor, safe stop | Remove direct vendor register assumptions into driver capabilities
Alarm engine | app/services/alarm_engine.py | Keep normalized alarm lifecycle | Catalog supplies severity/bit mappings per vendor
Storage | app/storage/sqlite_store.py | Keep WAL/history/audit/events/retention/export | Additive schema only if new asset metadata needs it
API | app/api/routes.py | Preserve existing endpoints/contracts wherever meaningful | Additive fields/endpoints; old routes remain compatible
Security | app/security/auth.py + confirmation gates | Keep exact role/write/confirmation model | No vendor-specific bypass
Deployment | systemd + deployment scripts | Keep single gateway service pattern | Rename/configure product identity only after platform freeze
Tests | tests/* | Keep feature-parity regression suite | Add vendor contract tests, simulated registers, commissioning fixtures

## Asset Coverage
Asset class | Protocol source | Telemetry | Control | Notes
Elecod PCS | Elecod Modbus V2.7.0 | AC/DC V/I/P, frequency, PF, temperatures, efficiency, status, faults | Start/stop, standby/shutdown, P/Q/PF, grid modes, config | Primary power-conversion asset
Lineage BAMS/System | Lineage System Data/Alarm | System state, SOC/SOH, total V/I, system limits, rack bitmap, FSS/aux status | Fault reset, RTC; DC combiner delay | Top-level battery/container summary
Lineage Battery Rack | Lineage Rack Data/Alarm | Rack V/I/SOC/SOH, limits, IR, contactors, alarms | Forced main contactor overrides only; use cautiously | One rack paired to one PCS logically
Battery cells | Lineage Cell Volt/Temp/SOC/Balance | Cell V, T, SOC, balancing | None | Bulk/slow polling
Battery packs | Lineage Pack Volt/Temp | Pack V and pole temperatures | None | 8 populated pack channels in current map
Chiller | Lineage Chiller | State, mode, pump, water T/P, ambient, faults | FC06 control/setpoints | Auxiliary asset
Temp/Humidity | Lineage Temp&Humidity | Comm, alarm, indoor T/RH | No control documented | Auxiliary sensor
Water sensor | Lineage Water sensor | Comm + water alarm | No control documented | Auxiliary safety sensor
Dehumidifier | Lineage Dehumidification | Comm, run, alarm, indoor T/RH, setpoint feedback | Write behavior not fully inspected/defined in current source excerpt | Auxiliary asset
Fire & Safety summary | Lineage System Data/Alarm | FSS warn/alarm/malfunction, Fire start/fault, gas alarm/fault, aerosol feedback | No full fire-controller control protocol | Logical/partial FSS asset via BMS
External PCC/Grid meter | Not in provided protocols | None | None | Separate meter protocol still required for true site import/export/zero-export control