## Northbound Protocol EN
Channel Name | Port | Device ID | Register Address | Register Count | Group No. | Entity Name | Point Name | Point Type | Unit | Description | Writable (0:No, 1:Yes) | Coefficient
Unity | 502 | 1 | 0 | 2 | 0 | EMS System Parameters | Available Count | Float |  |  | 1 | 1
Unity | 502 | 1 | 2 | 2 | 0 | EMS System Parameters | Slave Available Count | Float |  |  | 1 | 1
Unity | 502 | 1 | 4 | 2 | 0 | EMS System Parameters | Remote Mode | Float |  | 0,Local;1,Remote | 1 | 1
Unity | 502 | 1 | 6 | 2 | 0 | EMS System Parameters | Master/Slave Mode | Float |  | 0,Slave;1,Master | 1 | 1
Unity | 502 | 1 | 8 | 2 | 0 | EMS System Parameters | Slave Count | Float |  |  | 1 | 1
Unity | 502 | 1 | 10 | 2 | 0 | EMS System Parameters | Manual/Auto Mode | Float |  | 0,Manual;1,Auto | 1 | 1
Unity | 502 | 1 | 12 | 2 | 0 | EMS System Parameters | Manual Mode Control | Float |  | 1,Shutdown;2,Standby;3,Charge;4,Discharge | 1 | 1
Unity | 502 | 1 | 14 | 2 | 0 | EMS System Parameters | Auto Mode Control | Float |  | 1,Shutdown;2,Standby;3,Charge;4,Discharge | 1 | 1
Unity | 502 | 1 | 16 | 2 | 0 | EMS System Parameters | Master Control Mode | Float |  | 1,Shutdown;2,Standby;3,Charge;4,Discharge | 1 | 1
Unity | 502 | 1 | 18 | 2 | 0 | EMS System Parameters | Remote Control Mode | Float |  | 1,Shutdown;2,Standby;3,Charge;4,Discharge | 1 | 1
Unity | 502 | 1 | 20 | 2 | 0 | EMS System Parameters | Charge/Discharge Control Mode | Float |  | 1,Shutdown;2,Standby;3,Charge;4,Discharge | 1 | 1
Unity | 502 | 1 | 22 | 2 | 0 | EMS System Parameters | Power On Command | Float |  | 0,Stop;1,Power On | 1 | 1
Unity | 502 | 1 | 24 | 2 | 0 | EMS System Parameters | Manual Power On | Float |  | 0,Stop;1,Power On | 1 | 1
Unity | 502 | 1 | 26 | 2 | 0 | EMS System Parameters | Auto Power On | Float |  | 0,Stop;1,Power On | 1 | 1
Unity | 502 | 1 | 28 | 2 | 0 | EMS System Parameters | PCS Power On/Off Control | Float |  | 0,Stop;1,Power On | 1 | 1
Unity | 502 | 1 | 30 | 2 | 0 | EMS System Parameters | Master PCS Power On/Off Control | Float |  | 0,Stop;1,Power On | 1 | 1
Unity | 502 | 1 | 32 | 2 | 0 | EMS System Parameters | BMS Power On/Off Control | Float |  | 0,Stop;1,Power On | 1 | 1
Unity | 502 | 1 | 34 | 2 | 0 | EMS System Parameters | PCS Status | Float |  |  | 1 | 1
Unity | 502 | 1 | 36 | 2 | 0 | EMS System Parameters | Slave PCS Running Count | Float |  |  | 1 | 1
Unity | 502 | 1 | 38 | 2 | 0 | EMS System Parameters | BMS Status | Float |  | 0,Initializing;1,Self-Test;3,Power On;4,Power-On Complete;5,Charge Disabled;6,Discharge Disabled;7,Standby;8,Fault Power-Off;9,Fault Power-Off Cleared;10,Test Mode | 1 | 1
Unity | 502 | 1 | 40 | 2 | 0 | EMS System Parameters | PCS Running Status | Float |  | 0,Shutdown;1,Self-Test;2,Running;4,Fault;7,Standby | 1 | 1
Unity | 502 | 1 | 42 | 2 | 0 | EMS System Parameters | Manual Charge Value Setting | Float | kW |  | 1 | 1
Unity | 502 | 1 | 44 | 2 | 0 | EMS System Parameters | Manual Discharge Value Setting | Float | kW |  | 1 | 1
Unity | 502 | 1 | 46 | 2 | 0 | EMS System Parameters | Auto Charge Planned Value | Float | kW |  | 1 | 1
Unity | 502 | 1 | 48 | 2 | 0 | EMS System Parameters | Auto Discharge Planned Value | Float | kW |  | 1 | 1
Unity | 502 | 1 | 50 | 2 | 0 | EMS System Parameters | Master Charge Power Dispatch | Float | kW |  | 1 | 1
Unity | 502 | 1 | 52 | 2 | 0 | EMS System Parameters | Master Discharge Power Dispatch | Float | kW |  | 1 | 1
Unity | 502 | 1 | 54 | 2 | 0 | EMS System Parameters | Remote Power Dispatch | Float | kW |  | 1 | 1
Unity | 502 | 1 | 56 | 2 | 0 | EMS System Parameters | Charge Value Setting | Float | kW |  | 1 | 1
Unity | 502 | 1 | 58 | 2 | 0 | EMS System Parameters | Discharge Value Setting | Float | kW |  | 1 | 1
Unity | 502 | 1 | 60 | 2 | 0 | EMS System Parameters | Total Available Charge Power | Float | kW |  | 1 | 1
Unity | 502 | 1 | 62 | 2 | 0 | EMS System Parameters | Total Available Discharge Power | Float | kW |  | 1 | 1
Unity | 502 | 1 | 64 | 2 | 0 | EMS System Parameters | Slave Total Available Charge Power | Float | kW |  | 1 | 1
Unity | 502 | 1 | 66 | 2 | 0 | EMS System Parameters | Slave Total Available Discharge Power | Float | kW |  | 1 | 1
Unity | 502 | 1 | 68 | 2 | 0 | EMS System Parameters | Set Charge Percentage | Float | % |  | 1 | 1
Unity | 502 | 1 | 70 | 2 | 0 | EMS System Parameters | Set Discharge Percentage | Float | % |  | 1 | 1
Unity | 502 | 1 | 72 | 2 | 0 | EMS System Parameters | Load Power | Float | kW |  | 1 | 1
Unity | 502 | 1 | 74 | 2 | 0 | EMS System Parameters | Grid Meter Communication Status | Float |  | 0,Offline;1,Online | 1 | 1
Unity | 502 | 1 | 76 | 2 | 0 | EMS System Parameters | Grid Current Total Power | Float | kW |  | 1 | 1
Unity | 502 | 1 | 78 | 2 | 0 | EMS System Parameters | Metering Current Total Power | Float | kW |  | 1 | 1
Unity | 502 | 1 | 80 | 2 | 0 | EMS System Parameters | SOC | Float | % |  | 1 | 1
Unity | 502 | 1 | 82 | 2 | 0 | EMS System Parameters | Slave SOC | Float | % |  | 1 | 1
Unity | 502 | 1 | 84 | 2 | 0 | EMS System Parameters | SOC Limit Enable | Float |  | 0,Disabled;1,Enabled | 1 | 1
Unity | 502 | 1 | 86 | 2 | 0 | EMS System Parameters | Charge Cutoff SOC Setting | Float | % |  | 1 | 1
Unity | 502 | 1 | 88 | 2 | 0 | EMS System Parameters | Discharge Cutoff SOC Setting | Float | % |  | 1 | 1
Unity | 502 | 1 | 90 | 2 | 0 | EMS System Parameters | Master SOC Limit Enable | Float |  | 0,Disabled;1,Enabled | 1 | 1
Unity | 502 | 1 | 92 | 2 | 0 | EMS System Parameters | Master Charge Cutoff SOC Setting | Float | kW |  | 1 | 1
Unity | 502 | 1 | 94 | 2 | 0 | EMS System Parameters | Master Discharge Cutoff SOC Setting | Float | kW |  | 1 | 1
Unity | 502 | 1 | 96 | 2 | 0 | EMS System Parameters | Rate Limit Enable | Float |  | 0,Disabled;1,Enabled | 1 | 1
Unity | 502 | 1 | 98 | 2 | 0 | EMS System Parameters | Demand Enable | Float |  | 0,Disabled;1,Enabled | 1 | 1
Unity | 502 | 1 | 100 | 2 | 0 | EMS System Parameters | Anti-Reverse Flow Enable | Float |  | 0,Disabled;1,Enabled | 1 | 1
Unity | 502 | 1 | 102 | 2 | 0 | EMS System Parameters | Control Step | Float | kW |  | 1 | 1
Unity | 502 | 1 | 104 | 2 | 0 | EMS System Parameters | Control Cycle | Float | s |  | 1 | 1
Unity | 502 | 1 | 106 | 2 | 0 | EMS System Parameters | Demand | Float | kW |  | 1 | 1
Unity | 502 | 1 | 108 | 2 | 0 | EMS System Parameters | Demand Limit Percentage | Float | % |  | 1 | 1
Unity | 502 | 1 | 110 | 2 | 0 | EMS System Parameters | Anti-Reverse Flow Power Lower Limit Setting | Float | kW |  | 1 | 1
Unity | 502 | 1 | 112 | 2 | 0 | EMS System Parameters | Anti-Reverse Flow Power Upper Limit Setting | Float | kW |  | 1 | 1
Unity | 502 | 1 | 114 | 2 | 0 | EMS System Parameters | System Fault | Float |  |  | 1 | 1
Unity | 502 | 1 | 116 | 2 | 0 | EMS System Parameters | Master System Fault | Float |  |  | 1 | 1
Unity | 502 | 1 | 118 | 2 | 0 | EMS System Parameters | E-Stop | Float |  | 0,Normal;1,E-Stop | 1 | 1
Unity | 502 | 1 | 120 | 2 | 0 | EMS System Parameters | Master E-Stop | Float |  | 0,Normal;1,E-Stop | 1 | 1
Unity | 502 | 1 | 122 | 2 | 0 | EMS System Parameters | E-Stop Flag 1 | Float |  |  | 1 | 1
Unity | 502 | 1 | 124 | 2 | 0 | EMS System Parameters | E-Stop Flag 2 | Float |  |  | 1 | 1
Unity | 502 | 1 | 126 | 2 | 0 | EMS System Parameters | E-Stop Timer | Float |  |  | 1 | 1
Unity | 502 | 1 | 128 | 2 | 0 | EMS System Parameters | Flag | Float |  |  | 1 | 1
Unity | 502 | 1 | 130 | 2 | 0 | EMS System Parameters | Fire Protection Communication Status | Float |  | 0,Offline;1,Online | 1 | 1
Unity | 502 | 1 | 132 | 2 | 0 | EMS System Parameters | Fire Protection Offline | Float |  | 0,Normal;1,Offline | 1 | 1
Unity | 502 | 1 | 134 | 2 | 0 | EMS System Parameters | Fire Protection Alarm | Float |  | 0,No Fire Alarm;1,CO Fire Alarm;2,Temperature Fire Alarm;3,2+ Fire Alarms;4,Fire Extinguisher Activated | 1 | 1
Unity | 502 | 1 | 136 | 2 | 0 | EMS System Parameters | Fire Protection Fault | Float |  | 0,No Fault;1,Fire Extinguisher Activated;2,Sensor Fault;3,2+ Alarms | 1 | 1
Unity | 502 | 1 | 138 | 2 | 0 | EMS System Parameters | Fire Protection Spraying | Float |  | 0,Normal;1,Alarm | 1 | 1
Unity | 502 | 1 | 140 | 2 | 0 | EMS System Parameters | Fire Protection Status | Float |  | 0,Normal;1,Alarm | 1 | 1
Unity | 502 | 1 | 142 | 2 | 0 | EMS System Parameters | PPS Pulse | Float |  |  | 1 | 1
Unity | 502 | 1 | 144 | 2 | 0 | EMS System Parameters | PPS Pulse 1 | Float |  |  | 1 | 1
Unity | 502 | 1 | 146 | 2 | 0 | EMS System Parameters | Status | Float |  | 0,Standby;1,Discharge;2,Charge | 1 | 1
Unity | 502 | 1 | 148 | 2 | 0 | EMS System Parameters | Energy Storage Power | Float | kW |  | 1 | 1
Unity | 502 | 1 | 150 | 2 | 0 | EMS System Parameters | Slave Energy Storage Power | Float | kW |  | 1 | 1
Unity | 502 | 1 | 152 | 2 | 0 | EMS System Parameters | Manual On/Off-Grid Switching | Float |  | 0,On-Grid;1,Off-Grid | 1 | 1
Unity | 502 | 1 | 154 | 2 | 0 | EMS System Parameters | Reset | Float |  | 0,Normal;1,Reset | 1 | 1
Unity | 502 | 1 | 156 | 2 | 0 | EMS System Parameters | Running Indicator | Float |  | 0,Off;1,On | 1 | 1
Unity | 502 | 1 | 158 | 2 | 0 | EMS System Parameters | Fault Indicator | Float |  | 0,Off;1,On | 1 | 1
Unity | 502 | 1 | 160 | 2 | 0 | EMS System Parameters | PCS E-Stop Control | Float |  | 0,E-Stop;1,Normal | 1 | 1
Unity | 502 | 1 | 162 | 2 | 0 | EMS System Parameters | Circuit Breaker Control | Float |  | 0,Closed;1,Open | 1 | 1
Unity | 502 | 1 | 164 | 2 | 0 | EMS System Parameters | On/Off-Grid Switching | Float |  | 0,Completed;1,On-Grid;2,Off-Grid | 1 | 1
Unity | 502 | 1 | 166 | 2 | 0 | EMS System Parameters | Master On/Off-Grid Switching Dispatch | Float |  | 0,On-Grid;1,Off-Grid | 1 | 1
Unity | 502 | 1 | 168 | 2 | 0 | EMS System Parameters | Battery Pre-Charge Control | Float |  | 0,Completed;1,Power Off;2,Power On | 1 | 1
Unity | 502 | 1 | 170 | 2 | 0 | EMS System Parameters | Master Battery Pre-Charge Control Dispatch | Float |  | 0,Completed;1,Power Off;2,Power On | 1 | 1
Unity | 502 | 1 | 172 | 2 | 0 | EMS System Parameters | Master Communication Status | Float |  | 0,Offline;1,Online | 1 | 1
Unity | 502 | 1 | 174 | 2 | 0 | EMS System Parameters | Master Counter | Float |  |  | 1 | 1
Unity | 502 | 1 | 176 | 2 | 0 | EMS System Parameters | Off-Grid Shutdown SOC | Float | % |  | 1 | 1
Unity | 502 | 1 | 178 | 2 | 0 | EMS System Parameters | Master Off-Grid Shutdown SOC Dispatch | Float |  |  | 1 | 1
Unity | 502 | 1 | 180 | 2 | 0 | EMS System Parameters | PCS On/Off-Grid Status | Float |  | 0,Off-Grid;1,On-Grid | 1 | 1
Unity | 502 | 1 | 182 | 2 | 0 | EMS System Parameters | Off-Grid Power-On Timer | Float |  |  | 1 | 1
Unity | 502 | 1 | 184 | 2 | 0 | EMS System Parameters | Master Off-Grid Power-On Timer Dispatch | Float |  |  | 0 | 1
Unity | 502 | 1 | 186 | 2 | 0 | PCS1 | Rated Power | Float | kW |  | 0 | 1
Unity | 502 | 1 | 188 | 2 | 0 | PCS1 | Charge Power | Float | kW |  | 0 | 1
Unity | 502 | 1 | 190 | 2 | 0 | PCS1 | Discharge Power | Float | kW |  | 0 | 1
Unity | 502 | 1 | 192 | 2 | 0 | PCS1 | Charge/Discharge Power | Float | kW |  | 0 | 1
Unity | 502 | 1 | 194 | 2 | 0 | PCS1 | DC Power | Float | kW |  | 0 | 1
Unity | 502 | 1 | 196 | 2 | 0 | PCS1 | Available Charge Power | Float | kW |  | 0 | 1
Unity | 502 | 1 | 198 | 2 | 0 | PCS1 | Available Discharge Power | Float | kW |  | 0 | 1
Unity | 502 | 1 | 200 | 2 | 0 | PCS1 | Rate Limit Enable | Float |  | 0,Disabled;1,Enabled | 0 | 1
Unity | 502 | 1 | 202 | 2 | 0 | PCS1 | Equipment Available Charge Rate | Float |  |  | 0 | 1
Unity | 502 | 1 | 204 | 2 | 0 | PCS1 | Equipment Available Discharge Rate | Float |  |  | 0 | 1
Unity | 502 | 1 | 206 | 2 | 0 | PCS1 | BMS Available Charge Power | Float | kW |  | 0 | 1
Unity | 502 | 1 | 208 | 2 | 0 | PCS1 | BMS Available Discharge Power | Float | kW |  | 0 | 1
Unity | 502 | 1 | 210 | 2 | 0 | PCS1 | BMS Max Available Charge Current | Float | A |  | 0 | 1
Unity | 502 | 1 | 212 | 2 | 0 | PCS1 | BMS Max Available Discharge Current | Float | A |  | 0 | 1
Unity | 502 | 1 | 214 | 2 | 0 | PCS1 | BMS Total Voltage | Float | V |  | 0 | 1
Unity | 502 | 1 | 216 | 2 | 0 | PCS1 | Set Charge Percentage | Float | % |  | 0 | 1
Unity | 502 | 1 | 218 | 2 | 0 | PCS1 | Set Discharge Percentage | Float | % |  | 0 | 1
Unity | 502 | 1 | 220 | 2 | 0 | PCS1 | Charge/Discharge Control Mode | Float |  | 0,Not Configured;1,Shutdown;2,Standby;3,Charge;4,Discharge | 0 | 1
Unity | 502 | 1 | 222 | 2 | 0 | PCS1 | SOC | Float | % |  | 0 | 1
Unity | 502 | 1 | 224 | 2 | 0 | PCS1 | SOC Limit Enable | Float |  |  | 0 | 1
Unity | 502 | 1 | 226 | 2 | 0 | PCS1 | Charge Cutoff SOC Setting | Float | kW |  | 0 | 1
Unity | 502 | 1 | 228 | 2 | 0 | PCS1 | Discharge Cutoff SOC Setting | Float | kW |  | 0 | 1
Unity | 502 | 1 | 230 | 2 | 0 | PCS1 | Running Status | Float |  | 0,Shutdown;1,Self-Test;2,Running;4,Fault;7,Standby | 0 | 1
Unity | 502 | 1 | 232 | 2 | 0 | PCS1 | Fault Status | Float |  | 0,Normal;1,Fault | 0 | 1
Unity | 502 | 1 | 234 | 2 | 0 | PCS1 | On-Grid Status | Float |  | 0,Invalid;1,On-Grid | 0 | 1
Unity | 502 | 1 | 236 | 2 | 0 | PCS1 | Off-Grid Status | Float |  | 0,Invalid;1,Off-Grid | 0 | 1
Unity | 502 | 1 | 238 | 2 | 0 | PCS1 | Locked | Float |  | 0,Unlocked;1,Locked | 0 | 1
Unity | 502 | 1 | 240 | 2 | 0 | PCS1 | Fault Reset | Float |  | 0,Normal;1,Reset | 0 | 1
Unity | 502 | 1 | 242 | 2 | 0 | PCS1 | E-Stop | Float |  | 0,Normal;1,E-Stop | 0 | 1
Unity | 502 | 1 | 244 | 2 | 0 | PCS1 | Start/Stop Control | Float |  | 0,Stop;1,Start | 0 | 1
Unity | 502 | 1 | 246 | 2 | 0 | PCS1 | Power On Control | Float |  | 0,Invalid;1,Power On | 0 | 1
Unity | 502 | 1 | 248 | 2 | 0 | PCS1 | Shutdown Control | Float |  | 0,Invalid;1,Shutdown | 0 | 1
Unity | 502 | 1 | 250 | 2 | 0 | PCS1 | Auto Start/Stop Command | Float |  | 0,Stop;1,Start | 0 | 1
Unity | 502 | 1 | 252 | 2 | 0 | PCS1 | Open Failed | Float |  | 0,Normal;1,Open Failed | 0 | 1
Unity | 502 | 1 | 254 | 2 | 0 | PCS1 | Action Timeout Setting | Float | s |  | 0 | 1
Unity | 502 | 1 | 256 | 2 | 0 | PCS1 | Action Time | Float | s |  | 0 | 1
Unity | 502 | 1 | 258 | 2 | 0 | PCS1 | Offline Timeout Setting | Float | s |  | 0 | 1
Unity | 502 | 1 | 260 | 2 | 0 | PCS1 | Offline Time | Float | s |  | 0 | 1
Unity | 502 | 1 | 262 | 2 | 0 | PCS1 | Offline Status | Float |  |  | 0 | 1
Unity | 502 | 1 | 264 | 2 | 0 | PCS1 | Total Fault Status | Float |  | 0,Normal;1,Fault | 0 | 1
Unity | 502 | 1 | 266 | 2 | 0 | PCS1 | Time Reset | Float |  | 0,Normal;1,Reset | 0 | 1
Unity | 502 | 1 | 268 | 2 | 0 | PCS1 | Auto Available Status | Float |  | 0,Disabled;1,Available | 0 | 1
Unity | 502 | 1 | 270 | 2 | 0 | PCS1 | BMS Online Status | Float |  | 0,Offline;1,Online | 0 | 1
Unity | 502 | 1 | 272 | 2 | 0 | PCS1 | PCS Online Status | Float |  | 0,Offline;1,Online | 0 | 1
Unity | 502 | 1 | 274 | 2 | 0 | PCS1 | Liquid Cooling Online Status | Float |  | 0,Offline;1,Online | 0 | 1
Unity | 502 | 1 | 276 | 2 | 0 | PCS1 | Liquid Cooling Equipment Status | Float |  | 0,Shutdown;1,Self-Circulation;2,Standby;3,Cooling;4,Heating;5,Manual;6,Vacuuming;7,Fault Shutdown;8,Group Control Standby;9,Remote Shutdown;10,Auto Exhaust | 0 | 1
Unity | 502 | 1 | 278 | 2 | 0 | PCS1 | Fire Protection Status | Float |  | 0,Normal;1,Fire Protection Offline;2,Fire Protection Alarm | 0 | 1
Unity | 502 | 1 | 280 | 2 | 0 | PCS1 | Water Infiltration Alarm | Float |  | 0,Normal;1,Alarm | 0 | 1
Unity | 502 | 1 | 282 | 2 | 0 | PCS1 | PPS Pulse | Float |  |  | 0 | 1
Unity | 502 | 1 | 284 | 2 | 0 | PCS1 | On/Off-Grid Switching | Float |  | 0,On-Grid;1,Off-Grid | 0 | 1
Unity | 502 | 1 | 286 | 2 | 0 | PCS1 | On/Off-Grid Switching Flag | Float |  | 0,Completed;1,On-Grid;2,Off-Grid | 0 | 1
Unity | 502 | 1 | 288 | 2 | 0 | PCS1 | Battery Pre-Charge Control | Float |  | 0,Power Off;1,Power On | 0 | 1
Unity | 502 | 1 | 290 | 2 | 0 | PCS1 | Battery Pre-Charge Control Flag | Float |  | 0,Completed;1,Power Off;2,Power On | 0 | 1
Unity | 502 | 1 | 292 | 2 | 0 | PCS1 | Battery System Status | Float |  | 0,Normal;1,Charge Disabled;2,Discharge Disabled;3,Standby;4,Shutdown | 0 | 1
Unity | 502 | 1 | 294 | 2 | 0 | PCS1 | PCS Reset | Float |  | 0,Normal;1,Reset | 0 | 1
Unity | 502 | 1 | 296 | 2 | 0 | PCS1 | Off-Grid Shutdown SOC | Float |  |  | 0 | 1
Unity | 502 | 1 | 298 | 2 | 0 | PCS1 | System Abnormal | Float |  |  | 0 | 1
Unity | 502 | 1 | 300 | 2 | 0 | PCS1 | Off-Grid Power-On Timer | Float |  |  | 0 | 1
Unity | 502 | 1 | 302 | 2 | 0 | PCS1 | Off-Grid Power-On Timer Setting Value | Float |  |  | 0 | 1
Unity | 502 | 1 | 304 | 2 | 0 | PCS1 | Control Mode | Float |  | 0,Local;1,Remote | 0 | 1
Unity | 502 | 1 | 306 | 2 | 0 | PCS Communication Parameters 1 | Online Points | Float |  | 0,Offline;1,Online | 0 | 1
Unity | 502 | 1 | 308 | 2 | 0 | PCS Communication Parameters 1 | Fault Reset | Float |  | 0,Invalid;1,Reset | 0 | 1
Unity | 502 | 1 | 310 | 2 | 0 | PCS Communication Parameters 1 | Equipment Start | Float |  | 0,Invalid;1,Start | 0 | 1
Unity | 502 | 1 | 312 | 2 | 0 | PCS Communication Parameters 1 | Equipment Shutdown | Float |  | 0,Invalid;1,Shutdown | 0 | 1
Unity | 502 | 1 | 314 | 2 | 0 | PCS Communication Parameters 1 | Remote E-Stop | Float |  | 0,Invalid;1,E-Stop | 0 | 1
Unity | 502 | 1 | 316 | 2 | 0 | PCS Communication Parameters 1 | Cumulative Charge Energy Clear | Float |  | 0,Invalid;1,Clear | 0 | 1
Unity | 502 | 1 | 318 | 2 | 0 | PCS Communication Parameters 1 | Cumulative Discharge Energy Clear | Float |  | 0,Invalid;1,Clear | 0 | 1
Unity | 502 | 1 | 320 | 2 | 0 | PCS Communication Parameters 1 | Remote/Local Setting | Float |  | 0,Local;1,Remote | 0 | 1
Unity | 502 | 1 | 322 | 2 | 0 | PCS Communication Parameters 1 | Equipment Standby | Float |  | 0,Invalid;1,Standby | 0 | 1
Unity | 502 | 1 | 324 | 2 | 0 | PCS Communication Parameters 1 | Shutdown Status | Float |  | 0,Invalid;1,Shutdown | 0 | 1
Unity | 502 | 1 | 326 | 2 | 0 | PCS Communication Parameters 1 | Standby Status | Float |  | 0,Invalid;1,Standby | 0 | 1
Unity | 502 | 1 | 328 | 2 | 0 | PCS Communication Parameters 1 | Running Status | Float |  | 0,Invalid;1,Running | 0 | 1
Unity | 502 | 1 | 330 | 2 | 0 | PCS Communication Parameters 1 | Total Fault Status | Float |  | 0,Invalid;1,Fault | 0 | 1
Unity | 502 | 1 | 332 | 2 | 0 | PCS Communication Parameters 1 | Total Alarm Status | Float |  | 0,Invalid;1,Alarm | 0 | 1
Unity | 502 | 1 | 334 | 2 | 0 | PCS Communication Parameters 1 | Remote/Local Status | Float |  | 0,Local;1,Remote | 0 | 1
Unity | 502 | 1 | 336 | 2 | 0 | PCS Communication Parameters 1 | E-Stop Input Status | Float |  | 0,Invalid;1,E-Stop | 0 | 1
Unity | 502 | 1 | 338 | 2 | 0 | PCS Communication Parameters 1 | On-Grid Status | Float |  | 0,Invalid;1,On-Grid | 0 | 1
Unity | 502 | 1 | 340 | 2 | 0 | PCS Communication Parameters 1 | VF Off-Grid Status | Float |  | 0,Invalid;1,VF Off-Grid | 0 | 1
Unity | 502 | 1 | 342 | 2 | 0 | PCS Communication Parameters 1 | Overload Derating | Float |  | 0,Invalid;1,Overload Occurred | 0 | 1
Unity | 502 | 1 | 344 | 2 | 0 | PCS Communication Parameters 1 | BMS Dry Contact Input | Float |  | 0,Invalid;1,Fault Valid | 0 | 1
Unity | 502 | 1 | 346 | 2 | 0 | PCS Communication Parameters 1 | Phase A Voltage | Float | V |  | 0 | 1
Unity | 502 | 1 | 348 | 2 | 0 | PCS Communication Parameters 1 | Phase B Voltage | Float | V |  | 0 | 1
Unity | 502 | 1 | 350 | 2 | 0 | PCS Communication Parameters 1 | Phase C Voltage | Float | V |  | 0 | 1
Unity | 502 | 1 | 352 | 2 | 0 | PCS Communication Parameters 1 | Phase A Current | Float | A |  | 0 | 1
Unity | 502 | 1 | 354 | 2 | 0 | PCS Communication Parameters 1 | Phase B Current | Float | A |  | 0 | 1
Unity | 502 | 1 | 356 | 2 | 0 | PCS Communication Parameters 1 | Phase C Current | Float | A |  | 0 | 1
Unity | 502 | 1 | 358 | 2 | 0 | PCS Communication Parameters 1 | Grid Frequency | Float | Hz |  | 0 | 1
Unity | 502 | 1 | 360 | 2 | 0 | PCS Communication Parameters 1 | Phase A Active Power | Float | kW |  | 0 | 1
Unity | 502 | 1 | 362 | 2 | 0 | PCS Communication Parameters 1 | Phase B Active Power | Float | kW |  | 0 | 1
Unity | 502 | 1 | 364 | 2 | 0 | PCS Communication Parameters 1 | Phase C Active Power | Float | kW |  | 0 | 1
Unity | 502 | 1 | 366 | 2 | 0 | PCS Communication Parameters 1 | Total Active Power | Float | kW |  | 0 | 1
Unity | 502 | 1 | 368 | 2 | 0 | PCS Communication Parameters 1 | Phase A Reactive Power | Float | kVar |  | 0 | 1
Unity | 502 | 1 | 370 | 2 | 0 | PCS Communication Parameters 1 | Phase B Reactive Power | Float | kVar |  | 0 | 1
Unity | 502 | 1 | 372 | 2 | 0 | PCS Communication Parameters 1 | Phase C Reactive Power | Float | kVar |  | 0 | 1
Unity | 502 | 1 | 374 | 2 | 0 | PCS Communication Parameters 1 | Total Reactive Power | Float | kVar |  | 0 | 1
Unity | 502 | 1 | 376 | 2 | 0 | PCS Communication Parameters 1 | Phase A Apparent Power | Float | kVA |  | 0 | 1
Unity | 502 | 1 | 378 | 2 | 0 | PCS Communication Parameters 1 | Phase B Apparent Power | Float | kVA |  | 0 | 1
Unity | 502 | 1 | 380 | 2 | 0 | PCS Communication Parameters 1 | Phase C Apparent Power | Float | kVA |  | 0 | 1
Unity | 502 | 1 | 382 | 2 | 0 | PCS Communication Parameters 1 | Total Apparent Power | Float | kVA |  | 0 | 1
Unity | 502 | 1 | 384 | 2 | 0 | PCS Communication Parameters 1 | Phase A Power Factor | Float |  |  | 0 | 1
Unity | 502 | 1 | 386 | 2 | 0 | PCS Communication Parameters 1 | Phase B Power Factor | Float |  |  | 0 | 1
Unity | 502 | 1 | 388 | 2 | 0 | PCS Communication Parameters 1 | Phase C Power Factor | Float |  |  | 0 | 1
Unity | 502 | 1 | 390 | 2 | 0 | PCS Communication Parameters 1 | Total Power Factor | Float |  |  | 0 | 1
Unity | 502 | 1 | 392 | 2 | 0 | PCS Communication Parameters 1 | DC Power | Float | kW |  | 0 | 1
Unity | 502 | 1 | 394 | 2 | 0 | PCS Communication Parameters 1 | DC Voltage | Float | V |  | 0 | 1
Unity | 502 | 1 | 396 | 2 | 0 | PCS Communication Parameters 1 | DC Current | Float | A |  | 0 | 1
Unity | 502 | 1 | 398 | 2 | 0 | PCS Communication Parameters 1 | Heat Sink Temperature | Float | ℃ |  | 0 | 1
Unity | 502 | 1 | 400 | 2 | 0 | PCS Communication Parameters 1 | BMS Operating Status | Float |  |  | 0 | 1
Unity | 502 | 1 | 402 | 2 | 0 | PCS Communication Parameters 1 | PCS Running Status | Float |  | 0,Shutdown;1,Self-Test;2,Running;4,Fault;7,Standby | 0 | 1
Unity | 502 | 1 | 404 | 2 | 0 | PCS Communication Parameters 1 | AC Cumulative Charge Energy | Float | kWh |  | 0 | 1
Unity | 502 | 1 | 406 | 2 | 0 | PCS Communication Parameters 1 | AC Cumulative Discharge Energy | Float | kWh |  | 0 | 1
Unity | 502 | 1 | 408 | 2 | 0 | PCS Communication Parameters 1 | DC Cumulative Charge Energy | Float | kWh |  | 0 | 1
Unity | 502 | 1 | 410 | 2 | 0 | PCS Communication Parameters 1 | DC Cumulative Discharge Energy | Float | kWh |  | 0 | 1
Unity | 502 | 1 | 412 | 2 | 0 | PCS Communication Parameters 1 | PCS Communication Status Word | Float |  |  | 0 | 1
Unity | 502 | 1 | 414 | 2 | 0 | PCS Communication Parameters 1 | Second | Float |  |  | 0 | 1
Unity | 502 | 1 | 416 | 2 | 0 | PCS Communication Parameters 1 | Minute | Float |  |  | 0 | 1
Unity | 502 | 1 | 418 | 2 | 0 | PCS Communication Parameters 1 | Hour | Float |  |  | 0 | 1
Unity | 502 | 1 | 420 | 2 | 0 | PCS Communication Parameters 1 | Day | Float |  |  | 0 | 1
Unity | 502 | 1 | 422 | 2 | 0 | PCS Communication Parameters 1 | Month | Float |  |  | 0 | 1
Unity | 502 | 1 | 424 | 2 | 0 | PCS Communication Parameters 1 | Year | Float |  |  | 0 | 1
Unity | 502 | 1 | 426 | 2 | 0 | PCS Communication Parameters 1 | Phase N Current RMS | Float | A |  | 0 | 1
Unity | 502 | 1 | 428 | 2 | 0 | PCS Communication Parameters 1 | Derating Factor | Float |  |  | 0 | 1
Unity | 502 | 1 | 430 | 2 | 0 | PCS Communication Parameters 1 | Derating Flag | Float |  | 0,Not Derated;1,Upper Device or EMS Command Derating;2,BMS Derating;3,DC Over/Under-Voltage Derating;4,Over-Temp Derating;5,AC Under-Voltage Derating | 0 | 1
Unity | 502 | 1 | 432 | 2 | 0 | PCS Communication Parameters 1 | PCS Capacitor Upper DC Voltage | Float | V |  | 0 | 1
Unity | 502 | 1 | 434 | 2 | 0 | PCS Communication Parameters 1 | PCS Capacitor Lower DC Voltage | Float | V |  | 0 | 1
Unity | 502 | 1 | 436 | 2 | 0 | PCS Communication Parameters 1 | PCS Total DC Voltage | Float | V |  | 0 | 1
Unity | 502 | 1 | 438 | 2 | 0 | PCS Communication Parameters 1 | Leakage Current Value | Float | A |  | 0 | 1
Unity | 502 | 1 | 440 | 2 | 0 | PCS Communication Parameters 1 | Insulation Resistance Value | Float | KΩ |  | 0 | 1
Unity | 502 | 1 | 442 | 2 | 0 | PCS Communication Parameters 1 | Phase A Branch 1 Current | Float | A |  | 0 | 1
Unity | 502 | 1 | 444 | 2 | 0 | PCS Communication Parameters 1 | Phase B Branch 1 Current | Float | A |  | 0 | 1
Unity | 502 | 1 | 446 | 2 | 0 | PCS Communication Parameters 1 | Phase C Branch 1 Current | Float | A |  | 0 | 1
Unity | 502 | 1 | 448 | 2 | 0 | PCS Communication Parameters 1 | Phase N Branch 1 Current | Float | A |  | 0 | 1
Unity | 502 | 1 | 450 | 2 | 0 | PCS Communication Parameters 1 | Phase A Branch 2 Current | Float | A |  | 0 | 1
Unity | 502 | 1 | 452 | 2 | 0 | PCS Communication Parameters 1 | Phase B Branch 2 Current | Float | A |  | 0 | 1
Unity | 502 | 1 | 454 | 2 | 0 | PCS Communication Parameters 1 | Phase C Branch 2 Current | Float | A |  | 0 | 1
Unity | 502 | 1 | 456 | 2 | 0 | PCS Communication Parameters 1 | Phase N Branch 2 Current | Float | A |  | 0 | 1
Unity | 502 | 1 | 458 | 2 | 0 | PCS Communication Parameters 1 | Phase A Temperature | Float | ℃ |  | 0 | 1
Unity | 502 | 1 | 460 | 2 | 0 | PCS Communication Parameters 1 | Phase B Temperature | Float | ℃ |  | 0 | 1
Unity | 502 | 1 | 462 | 2 | 0 | PCS Communication Parameters 1 | Phase C Temperature | Float | ℃ |  | 0 | 1
Unity | 502 | 1 | 464 | 2 | 0 | PCS Communication Parameters 1 | Phase N Temperature | Float | ℃ |  | 0 | 1
Unity | 502 | 1 | 466 | 2 | 0 | PCS Communication Parameters 1 | Air Inlet Temperature | Float | ℃ |  | 0 | 1
Unity | 502 | 1 | 468 | 2 | 0 | PCS Communication Parameters 1 | Cavity Temperature | Float | ℃ |  | 0 | 1
Unity | 502 | 1 | 470 | 2 | 0 | PCS Communication Parameters 1 | Air Outlet Temperature | Float | ℃ |  | 0 | 1
Unity | 502 | 1 | 472 | 2 | 0 | PCS Communication Parameters 1 | Control Chip Junction Temperature | Float | ℃ |  | 0 | 1
Unity | 502 | 1 | 474 | 2 | 0 | PCS Communication Parameters 1 | Communication Chip Junction Temperature | Float | ℃ |  | 0 | 1
Unity | 502 | 1 | 476 | 2 | 0 | PCS Communication Parameters 1 | Operating Mode Selection | Float |  | 0,Reserved;1,Constant Current Charging;2,Constant Voltage Charging;3,Constant Power Charging;4,DC Constant Voltage Mode | 0 | 1
Unity | 502 | 1 | 478 | 2 | 0 | PCS Communication Parameters 1 | Constant Voltage Charge Voltage Setting | Float | V |  | 0 | 1
Unity | 502 | 1 | 480 | 2 | 0 | PCS Communication Parameters 1 | Constant Current Charge Current Setting | Float | A |  | 0 | 1
Unity | 502 | 1 | 482 | 2 | 0 | PCS Communication Parameters 1 | Active Power Setting | Float | kW |  | 0 | 1
Unity | 502 | 1 | 484 | 2 | 0 | PCS Communication Parameters 1 | Reactive Power Setting | Float | kVar |  | 0 | 1
Unity | 502 | 1 | 486 | 2 | 0 | PCS Communication Parameters 1 | On/Off-Grid Setting | Float |  | 0,On-Grid Mode;1,Off-Grid Mode;2,VSG Mode | 0 | 1
Unity | 502 | 1 | 488 | 2 | 0 | PCS Communication Parameters 1 | Off-Grid Output Voltage Setpoint | Float | V |  | 0 | 1
Unity | 502 | 1 | 490 | 2 | 0 | PCS Communication Parameters 1 | Off-Grid Output Frequency Setpoint | Float | Hz |  | 0 | 1
Unity | 502 | 1 | 492 | 2 | 0 | PCS Communication Parameters 1 | Phase A Active Power Setting | Float | kW |  | 0 | 1
Unity | 502 | 1 | 494 | 2 | 0 | PCS Communication Parameters 1 | Phase B Active Power Setting | Float | kW |  | 0 | 1
Unity | 502 | 1 | 496 | 2 | 0 | PCS Communication Parameters 1 | Phase C Active Power Setting | Float | kW |  | 0 | 1
Unity | 502 | 1 | 498 | 2 | 0 | PCS Communication Parameters 1 | Phase A Reactive Power Setting | Float | kVar |  | 0 | 1
Unity | 502 | 1 | 500 | 2 | 0 | PCS Communication Parameters 1 | Phase B Reactive Power Setting | Float | kVar |  | 0 | 1
Unity | 502 | 1 | 502 | 2 | 0 | PCS Communication Parameters 1 | Phase C Reactive Power Setting | Float | kVar |  | 0 | 1
Unity | 502 | 1 | 504 | 2 | 0 | PCS Communication Parameters 1 | Off-Grid Phase A Voltage Setting | Float | V |  | 0 | 1
Unity | 502 | 1 | 506 | 2 | 0 | PCS Communication Parameters 1 | Off-Grid Phase B Voltage Setting | Float | V |  | 0 | 1
Unity | 502 | 1 | 508 | 2 | 0 | PCS Communication Parameters 1 | Off-Grid Phase C Voltage Setting | Float | V |  | 0 | 1
Unity | 502 | 1 | 510 | 2 | 0 | PCS Communication Parameters 1 | Primary Frequency Regulation Frequency Deadband | Float | Hz |  | 0 | 1
Unity | 502 | 1 | 512 | 2 | 0 | PCS Communication Parameters 1 | Primary Frequency Regulation K Value | Float |  |  | 0 | 1
Unity | 502 | 1 | 514 | 2 | 0 | PCS Communication Parameters 1 | VSG Frequency Droop Factor | Float |  |  | 0 | 1
Unity | 502 | 1 | 516 | 2 | 0 | PCS Communication Parameters 1 | VSG Voltage Droop Factor | Float |  |  | 0 | 1
Unity | 502 | 1 | 518 | 2 | 0 | PCS Communication Parameters 1 | On/Off-Grid Switch Running Mode | Float |  | 0,None;1,Manual;2,Auto;3,Hybrid;4,Silent | 0 | 1
Unity | 502 | 1 | 520 | 2 | 0 | PCS Communication Parameters 1 | Active Power Control Method | Float |  | 0,Per-Phase Power Control Mode;1,Total Power Control Mode | 0 | 1
Unity | 502 | 1 | 522 | 2 | 0 | PCS Communication Parameters 1 | Time Sync-Second | Float |  |  | 0 | 1
Unity | 502 | 1 | 524 | 2 | 0 | PCS Communication Parameters 1 | Time Sync-Minute | Float |  |  | 0 | 1
Unity | 502 | 1 | 526 | 2 | 0 | PCS Communication Parameters 1 | Time Sync-Hour | Float |  |  | 0 | 1
Unity | 502 | 1 | 528 | 2 | 0 | PCS Communication Parameters 1 | Time Sync-Day | Float |  |  | 0 | 1
Unity | 502 | 1 | 530 | 2 | 0 | PCS Communication Parameters 1 | Time Sync-Month | Float |  |  | 0 | 1
Unity | 502 | 1 | 532 | 2 | 0 | PCS Communication Parameters 1 | Time Sync-Year | Float |  |  | 0 | 1
Unity | 502 | 1 | 534 | 2 | 0 | PCS Communication Parameters 1 | Reactive Power Mode | Float |  | 0,Constant Power Mode;1,Constant Power Factor Mode | 0 | 1
Unity | 502 | 1 | 536 | 2 | 0 | PCS Communication Parameters 1 | Power Factor Setting | Float |  |  | 0 | 1
Unity | 502 | 1 | 538 | 2 | 0 | PCS Communication Parameters 1 | Insulation Detection Enable | Float |  | 0,Disabled;1,Enabled | 0 | 1
Unity | 502 | 1 | 540 | 2 | 0 | PCS Communication Parameters 1 | Leakage Current Threshold Setting | Float | A |  | 0 | 1
Unity | 502 | 1 | 542 | 2 | 0 | PCS Communication Parameters 1 | Insulation Resistance Threshold Setting | Float | KΩ |  | 0 | 1
Unity | 502 | 1 | 544 | 2 | 0 | PCS Communication Parameters 1 | Primary Frequency Regulation Enable | Float |  | 0,Disabled;1,Enabled | 0 | 1
Unity | 502 | 1 | 546 | 2 | 0 | PCS Communication Parameters 1 | HW Fault-Phase A HW Over-Current | Float |  | 0,Normal;1,Fault | 0 | 1
Unity | 502 | 1 | 548 | 2 | 0 | PCS Communication Parameters 1 | HW Fault-Phase B HW Over-Current | Float |  | 0,Normal;1,Fault | 0 | 1
Unity | 502 | 1 | 550 | 2 | 0 | PCS Communication Parameters 1 | HW Fault-Phase C HW Over-Current | Float |  | 0,Normal;1,Fault | 0 | 1
Unity | 502 | 1 | 552 | 2 | 0 | PCS Communication Parameters 1 | HW Fault-Phase N HW Over-Current | Float |  | 0,Normal;1,Fault | 0 | 1
Unity | 502 | 1 | 554 | 2 | 0 | PCS Communication Parameters 1 | HW Fault-AC/DC Power Mismatch | Float |  | 0,Normal;1,Fault | 0 | 1
Unity | 502 | 1 | 556 | 2 | 0 | PCS Communication Parameters 1 | HW Fault-Auxiliary Power Loss | Float |  | 0,Normal;1,Fault | 0 | 1
Unity | 502 | 1 | 558 | 2 | 0 | PCS Communication Parameters 1 | HW Fault-Temp Too Low or Sensor Fault | Float |  | 0,Normal;1,Fault | 0 | 1
Unity | 502 | 1 | 560 | 2 | 0 | PCS Communication Parameters 1 | HW Fault-Insulation Fault | Float |  | 0,Normal;1,Fault | 0 | 1
Unity | 502 | 1 | 562 | 2 | 0 | PCS Communication Parameters 1 | HW Fault-Total Drive Fault | Float |  | 0,Normal;1,Fault | 0 | 1
Unity | 502 | 1 | 564 | 2 | 0 | PCS Communication Parameters 1 | SW Fault-Phase A Drive Fault | Float |  | 0,Normal;1,Fault | 0 | 1
Unity | 502 | 1 | 566 | 2 | 0 | PCS Communication Parameters 1 | HW Fault-Phase B Drive Fault | Float |  | 0,Normal;1,Fault | 0 | 1
Unity | 502 | 1 | 568 | 2 | 0 | PCS Communication Parameters 1 | HW Fault-Phase C Drive Fault | Float |  | 0,Normal;1,Fault | 0 | 1
Unity | 502 | 1 | 570 | 2 | 0 | PCS Communication Parameters 1 | HW Fault-Phase N Drive Fault | Float |  | 0,Normal;1,Fault | 0 | 1
Unity | 502 | 1 | 572 | 2 | 0 | PCS Communication Parameters 1 | HW Fault-Heat Sink Over-Temp Fault | Float |  | 0,Normal;1,Fault | 0 | 1
Unity | 502 | 1 | 574 | 2 | 0 | PCS Communication Parameters 1 | HW Fault-Ambient Over-Temp Fault | Float |  | 0,Normal;1,Fault | 0 | 1
Unity | 502 | 1 | 576 | 2 | 0 | PCS Communication Parameters 1 | SW Fault-Phase A Output Overload | Float |  | 0,Normal;1,Fault | 0 | 1
Unity | 502 | 1 | 578 | 2 | 0 | PCS Communication Parameters 1 | SW Fault-Phase A Output Over-Current | Float |  | 0,Normal;1,Fault | 0 | 1
Unity | 502 | 1 | 580 | 2 | 0 | PCS Communication Parameters 1 | SW Fault-Phase B Output Overload | Float |  | 0,Normal;1,Fault | 0 | 1
Unity | 502 | 1 | 582 | 2 | 0 | PCS Communication Parameters 1 | SW Fault-Phase B Output Over-Current | Float |  | 0,Normal;1,Fault | 0 | 1
Unity | 502 | 1 | 584 | 2 | 0 | PCS Communication Parameters 1 | SW Fault-Phase C Output Overload | Float |  | 0,Normal;1,Fault | 0 | 1
Unity | 502 | 1 | 586 | 2 | 0 | PCS Communication Parameters 1 | SW Fault-Phase C Output Over-Current | Float |  | 0,Normal;1,Fault | 0 | 1
Unity | 502 | 1 | 588 | 2 | 0 | PCS Communication Parameters 1 | SW Fault-Phase N Output Overload | Float |  | 0,Normal;1,Fault | 0 | 1
Unity | 502 | 1 | 590 | 2 | 0 | PCS Communication Parameters 1 | SW Fault-Phase N Output Over-Current | Float |  | 0,Normal;1,Fault | 0 | 1
Unity | 502 | 1 | 592 | 2 | 0 | PCS Communication Parameters 1 | SW Fault-AC Over-Voltage | Float |  | 0,Normal;1,Fault | 0 | 1
Unity | 502 | 1 | 594 | 2 | 0 | PCS Communication Parameters 1 | SW Fault-AC Under-Voltage | Float |  | 0,Normal;1,Fault | 0 | 1
Unity | 502 | 1 | 596 | 2 | 0 | PCS Communication Parameters 1 | SW Fault-AC Output Over-Voltage | Float |  | 0,Normal;1,Fault | 0 | 1
Unity | 502 | 1 | 598 | 2 | 0 | PCS Communication Parameters 1 | SW Fault-AC Output Under-Voltage | Float |  | 0,Normal;1,Fault | 0 | 1
Unity | 502 | 1 | 600 | 2 | 0 | PCS Communication Parameters 1 | SW Fault-THDU Over-Limit | Float |  | 0,Normal;1,Fault | 0 | 1
Unity | 502 | 1 | 602 | 2 | 0 | PCS Communication Parameters 1 | SW Fault-AC Phase Loss | Float |  | 0,Normal;1,Fault | 0 | 1
Unity | 502 | 1 | 604 | 2 | 0 | PCS Communication Parameters 1 | SW Fault-AC Phase Sequence Error | Float |  | 0,Normal;1,Fault | 0 | 1
Unity | 502 | 1 | 606 | 2 | 0 | PCS Communication Parameters 1 | SW Fault-DC Reverse Connection Fault | Float |  | 0,Normal;1,Fault | 0 | 1
Unity | 502 | 1 | 608 | 2 | 0 | PCS Communication Parameters 1 | SW Fault-DC Bus SW Over-Voltage | Float |  | 0,Normal;1,Fault | 0 | 1
Unity | 502 | 1 | 610 | 2 | 0 | PCS Communication Parameters 1 | SW Fault-DC Bus SW Under-Voltage | Float |  | 0,Normal;1,Fault | 0 | 1
Unity | 502 | 1 | 612 | 2 | 0 | PCS Communication Parameters 1 | SW Fault-AC Over-Frequency | Float |  | 0,Normal;1,Fault | 0 | 1
Unity | 502 | 1 | 614 | 2 | 0 | PCS Communication Parameters 1 | SW Fault-AC Under-Frequency | Float |  | 0,Normal;1,Fault | 0 | 1
Unity | 502 | 1 | 616 | 2 | 0 | PCS Communication Parameters 1 | SW Fault-DC Charge Over-Current | Float |  | 0,Normal;1,Fault | 0 | 1
Unity | 502 | 1 | 618 | 2 | 0 | PCS Communication Parameters 1 | SW Fault-DC Discharge Over-Current | Float |  | 0,Normal;1,Fault | 0 | 1
Unity | 502 | 1 | 620 | 2 | 0 | PCS Communication Parameters 1 | SW Fault-SPI Communication Fault | Float |  | 0,Normal;1,Fault | 0 | 1
Unity | 502 | 1 | 622 | 2 | 0 | PCS Communication Parameters 1 | SW Fault-DC Component Over-Limit | Float |  | 0,Normal;1,Fault | 0 | 1
Unity | 502 | 1 | 624 | 2 | 0 | PCS Communication Parameters 1 | SW Fault-AC Relay Close Fault | Float |  | 0,Normal;1,Fault | 0 | 1
Unity | 502 | 1 | 626 | 2 | 0 | PCS Communication Parameters 1 | SW Fault-AC Relay Open Fault | Float |  | 0,Normal;1,Fault | 0 | 1
Unity | 502 | 1 | 628 | 2 | 0 | PCS Communication Parameters 1 | SW Fault-AC Soft-Start Relay Close Fault | Float |  | 0,Normal;1,Fault | 0 | 1
Unity | 502 | 1 | 630 | 2 | 0 | PCS Communication Parameters 1 | SW Fault-AC Soft-Start Relay Open Fault | Float |  | 0,Normal;1,Fault | 0 | 1
Unity | 502 | 1 | 632 | 2 | 0 | PCS Communication Parameters 1 | SW Fault-DC Main Positive Close Fault | Float |  | 0,Normal;1,Fault | 0 | 1
Unity | 502 | 1 | 634 | 2 | 0 | PCS Communication Parameters 1 | SW Fault-DC Main Positive Open Fault | Float |  | 0,Normal;1,Fault | 0 | 1
Unity | 502 | 1 | 636 | 2 | 0 | PCS Communication Parameters 1 | SW Fault-DC Main Negative Close Fault | Float |  | 0,Normal;1,Fault | 0 | 1
Unity | 502 | 1 | 638 | 2 | 0 | PCS Communication Parameters 1 | SW Fault-DC Main Negative Close Fault 2 | Float |  | 0,Normal;1,Fault | 0 | 1
Unity | 502 | 1 | 640 | 2 | 0 | PCS Communication Parameters 1 | SW Fault-Ferroelectric Parameter Save Error | Float |  | 0,Normal;1,Fault | 0 | 1
Unity | 502 | 1 | 642 | 2 | 0 | PCS Communication Parameters 1 | SW Fault-DC Soft Start Failure | Float |  | 0,Normal;1,Fault | 0 | 1
Unity | 502 | 1 | 644 | 2 | 0 | PCS Communication Parameters 1 | SW Fault-AC/DC Voltage Mismatch | Float |  | 0,Normal;1,Fault | 0 | 1
Unity | 502 | 1 | 646 | 2 | 0 | PCS Communication Parameters 1 | SW Fault-Grid Island Fault | Float |  | 0,Normal;1,Fault | 0 | 1
Unity | 502 | 1 | 648 | 2 | 0 | PCS Communication Parameters 1 | SW Fault-Start Condition Not Met | Float |  | 0,Normal;1,Fault | 0 | 1
Unity | 502 | 1 | 650 | 2 | 0 | PCS Communication Parameters 1 | SW Fault-Switch Fault During Operation | Float |  | 0,Normal;1,Fault | 0 | 1
Unity | 502 | 1 | 652 | 2 | 0 | PCS Communication Parameters 1 | SW Fault-Start Timeout Fault | Float |  | 0,Normal;1,Fault | 0 | 1
Unity | 502 | 1 | 654 | 2 | 0 | PCS Communication Parameters 1 | SW Fault-Parameter Configuration Setting Error | Float |  | 0,Normal;1,Fault | 0 | 1
Unity | 502 | 1 | 656 | 2 | 0 | PCS Communication Parameters 1 | SW Fault-Branch Instantaneous Value Unbalance Fault | Float |  | 0,Normal;1,Fault | 0 | 1
Unity | 502 | 1 | 658 | 2 | 0 | PCS Communication Parameters 1 | SW Fault-DC Path RMS Unbalance Abnormal | Float |  | 0,Normal;1,Fault | 0 | 1
Unity | 502 | 1 | 660 | 2 | 0 | PCS Communication Parameters 1 | SW Fault-AC Voltage Unbalance Fault | Float |  | 0,Normal;1,Fault | 0 | 1
Unity | 502 | 1 | 662 | 2 | 0 | PCS Communication Parameters 1 | SW Alarm-Parameter Upgrade Fault | Float |  | 0,Normal;1,Fault | 0 | 1
Unity | 502 | 1 | 664 | 2 | 0 | PCS Communication Parameters 1 | SW Fault-Ferroelectric Chip Fault | Float |  | 0,Normal;1,Fault | 0 | 1
Unity | 502 | 1 | 666 | 2 | 0 | PCS Communication Parameters 1 | HW Fault-Fuse Blow Fault | Float |  | 0,Normal;1,Fault | 0 | 1
Unity | 502 | 1 | 668 | 2 | 0 | PCS Communication Parameters 1 | SW Fault-Fiber Optic Communication Fault | Float |  | 0,Normal;1,Fault | 0 | 1
Unity | 502 | 1 | 670 | 2 | 0 | PCS Communication Parameters 1 | SW Fault-Battery SW Over-Voltage | Float |  | 0,Normal;1,Fault | 0 | 1
Unity | 502 | 1 | 672 | 2 | 0 | PCS Communication Parameters 1 | SW Fault-Battery SW Under-Voltage | Float |  | 0,Normal;1,Fault | 0 | 1
Unity | 502 | 1 | 674 | 2 | 0 | PCS Communication Parameters 1 | SW Fault-Bus Voltage Unbalance | Float |  | 0,Normal;1,Fault | 0 | 1
Unity | 502 | 1 | 676 | 2 | 0 | PCS Communication Parameters 1 | SW Fault-Half Bus Over-Voltage | Float |  | 0,Normal;1,Fault | 0 | 1
Unity | 502 | 1 | 678 | 2 | 0 | PCS Communication Parameters 1 | SW Fault-Internal Communication Offline | Float |  | 0,Normal;1,Fault | 0 | 1
Unity | 502 | 1 | 680 | 2 | 0 | PCS Communication Parameters 1 | Leakage Current Over-Limit Protection | Float |  | 0,Normal;1,Fault | 0 | 1
Unity | 502 | 1 | 682 | 2 | 0 | PCS Communication Parameters 1 | HW Fault-Zero Drift | Float |  | 0,Normal;1,Fault | 0 | 1
Unity | 502 | 1 | 684 | 2 | 0 | PCS Communication Parameters 1 | HW Fault-DC Soft Start Fault | Float |  | 0,Normal;1,Fault | 0 | 1
Unity | 502 | 1 | 686 | 2 | 0 | PCS Communication Parameters 1 | HW Fault-AC Over-Current | Float |  | 0,Normal;1,Fault | 0 | 1
Unity | 502 | 1 | 688 | 2 | 0 | PCS Communication Parameters 1 | SW Fault-AC Over-Current | Float |  | 0,Normal;1,Fault | 0 | 1
Unity | 502 | 1 | 690 | 2 | 0 | PCS Communication Parameters 1 | HW Fault-Half Bus Over-Voltage | Float |  | 0,Normal;1,Fault | 0 | 1
Unity | 502 | 1 | 692 | 2 | 0 | PCS Communication Parameters 1 | HW Fault-DC Over-Voltage | Float |  | 0,Normal;1,Fault | 0 | 1
Unity | 502 | 1 | 694 | 2 | 0 | PCS Communication Parameters 1 | HW Fault-AC Soft Start Fault | Float |  | 0,Normal;1,Fault | 0 | 1
Unity | 502 | 1 | 696 | 2 | 0 | PCS Communication Parameters 1 | SW Fault-ARM Internal Communication Fault | Float |  | 0,Normal;1,Fault | 0 | 1
Unity | 502 | 1 | 698 | 2 | 0 | PCS Communication Parameters 1 | SW Fault-ARM EMS Communication Fault | Float |  | 0,Normal;1,Fault | 0 | 1
Unity | 502 | 1 | 700 | 2 | 0 | PCS Communication Parameters 1 | SW Fault-ARM SPI Fault Recording Communication Fault | Float |  | 0,Normal;1,Fault | 0 | 1
Unity | 502 | 1 | 702 | 2 | 0 | PCS Communication Parameters 1 | SW Fault-ARM SD Card Fault | Float |  | 0,Normal;1,Fault | 0 | 1
Unity | 502 | 1 | 704 | 2 | 0 | PCS Communication Parameters 1 | SW Fault-ARM RTC Fault | Float |  | 0,Normal;1,Fault | 0 | 1
Unity | 502 | 1 | 706 | 2 | 0 | PCS Communication Parameters 1 | SW Fault-ARM Internal Communication Protocol Version Mismatch | Float |  | 0,Normal;1,Fault | 0 | 1
Unity | 502 | 1 | 708 | 2 | 0 | PCS Communication Parameters 1 | SW Fault-ARM COM1 Ethernet Communication Fault | Float |  | 0,Normal;1,Fault | 0 | 1
Unity | 502 | 1 | 710 | 2 | 0 | PCS Communication Parameters 1 | SW Fault-ARM E-Stop Input Signal Feedback | Float |  | 0,Normal;1,Fault | 0 | 1
Unity | 502 | 1 | 712 | 2 | 0 | PCS Communication Parameters 1 | SW Fault-ARM BMS Dry Contact Signal Feedback | Float |  | 0,Normal;1,Fault | 0 | 1
Unity | 502 | 1 | 714 | 2 | 0 | PCS Communication Parameters 1 | SW Fault-ARM Inbo STS Switch Thyristor Over-Temp | Float |  | 0,Normal;1,Fault | 0 | 1
Unity | 502 | 1 | 716 | 2 | 0 | PCS Communication Parameters 1 | BMS Communication Fault | Float |  | 0,Normal;1,Fault | 0 | 1
Unity | 502 | 1 | 718 | 2 | 0 | PCS Communication Parameters 1 | BMS Temperature Abnormal | Float |  | 0,Normal;1,Fault | 0 | 1
Unity | 502 | 1 | 720 | 2 | 0 | PCS Communication Parameters 1 | BMS Trip | Float |  | 0,Normal;1,Fault | 0 | 1
Unity | 502 | 1 | 722 | 2 | 0 | PCS Communication Parameters 1 | BMS Battery Alarm | Float |  | 0,Normal;1,Fault | 0 | 1
Unity | 502 | 1 | 724 | 2 | 0 | PCS Communication Parameters 1 | SW E-Stop Fault Feedback | Float |  | 0,Normal;1,Fault | 0 | 1
Unity | 502 | 1 | 726 | 2 | 0 | BMS Communication Parameters 1 | Online Points | Float |  | 0,Offline;1,Online | 0 | 1
Unity | 502 | 1 | 728 | 2 | 0 | BMS Communication Parameters 1 | Total Voltage Diff Too Large | Float |  | 0,Normal;1,Fault | 0 | 1
Unity | 502 | 1 | 730 | 2 | 0 | BMS Communication Parameters 1 | Insulation Too Low | Float |  | 0,Normal;1,Fault | 0 | 1
Unity | 502 | 1 | 732 | 2 | 0 | BMS Communication Parameters 1 | Cell Voltage Too High | Float |  | 0,Normal;1,Fault | 0 | 1
Unity | 502 | 1 | 734 | 2 | 0 | BMS Communication Parameters 1 | Cell Temp Too High | Float |  | 0,Normal;1,Fault | 0 | 1
Unity | 502 | 1 | 736 | 2 | 0 | BMS Communication Parameters 1 | Cell Voltage Update Fault | Float |  | 0,Normal;1,Fault | 0 | 1
Unity | 502 | 1 | 738 | 2 | 0 | BMS Communication Parameters 1 | Pole Temp Too High | Float |  | 0,Normal;1,Fault | 0 | 1
Unity | 502 | 1 | 740 | 2 | 0 | BMS Communication Parameters 1 | Current Too High | Float |  | 0,Normal;1,Fault | 0 | 1
Unity | 502 | 1 | 742 | 2 | 0 | BMS Communication Parameters 1 | Insulation Fault | Float |  | 0,Normal;1,Fault | 0 | 1
Unity | 502 | 1 | 744 | 2 | 0 | BMS Communication Parameters 1 | NTC Fault (Functional Safety Fault) | Float |  | 0,Normal;1,Fault | 0 | 1
Unity | 502 | 1 | 746 | 2 | 0 | BMS Communication Parameters 1 | Pole Temp Sensor Fault | Float |  | 0,Normal;1,Fault | 0 | 1
Unity | 502 | 1 | 748 | 2 | 0 | BMS Communication Parameters 1 | Battery Temperature Sensor Fault | Float |  | 0,Normal;1,Fault | 0 | 1
Unity | 502 | 1 | 750 | 2 | 0 | BMS Communication Parameters 1 | Voltage Sampling Fault | Float |  | 0,Normal;1,Fault | 0 | 1
Unity | 502 | 1 | 752 | 2 | 0 | BMS Communication Parameters 1 | Sampling Chip Fault | Float |  | 0,Normal;1,Fault | 0 | 1
Unity | 502 | 1 | 754 | 2 | 0 | BMS Communication Parameters 1 | Current Sampling Fault (Functional Safety Fault) | Float |  | 0,Normal;1,Fault | 0 | 1
Unity | 502 | 1 | 756 | 2 | 0 | BMS Communication Parameters 1 | Battery Temperature Too Low | Float |  | 0,Normal;1,Fault | 0 | 1
Unity | 502 | 1 | 758 | 2 | 0 | BMS Communication Parameters 1 | Charge Over-Current | Float |  | 0,Normal;1,Fault | 0 | 1
Unity | 502 | 1 | 760 | 2 | 0 | BMS Communication Parameters 1 | BMU Self-Test | Float |  | 0,Normal;1,Fault | 0 | 1
Unity | 502 | 1 | 762 | 2 | 0 | BMS Communication Parameters 1 | BCU Self-Test | Float |  | 0,Normal;1,Fault | 0 | 1
Unity | 502 | 1 | 764 | 2 | 0 | BMS Communication Parameters 1 | Fuse Fault | Float |  | 0,Normal;1,Fault | 0 | 1
Unity | 502 | 1 | 766 | 2 | 0 | BMS Communication Parameters 1 | Contactor Fault | Float |  | 0,Normal;1,Fault | 0 | 1
Unity | 502 | 1 | 768 | 2 | 0 | BMS Communication Parameters 1 | BMU Communication Fault | Float |  | 0,Normal;1,Fault | 0 | 1
Unity | 502 | 1 | 770 | 2 | 0 | BMS Communication Parameters 1 | BAU Communication Fault | Float |  | 0,Normal;1,Fault | 0 | 1
Unity | 502 | 1 | 772 | 2 | 0 | BMS Communication Parameters 1 | Current Sampling Fault | Float |  | 0,Normal;1,Fault | 0 | 1
Unity | 502 | 1 | 774 | 2 | 0 | BMS Communication Parameters 1 | Insulation Monitoring Fault | Float |  | 0,Normal;1,Fault | 0 | 1
Unity | 502 | 1 | 776 | 2 | 0 | BMS Communication Parameters 1 | Isolation Switch Status | Float |  | 0,Normal;1,Fault | 0 | 1
Unity | 502 | 1 | 778 | 2 | 0 | BMS Communication Parameters 1 | NTC Fault | Float |  | 0,Normal;1,Fault | 0 | 1
Unity | 502 | 1 | 780 | 2 | 0 | BMS Communication Parameters 1 | HV Box Temperature Fault | Float |  | 0,Normal;1,Fault | 0 | 1
Unity | 502 | 1 | 782 | 2 | 0 | BMS Communication Parameters 1 | HV Circuit Fault | Float |  | 0,Normal;1,Fault | 0 | 1
Unity | 502 | 1 | 784 | 2 | 0 | BMS Communication Parameters 1 | Functional Safety Fault | Float |  | 0,Normal;1,Fault | 0 | 1
Unity | 502 | 1 | 786 | 2 | 0 | BMS Communication Parameters 1 | PCS Communication Fault | Float |  | 0,Normal;1,Fault | 0 | 1
Unity | 502 | 1 | 788 | 2 | 0 | BMS Communication Parameters 1 | Total Voltage Over-Voltage (Level 1) | Float |  | 0,Normal;1,Fault | 0 | 1
Unity | 502 | 1 | 790 | 2 | 0 | BMS Communication Parameters 1 | Total Voltage Under-Voltage (Level 1) | Float |  | 0,Normal;1,Fault | 0 | 1
Unity | 502 | 1 | 792 | 2 | 0 | BMS Communication Parameters 1 | Cell Over-Voltage (Level 1) | Float |  | 0,Normal;1,Fault | 0 | 1
Unity | 502 | 1 | 794 | 2 | 0 | BMS Communication Parameters 1 | Cell Under-Voltage (Level 1) | Float |  | 0,Normal;1,Fault | 0 | 1
Unity | 502 | 1 | 796 | 2 | 0 | BMS Communication Parameters 1 | Discharge Over-Current (Level 1) | Float |  | 0,Normal;1,Fault | 0 | 1
Unity | 502 | 1 | 798 | 2 | 0 | BMS Communication Parameters 1 | Charge Over-Current (Level 1) | Float |  | 0,Normal;1,Fault | 0 | 1
Unity | 502 | 1 | 800 | 2 | 0 | BMS Communication Parameters 1 | Discharge Over-Temp (Level 1) | Float |  | 0,Normal;1,Fault | 0 | 1
Unity | 502 | 1 | 802 | 2 | 0 | BMS Communication Parameters 1 | Discharge Under-Temp (Level 1) | Float |  | 0,Normal;1,Fault | 0 | 1
Unity | 502 | 1 | 804 | 2 | 0 | BMS Communication Parameters 1 | Charge Over-Temp (Level 1) | Float |  | 0,Normal;1,Fault | 0 | 1
Unity | 502 | 1 | 806 | 2 | 0 | BMS Communication Parameters 1 | Charge Under-Temp (Level 1) | Float |  | 0,Normal;1,Fault | 0 | 1
Unity | 502 | 1 | 808 | 2 | 0 | BMS Communication Parameters 1 | Insulation Too Low (Level 1) | Float |  | 0,Normal;1,Fault | 0 | 1
Unity | 502 | 1 | 810 | 2 | 0 | BMS Communication Parameters 1 | Pole Over-Temp (Level 1) | Float |  | 0,Normal;1,Fault | 0 | 1
Unity | 502 | 1 | 812 | 2 | 0 | BMS Communication Parameters 1 | HV Box Over-Temp (Level 1) | Float |  | 0,Normal;1,Fault | 0 | 1
Unity | 502 | 1 | 814 | 2 | 0 | BMS Communication Parameters 1 | Cell Voltage Diff (Level 1) | Float |  | 0,Normal;1,Fault | 0 | 1
Unity | 502 | 1 | 816 | 2 | 0 | BMS Communication Parameters 1 | Cell Temp Diff (Level 1) | Float |  | 0,Normal;1,Fault | 0 | 1
Unity | 502 | 1 | 818 | 2 | 0 | BMS Communication Parameters 1 | Total Voltage Over-Voltage (Level 2) | Float |  | 0,Normal;1,Fault | 0 | 1
Unity | 502 | 1 | 820 | 2 | 0 | BMS Communication Parameters 1 | Total Voltage Under-Voltage (Level 2) | Float |  | 0,Normal;1,Fault | 0 | 1
Unity | 502 | 1 | 822 | 2 | 0 | BMS Communication Parameters 1 | Cell Over-Voltage (Level 2) | Float |  | 0,Normal;1,Fault | 0 | 1
Unity | 502 | 1 | 824 | 2 | 0 | BMS Communication Parameters 1 | Cell Under-Voltage (Level 2) | Float |  | 0,Normal;1,Fault | 0 | 1
Unity | 502 | 1 | 826 | 2 | 0 | BMS Communication Parameters 1 | Discharge Over-Current (Level 2) | Float |  | 0,Normal;1,Fault | 0 | 1
Unity | 502 | 1 | 828 | 2 | 0 | BMS Communication Parameters 1 | Charge Over-Current (Level 2) | Float |  | 0,Normal;1,Fault | 0 | 1
Unity | 502 | 1 | 830 | 2 | 0 | BMS Communication Parameters 1 | Discharge Over-Temp (Level 2) | Float |  | 0,Normal;1,Fault | 0 | 1
Unity | 502 | 1 | 832 | 2 | 0 | BMS Communication Parameters 1 | Discharge Under-Temp (Level 2) | Float |  | 0,Normal;1,Fault | 0 | 1
Unity | 502 | 1 | 834 | 2 | 0 | BMS Communication Parameters 1 | Charge Over-Temp (Level 2) | Float |  | 0,Normal;1,Fault | 0 | 1
Unity | 502 | 1 | 836 | 2 | 0 | BMS Communication Parameters 1 | Charge Under-Temp (Level 2) | Float |  | 0,Normal;1,Fault | 0 | 1
Unity | 502 | 1 | 838 | 2 | 0 | BMS Communication Parameters 1 | Insulation Too Low (Level 2) | Float |  | 0,Normal;1,Fault | 0 | 1
Unity | 502 | 1 | 840 | 2 | 0 | BMS Communication Parameters 1 | Pole Over-Temp (Level 2) | Float |  | 0,Normal;1,Fault | 0 | 1
Unity | 502 | 1 | 842 | 2 | 0 | BMS Communication Parameters 1 | HV Box Over-Temp (Level 2) | Float |  | 0,Normal;1,Fault | 0 | 1
Unity | 502 | 1 | 844 | 2 | 0 | BMS Communication Parameters 1 | Cell Voltage Diff (Level 2) | Float |  | 0,Normal;1,Fault | 0 | 1
Unity | 502 | 1 | 846 | 2 | 0 | BMS Communication Parameters 1 | Cell Temp Diff (Level 2) | Float |  | 0,Normal;1,Fault | 0 | 1
Unity | 502 | 1 | 848 | 2 | 0 | BMS Communication Parameters 1 | Total Voltage Over-Voltage (Level 3) | Float |  | 0,Normal;1,Fault | 0 | 1
Unity | 502 | 1 | 850 | 2 | 0 | BMS Communication Parameters 1 | Total Voltage Under-Voltage (Level 3) | Float |  | 0,Normal;1,Fault | 0 | 1
Unity | 502 | 1 | 852 | 2 | 0 | BMS Communication Parameters 1 | Cell Over-Voltage (Level 3) | Float |  | 0,Normal;1,Fault | 0 | 1
Unity | 502 | 1 | 854 | 2 | 0 | BMS Communication Parameters 1 | Cell Under-Voltage (Level 3) | Float |  | 0,Normal;1,Fault | 0 | 1
Unity | 502 | 1 | 856 | 2 | 0 | BMS Communication Parameters 1 | Discharge Over-Current (Level 3) | Float |  | 0,Normal;1,Fault | 0 | 1
Unity | 502 | 1 | 858 | 2 | 0 | BMS Communication Parameters 1 | Charge Over-Current (Level 3) | Float |  | 0,Normal;1,Fault | 0 | 1
Unity | 502 | 1 | 860 | 2 | 0 | BMS Communication Parameters 1 | Discharge Over-Temp (Level 3) | Float |  | 0,Normal;1,Fault | 0 | 1
Unity | 502 | 1 | 862 | 2 | 0 | BMS Communication Parameters 1 | Discharge Under-Temp (Level 3) | Float |  | 0,Normal;1,Fault | 0 | 1
Unity | 502 | 1 | 864 | 2 | 0 | BMS Communication Parameters 1 | Charge Over-Temp (Level 3) | Float |  | 0,Normal;1,Fault | 0 | 1
Unity | 502 | 1 | 866 | 2 | 0 | BMS Communication Parameters 1 | Charge Under-Temp (Level 3) | Float |  | 0,Normal;1,Fault | 0 | 1
Unity | 502 | 1 | 868 | 2 | 0 | BMS Communication Parameters 1 | Insulation Too Low (Level 3) | Float |  | 0,Normal;1,Fault | 0 | 1
Unity | 502 | 1 | 870 | 2 | 0 | BMS Communication Parameters 1 | Pole Over-Temp (Level 3) | Float |  | 0,Normal;1,Fault | 0 | 1
Unity | 502 | 1 | 872 | 2 | 0 | BMS Communication Parameters 1 | HV Box Over-Temp (Level 3) | Float |  | 0,Normal;1,Fault | 0 | 1
Unity | 502 | 1 | 874 | 2 | 0 | BMS Communication Parameters 1 | Cell Voltage Diff (Level 3) | Float |  | 0,Normal;1,Fault | 0 | 1
Unity | 502 | 1 | 876 | 2 | 0 | BMS Communication Parameters 1 | Cell Temp Diff (Level 3) | Float |  | 0,Normal;1,Fault | 0 | 1
Unity | 502 | 1 | 878 | 2 | 0 | BMS Communication Parameters 1 | SOC Too Low (Level 3) | Float |  | 0,Normal;1,Fault | 0 | 1
Unity | 502 | 1 | 880 | 2 | 0 | BMS Communication Parameters 1 | Total Voltage Diff Over-High (Level 1) | Float |  | 0,Normal;1,Fault | 0 | 1
Unity | 502 | 1 | 882 | 2 | 0 | BMS Communication Parameters 1 | Module Over-Voltage (Level 1) | Float |  | 0,Normal;1,Fault | 0 | 1
Unity | 502 | 1 | 884 | 2 | 0 | BMS Communication Parameters 1 | Module Under-Voltage (Level 1) | Float |  | 0,Normal;1,Fault | 0 | 1
Unity | 502 | 1 | 886 | 2 | 0 | BMS Communication Parameters 1 | Temperature Rise Too High (Level 1) | Float |  | 0,Normal;1,Fault | 0 | 1
Unity | 502 | 1 | 888 | 2 | 0 | BMS Communication Parameters 1 | Module Voltage Diff Too Large (Level 1) | Float |  | 0,Normal;1,Fault | 0 | 1
Unity | 502 | 1 | 890 | 2 | 0 | BMS Communication Parameters 1 | Total Voltage Diff Over-High (Level 2) | Float |  | 0,Normal;1,Fault | 0 | 1
Unity | 502 | 1 | 892 | 2 | 0 | BMS Communication Parameters 1 | Module Over-Voltage (Level 2) | Float |  | 0,Normal;1,Fault | 0 | 1
Unity | 502 | 1 | 894 | 2 | 0 | BMS Communication Parameters 1 | Module Under-Voltage (Level 2) | Float |  | 0,Normal;1,Fault | 0 | 1
Unity | 502 | 1 | 896 | 2 | 0 | BMS Communication Parameters 1 | Temperature Rise Too High (Level 2) | Float |  | 0,Normal;1,Fault | 0 | 1
Unity | 502 | 1 | 898 | 2 | 0 | BMS Communication Parameters 1 | Module Voltage Diff Too Large (Level 2) | Float |  | 0,Normal;1,Fault | 0 | 1
Unity | 502 | 1 | 900 | 2 | 0 | BMS Communication Parameters 1 | Total Voltage Diff Over-High (Level 3) | Float |  | 0,Normal;1,Fault | 0 | 1
Unity | 502 | 1 | 902 | 2 | 0 | BMS Communication Parameters 1 | Module Over-Voltage (Level 3) | Float |  | 0,Normal;1,Fault | 0 | 1
Unity | 502 | 1 | 904 | 2 | 0 | BMS Communication Parameters 1 | Module Under-Voltage (Level 3) | Float |  | 0,Normal;1,Fault | 0 | 1
Unity | 502 | 1 | 906 | 2 | 0 | BMS Communication Parameters 1 | Temperature Rise Too High (Level 3) | Float |  | 0,Normal;1,Fault | 0 | 1
Unity | 502 | 1 | 908 | 2 | 0 | BMS Communication Parameters 1 | Module Voltage Diff Too Large (Level 3) | Float |  | 0,Normal;1,Fault | 0 | 1
Unity | 502 | 1 | 910 | 2 | 0 | BMS Communication Parameters 1 | Pre-Power-On Phase | Float |  | 0,Pending Start;1,Pre-Charging;2,Pre-Charging;3,Pre-Charge Success;4,Pre-Charge Failed | 0 | 1
Unity | 502 | 1 | 912 | 2 | 0 | BMS Communication Parameters 1 | System Status | Float |  | 0,Normal;1,Charge Disabled;2,Discharge Disabled;3,Standby;4,Shutdown | 0 | 1
Unity | 502 | 1 | 914 | 2 | 0 | BMS Communication Parameters 1 | Heartbeat Frame | Float |  |  | 0 | 1
Unity | 502 | 1 | 916 | 2 | 0 | BMS Communication Parameters 1 | Slave Registration Status | Float |  | 0,Slave Registration Failed;1,Slave Registration Successful | 0 | 1
Unity | 502 | 1 | 918 | 2 | 0 | BMS Communication Parameters 1 | Pre-Charge Failure Reason | Float |  |  | 0 | 1
Unity | 502 | 1 | 920 | 2 | 0 | BMS Communication Parameters 1 | Charge/Discharge Status | Float |  | 0,Idle;1,Discharge;2,Charge | 0 | 1
Unity | 502 | 1 | 922 | 2 | 0 | BMS Communication Parameters 1 | Full Charge/Full Discharge Flag | Float |  | 0,Invalid;1,Fully Charged;2,Fully Discharged | 0 | 1
Unity | 502 | 1 | 924 | 2 | 0 | BMS Communication Parameters 1 | Positive Contact Status | Float |  | 0,Open;1,Closed | 0 | 1
Unity | 502 | 1 | 926 | 2 | 0 | BMS Communication Parameters 1 | Pre-Charge Contactor Status | Float |  | 0,Open;1,Closed | 0 | 1
Unity | 502 | 1 | 928 | 2 | 0 | BMS Communication Parameters 1 | Negative Contactor Status | Float |  | 0,Open;1,Closed | 0 | 1
Unity | 502 | 1 | 930 | 2 | 0 | BMS Communication Parameters 1 | Isolation Switch Feedback Status | Float |  | 0,Open;1,Closed | 0 | 1
Unity | 502 | 1 | 932 | 2 | 0 | BMS Communication Parameters 1 | Slave Init Fault (Level 1) | Float |  | 0,Normal;1,Fault | 0 | 1
Unity | 502 | 1 | 934 | 2 | 0 | BMS Communication Parameters 1 | Sampling Line Fault (Level 1) | Float |  | 0,Normal;1,Fault | 0 | 1
Unity | 502 | 1 | 936 | 2 | 0 | BMS Communication Parameters 1 | Connection Line Fault (Level 1) | Float |  | 0,Normal;1,Fault | 0 | 1
Unity | 502 | 1 | 938 | 2 | 0 | BMS Communication Parameters 1 | Sampling Chip Fault (Level 1) | Float |  | 0,Normal;1,Fault | 0 | 1
Unity | 502 | 1 | 940 | 2 | 0 | BMS Communication Parameters 1 | Voltage Sampling Fault (Level 1) | Float |  | 0,Normal;1,Fault | 0 | 1
Unity | 502 | 1 | 942 | 2 | 0 | BMS Communication Parameters 1 | Battery Temperature Sampling Fault (Level 1) | Float |  | 0,Normal;1,Fault | 0 | 1
Unity | 502 | 1 | 944 | 2 | 0 | BMS Communication Parameters 1 | Temperature Sensor Fault (Level 1) | Float |  | 0,Normal;1,Fault | 0 | 1
Unity | 502 | 1 | 946 | 2 | 0 | BMS Communication Parameters 1 | Standby (Level 1) | Float |  | 0,Normal;1,Fault | 0 | 1
Unity | 502 | 1 | 948 | 2 | 0 | BMS Communication Parameters 1 | EEPROM Fault (Level 1) | Float |  | 0,Normal;1,Fault | 0 | 1
Unity | 502 | 1 | 950 | 2 | 0 | BMS Communication Parameters 1 | Passive Balancing Fault (Level 3) | Float |  | 0,Normal;1,Fault | 0 | 1
Unity | 502 | 1 | 952 | 2 | 0 | BMS Communication Parameters 1 | Passive Balancing Temp Fault (Level 3) | Float |  | 0,Normal;1,Fault | 0 | 1
Unity | 502 | 1 | 954 | 2 | 0 | BMS Communication Parameters 1 | Active Balancing Fault (Level 3) | Float |  | 0,Normal;1,Fault | 0 | 1
Unity | 502 | 1 | 956 | 2 | 0 | BMS Communication Parameters 1 | Active Balancing Temp Fault (Level 3) | Float |  | 0,Normal;1,Fault | 0 | 1
Unity | 502 | 1 | 958 | 2 | 0 | BMS Communication Parameters 1 | Pole Temp Fault (Level 1) | Float |  | 0,Normal;1,Fault | 0 | 1
Unity | 502 | 1 | 960 | 2 | 0 | BMS Communication Parameters 1 | Inter-Module Balancing Fault (Level 3) | Float |  | 0,Normal;1,Fault | 0 | 1
Unity | 502 | 1 | 962 | 2 | 0 | BMS Communication Parameters 1 | Cell Voltage 1 | Float | mV |  | 0 | 1
Unity | 502 | 1 | 964 | 2 | 0 | BMS Communication Parameters 1 | Cell Voltage 2 | Float | mV |  | 0 | 1
Unity | 502 | 1 | 966 | 2 | 0 | BMS Communication Parameters 1 | Cell Voltage 3 | Float | mV |  | 0 | 1
Unity | 502 | 1 | 968 | 2 | 0 | BMS Communication Parameters 1 | Cell Voltage 4 | Float | mV |  | 0 | 1
Unity | 502 | 1 | 970 | 2 | 0 | BMS Communication Parameters 1 | Cell Voltage 5 | Float | mV |  | 0 | 1
Unity | 502 | 1 | 972 | 2 | 0 | BMS Communication Parameters 1 | Cell Voltage 6 | Float | mV |  | 0 | 1
Unity | 502 | 1 | 974 | 2 | 0 | BMS Communication Parameters 1 | Cell Voltage 7 | Float | mV |  | 0 | 1
Unity | 502 | 1 | 976 | 2 | 0 | BMS Communication Parameters 1 | Cell Voltage 8 | Float | mV |  | 0 | 1
Unity | 502 | 1 | 978 | 2 | 0 | BMS Communication Parameters 1 | Cell Voltage 9 | Float | mV |  | 0 | 1
Unity | 502 | 1 | 980 | 2 | 0 | BMS Communication Parameters 1 | Cell Voltage 10 | Float | mV |  | 0 | 1
Unity | 502 | 1 | 982 | 2 | 0 | BMS Communication Parameters 1 | Cell Voltage 11 | Float | mV |  | 0 | 1
Unity | 502 | 1 | 984 | 2 | 0 | BMS Communication Parameters 1 | Cell Voltage 12 | Float | mV |  | 0 | 1
Unity | 502 | 1 | 986 | 2 | 0 | BMS Communication Parameters 1 | Cell Voltage 13 | Float | mV |  | 0 | 1
Unity | 502 | 1 | 988 | 2 | 0 | BMS Communication Parameters 1 | Cell Voltage 14 | Float | mV |  | 0 | 1
Unity | 502 | 1 | 990 | 2 | 0 | BMS Communication Parameters 1 | Cell Voltage 15 | Float | mV |  | 0 | 1
Unity | 502 | 1 | 992 | 2 | 0 | BMS Communication Parameters 1 | Cell Voltage 16 | Float | mV |  | 0 | 1
Unity | 502 | 1 | 994 | 2 | 0 | BMS Communication Parameters 1 | Cell Voltage 17 | Float | mV |  | 0 | 1
Unity | 502 | 1 | 996 | 2 | 0 | BMS Communication Parameters 1 | Cell Voltage 18 | Float | mV |  | 0 | 1
Unity | 502 | 1 | 998 | 2 | 0 | BMS Communication Parameters 1 | Cell Voltage 19 | Float | mV |  | 0 | 1
Unity | 502 | 1 | 1000 | 2 | 0 | BMS Communication Parameters 1 | Cell Voltage 20 | Float | mV |  | 0 | 1
Unity | 502 | 1 | 1002 | 2 | 0 | BMS Communication Parameters 1 | Cell Voltage 21 | Float | mV |  | 0 | 1
Unity | 502 | 1 | 1004 | 2 | 0 | BMS Communication Parameters 1 | Cell Voltage 22 | Float | mV |  | 0 | 1
Unity | 502 | 1 | 1006 | 2 | 0 | BMS Communication Parameters 1 | Cell Voltage 23 | Float | mV |  | 0 | 1
Unity | 502 | 1 | 1008 | 2 | 0 | BMS Communication Parameters 1 | Cell Voltage 24 | Float | mV |  | 0 | 1
Unity | 502 | 1 | 1010 | 2 | 0 | BMS Communication Parameters 1 | Cell Voltage 25 | Float | mV |  | 0 | 1
Unity | 502 | 1 | 1012 | 2 | 0 | BMS Communication Parameters 1 | Cell Voltage 26 | Float | mV |  | 0 | 1
Unity | 502 | 1 | 1014 | 2 | 0 | BMS Communication Parameters 1 | Cell Voltage 27 | Float | mV |  | 0 | 1
Unity | 502 | 1 | 1016 | 2 | 0 | BMS Communication Parameters 1 | Cell Voltage 28 | Float | mV |  | 0 | 1
Unity | 502 | 1 | 1018 | 2 | 0 | BMS Communication Parameters 1 | Cell Voltage 29 | Float | mV |  | 0 | 1
Unity | 502 | 1 | 1020 | 2 | 0 | BMS Communication Parameters 1 | Cell Voltage 30 | Float | mV |  | 0 | 1
Unity | 502 | 1 | 1022 | 2 | 0 | BMS Communication Parameters 1 | Cell Voltage 31 | Float | mV |  | 0 | 1
Unity | 502 | 1 | 1024 | 2 | 0 | BMS Communication Parameters 1 | Cell Voltage 32 | Float | mV |  | 0 | 1
Unity | 502 | 1 | 1026 | 2 | 0 | BMS Communication Parameters 1 | Cell Voltage 33 | Float | mV |  | 0 | 1
Unity | 502 | 1 | 1028 | 2 | 0 | BMS Communication Parameters 1 | Cell Voltage 34 | Float | mV |  | 0 | 1
Unity | 502 | 1 | 1030 | 2 | 0 | BMS Communication Parameters 1 | Cell Voltage 35 | Float | mV |  | 0 | 1
Unity | 502 | 1 | 1032 | 2 | 0 | BMS Communication Parameters 1 | Cell Voltage 36 | Float | mV |  | 0 | 1
Unity | 502 | 1 | 1034 | 2 | 0 | BMS Communication Parameters 1 | Cell Voltage 37 | Float | mV |  | 0 | 1
Unity | 502 | 1 | 1036 | 2 | 0 | BMS Communication Parameters 1 | Cell Voltage 38 | Float | mV |  | 0 | 1
Unity | 502 | 1 | 1038 | 2 | 0 | BMS Communication Parameters 1 | Cell Voltage 39 | Float | mV |  | 0 | 1
Unity | 502 | 1 | 1040 | 2 | 0 | BMS Communication Parameters 1 | Cell Voltage 40 | Float | mV |  | 0 | 1
Unity | 502 | 1 | 1042 | 2 | 0 | BMS Communication Parameters 1 | Cell Voltage 41 | Float | mV |  | 0 | 1
Unity | 502 | 1 | 1044 | 2 | 0 | BMS Communication Parameters 1 | Cell Voltage 42 | Float | mV |  | 0 | 1
Unity | 502 | 1 | 1046 | 2 | 0 | BMS Communication Parameters 1 | Cell Voltage 43 | Float | mV |  | 0 | 1
Unity | 502 | 1 | 1048 | 2 | 0 | BMS Communication Parameters 1 | Cell Voltage 44 | Float | mV |  | 0 | 1
Unity | 502 | 1 | 1050 | 2 | 0 | BMS Communication Parameters 1 | Cell Voltage 45 | Float | mV |  | 0 | 1
Unity | 502 | 1 | 1052 | 2 | 0 | BMS Communication Parameters 1 | Cell Voltage 46 | Float | mV |  | 0 | 1
Unity | 502 | 1 | 1054 | 2 | 0 | BMS Communication Parameters 1 | Cell Voltage 47 | Float | mV |  | 0 | 1
Unity | 502 | 1 | 1056 | 2 | 0 | BMS Communication Parameters 1 | Cell Voltage 48 | Float | mV |  | 0 | 1
Unity | 502 | 1 | 1058 | 2 | 0 | BMS Communication Parameters 1 | Cell Voltage 49 | Float | mV |  | 0 | 1
Unity | 502 | 1 | 1060 | 2 | 0 | BMS Communication Parameters 1 | Cell Voltage 50 | Float | mV |  | 0 | 1
Unity | 502 | 1 | 1062 | 2 | 0 | BMS Communication Parameters 1 | Cell Voltage 51 | Float | mV |  | 0 | 1
Unity | 502 | 1 | 1064 | 2 | 0 | BMS Communication Parameters 1 | Cell Voltage 52 | Float | mV |  | 0 | 1
Unity | 502 | 1 | 1066 | 2 | 0 | BMS Communication Parameters 1 | Cell Voltage 53 | Float | mV |  | 0 | 1
Unity | 502 | 1 | 1068 | 2 | 0 | BMS Communication Parameters 1 | Cell Voltage 54 | Float | mV |  | 0 | 1
Unity | 502 | 1 | 1070 | 2 | 0 | BMS Communication Parameters 1 | Cell Voltage 55 | Float | mV |  | 0 | 1
Unity | 502 | 1 | 1072 | 2 | 0 | BMS Communication Parameters 1 | Cell Voltage 56 | Float | mV |  | 0 | 1
Unity | 502 | 1 | 1074 | 2 | 0 | BMS Communication Parameters 1 | Cell Voltage 57 | Float | mV |  | 0 | 1
Unity | 502 | 1 | 1076 | 2 | 0 | BMS Communication Parameters 1 | Cell Voltage 58 | Float | mV |  | 0 | 1
Unity | 502 | 1 | 1078 | 2 | 0 | BMS Communication Parameters 1 | Cell Voltage 59 | Float | mV |  | 0 | 1
Unity | 502 | 1 | 1080 | 2 | 0 | BMS Communication Parameters 1 | Cell Voltage 60 | Float | mV |  | 0 | 1
Unity | 502 | 1 | 1082 | 2 | 0 | BMS Communication Parameters 1 | Cell Voltage 61 | Float | mV |  | 0 | 1
Unity | 502 | 1 | 1084 | 2 | 0 | BMS Communication Parameters 1 | Cell Voltage 62 | Float | mV |  | 0 | 1
Unity | 502 | 1 | 1086 | 2 | 0 | BMS Communication Parameters 1 | Cell Voltage 63 | Float | mV |  | 0 | 1
Unity | 502 | 1 | 1088 | 2 | 0 | BMS Communication Parameters 1 | Cell Voltage 64 | Float | mV |  | 0 | 1
Unity | 502 | 1 | 1090 | 2 | 0 | BMS Communication Parameters 1 | Cell Voltage 65 | Float | mV |  | 0 | 1
Unity | 502 | 1 | 1092 | 2 | 0 | BMS Communication Parameters 1 | Cell Voltage 66 | Float | mV |  | 0 | 1
Unity | 502 | 1 | 1094 | 2 | 0 | BMS Communication Parameters 1 | Cell Voltage 67 | Float | mV |  | 0 | 1
Unity | 502 | 1 | 1096 | 2 | 0 | BMS Communication Parameters 1 | Cell Voltage 68 | Float | mV |  | 0 | 1
Unity | 502 | 1 | 1098 | 2 | 0 | BMS Communication Parameters 1 | Cell Voltage 69 | Float | mV |  | 0 | 1
Unity | 502 | 1 | 1100 | 2 | 0 | BMS Communication Parameters 1 | Cell Voltage 70 | Float | mV |  | 0 | 1
Unity | 502 | 1 | 1102 | 2 | 0 | BMS Communication Parameters 1 | Cell Voltage 71 | Float | mV |  | 0 | 1
Unity | 502 | 1 | 1104 | 2 | 0 | BMS Communication Parameters 1 | Cell Voltage 72 | Float | mV |  | 0 | 1
Unity | 502 | 1 | 1106 | 2 | 0 | BMS Communication Parameters 1 | Cell Voltage 73 | Float | mV |  | 0 | 1
Unity | 502 | 1 | 1108 | 2 | 0 | BMS Communication Parameters 1 | Cell Voltage 74 | Float | mV |  | 0 | 1
Unity | 502 | 1 | 1110 | 2 | 0 | BMS Communication Parameters 1 | Cell Voltage 75 | Float | mV |  | 0 | 1
Unity | 502 | 1 | 1112 | 2 | 0 | BMS Communication Parameters 1 | Cell Voltage 76 | Float | mV |  | 0 | 1
Unity | 502 | 1 | 1114 | 2 | 0 | BMS Communication Parameters 1 | Cell Voltage 77 | Float | mV |  | 0 | 1
Unity | 502 | 1 | 1116 | 2 | 0 | BMS Communication Parameters 1 | Cell Voltage 78 | Float | mV |  | 0 | 1
Unity | 502 | 1 | 1118 | 2 | 0 | BMS Communication Parameters 1 | Cell Voltage 79 | Float | mV |  | 0 | 1
Unity | 502 | 1 | 1120 | 2 | 0 | BMS Communication Parameters 1 | Cell Voltage 80 | Float | mV |  | 0 | 1
Unity | 502 | 1 | 1122 | 2 | 0 | BMS Communication Parameters 1 | Cell Voltage 81 | Float | mV |  | 0 | 1
Unity | 502 | 1 | 1124 | 2 | 0 | BMS Communication Parameters 1 | Cell Voltage 82 | Float | mV |  | 0 | 1
Unity | 502 | 1 | 1126 | 2 | 0 | BMS Communication Parameters 1 | Cell Voltage 83 | Float | mV |  | 0 | 1
Unity | 502 | 1 | 1128 | 2 | 0 | BMS Communication Parameters 1 | Cell Voltage 84 | Float | mV |  | 0 | 1
Unity | 502 | 1 | 1130 | 2 | 0 | BMS Communication Parameters 1 | Cell Voltage 85 | Float | mV |  | 0 | 1
Unity | 502 | 1 | 1132 | 2 | 0 | BMS Communication Parameters 1 | Cell Voltage 86 | Float | mV |  | 0 | 1
Unity | 502 | 1 | 1134 | 2 | 0 | BMS Communication Parameters 1 | Cell Voltage 87 | Float | mV |  | 0 | 1
Unity | 502 | 1 | 1136 | 2 | 0 | BMS Communication Parameters 1 | Cell Voltage 88 | Float | mV |  | 0 | 1
Unity | 502 | 1 | 1138 | 2 | 0 | BMS Communication Parameters 1 | Cell Voltage 89 | Float | mV |  | 0 | 1
Unity | 502 | 1 | 1140 | 2 | 0 | BMS Communication Parameters 1 | Cell Voltage 90 | Float | mV |  | 0 | 1
Unity | 502 | 1 | 1142 | 2 | 0 | BMS Communication Parameters 1 | Cell Voltage 91 | Float | mV |  | 0 | 1
Unity | 502 | 1 | 1144 | 2 | 0 | BMS Communication Parameters 1 | Cell Voltage 92 | Float | mV |  | 0 | 1
Unity | 502 | 1 | 1146 | 2 | 0 | BMS Communication Parameters 1 | Cell Voltage 93 | Float | mV |  | 0 | 1
Unity | 502 | 1 | 1148 | 2 | 0 | BMS Communication Parameters 1 | Cell Voltage 94 | Float | mV |  | 0 | 1
Unity | 502 | 1 | 1150 | 2 | 0 | BMS Communication Parameters 1 | Cell Voltage 95 | Float | mV |  | 0 | 1
Unity | 502 | 1 | 1152 | 2 | 0 | BMS Communication Parameters 1 | Cell Voltage 96 | Float | mV |  | 0 | 1
Unity | 502 | 1 | 1154 | 2 | 0 | BMS Communication Parameters 1 | Cell Voltage 97 | Float | mV |  | 0 | 1
Unity | 502 | 1 | 1156 | 2 | 0 | BMS Communication Parameters 1 | Cell Voltage 98 | Float | mV |  | 0 | 1
Unity | 502 | 1 | 1158 | 2 | 0 | BMS Communication Parameters 1 | Cell Voltage 99 | Float | mV |  | 0 | 1
Unity | 502 | 1 | 1160 | 2 | 0 | BMS Communication Parameters 1 | Cell Voltage 100 | Float | mV |  | 0 | 1
Unity | 502 | 1 | 1162 | 2 | 0 | BMS Communication Parameters 1 | Cell Voltage 101 | Float | mV |  | 0 | 1
Unity | 502 | 1 | 1164 | 2 | 0 | BMS Communication Parameters 1 | Cell Voltage 102 | Float | mV |  | 0 | 1
Unity | 502 | 1 | 1166 | 2 | 0 | BMS Communication Parameters 1 | Cell Voltage 103 | Float | mV |  | 0 | 1
Unity | 502 | 1 | 1168 | 2 | 0 | BMS Communication Parameters 1 | Cell Voltage 104 | Float | mV |  | 0 | 1
Unity | 502 | 1 | 1170 | 2 | 0 | BMS Communication Parameters 1 | Cell Voltage 105 | Float | mV |  | 0 | 1
Unity | 502 | 1 | 1172 | 2 | 0 | BMS Communication Parameters 1 | Cell Voltage 106 | Float | mV |  | 0 | 1
Unity | 502 | 1 | 1174 | 2 | 0 | BMS Communication Parameters 1 | Cell Voltage 107 | Float | mV |  | 0 | 1
Unity | 502 | 1 | 1176 | 2 | 0 | BMS Communication Parameters 1 | Cell Voltage 108 | Float | mV |  | 0 | 1
Unity | 502 | 1 | 1178 | 2 | 0 | BMS Communication Parameters 1 | Cell Voltage 109 | Float | mV |  | 0 | 1
Unity | 502 | 1 | 1180 | 2 | 0 | BMS Communication Parameters 1 | Cell Voltage 110 | Float | mV |  | 0 | 1
Unity | 502 | 1 | 1182 | 2 | 0 | BMS Communication Parameters 1 | Cell Voltage 111 | Float | mV |  | 0 | 1
Unity | 502 | 1 | 1184 | 2 | 0 | BMS Communication Parameters 1 | Cell Voltage 112 | Float | mV |  | 0 | 1
Unity | 502 | 1 | 1186 | 2 | 0 | BMS Communication Parameters 1 | Cell Voltage 113 | Float | mV |  | 0 | 1
Unity | 502 | 1 | 1188 | 2 | 0 | BMS Communication Parameters 1 | Cell Voltage 114 | Float | mV |  | 0 | 1
Unity | 502 | 1 | 1190 | 2 | 0 | BMS Communication Parameters 1 | Cell Voltage 115 | Float | mV |  | 0 | 1
Unity | 502 | 1 | 1192 | 2 | 0 | BMS Communication Parameters 1 | Cell Voltage 116 | Float | mV |  | 0 | 1
Unity | 502 | 1 | 1194 | 2 | 0 | BMS Communication Parameters 1 | Cell Voltage 117 | Float | mV |  | 0 | 1
Unity | 502 | 1 | 1196 | 2 | 0 | BMS Communication Parameters 1 | Cell Voltage 118 | Float | mV |  | 0 | 1
Unity | 502 | 1 | 1198 | 2 | 0 | BMS Communication Parameters 1 | Cell Voltage 119 | Float | mV |  | 0 | 1
Unity | 502 | 1 | 1200 | 2 | 0 | BMS Communication Parameters 1 | Cell Voltage 120 | Float | mV |  | 0 | 1
Unity | 502 | 1 | 1202 | 2 | 0 | BMS Communication Parameters 1 | Cell Voltage 121 | Float | mV |  | 0 | 1
Unity | 502 | 1 | 1204 | 2 | 0 | BMS Communication Parameters 1 | Cell Voltage 122 | Float | mV |  | 0 | 1
Unity | 502 | 1 | 1206 | 2 | 0 | BMS Communication Parameters 1 | Cell Voltage 123 | Float | mV |  | 0 | 1
Unity | 502 | 1 | 1208 | 2 | 0 | BMS Communication Parameters 1 | Cell Voltage 124 | Float | mV |  | 0 | 1
Unity | 502 | 1 | 1210 | 2 | 0 | BMS Communication Parameters 1 | Cell Voltage 125 | Float | mV |  | 0 | 1
Unity | 502 | 1 | 1212 | 2 | 0 | BMS Communication Parameters 1 | Cell Voltage 126 | Float | mV |  | 0 | 1
Unity | 502 | 1 | 1214 | 2 | 0 | BMS Communication Parameters 1 | Cell Voltage 127 | Float | mV |  | 0 | 1
Unity | 502 | 1 | 1216 | 2 | 0 | BMS Communication Parameters 1 | Cell Voltage 128 | Float | mV |  | 0 | 1
Unity | 502 | 1 | 1218 | 2 | 0 | BMS Communication Parameters 1 | Cell Voltage 129 | Float | mV |  | 0 | 1
Unity | 502 | 1 | 1220 | 2 | 0 | BMS Communication Parameters 1 | Cell Voltage 130 | Float | mV |  | 0 | 1
Unity | 502 | 1 | 1222 | 2 | 0 | BMS Communication Parameters 1 | Cell Voltage 131 | Float | mV |  | 0 | 1
Unity | 502 | 1 | 1224 | 2 | 0 | BMS Communication Parameters 1 | Cell Voltage 132 | Float | mV |  | 0 | 1
Unity | 502 | 1 | 1226 | 2 | 0 | BMS Communication Parameters 1 | Cell Voltage 133 | Float | mV |  | 0 | 1
Unity | 502 | 1 | 1228 | 2 | 0 | BMS Communication Parameters 1 | Cell Voltage 134 | Float | mV |  | 0 | 1
Unity | 502 | 1 | 1230 | 2 | 0 | BMS Communication Parameters 1 | Cell Voltage 135 | Float | mV |  | 0 | 1
Unity | 502 | 1 | 1232 | 2 | 0 | BMS Communication Parameters 1 | Cell Voltage 136 | Float | mV |  | 0 | 1
Unity | 502 | 1 | 1234 | 2 | 0 | BMS Communication Parameters 1 | Cell Voltage 137 | Float | mV |  | 0 | 1
Unity | 502 | 1 | 1236 | 2 | 0 | BMS Communication Parameters 1 | Cell Voltage 138 | Float | mV |  | 0 | 1
Unity | 502 | 1 | 1238 | 2 | 0 | BMS Communication Parameters 1 | Cell Voltage 139 | Float | mV |  | 0 | 1
Unity | 502 | 1 | 1240 | 2 | 0 | BMS Communication Parameters 1 | Cell Voltage 140 | Float | mV |  | 0 | 1
Unity | 502 | 1 | 1242 | 2 | 0 | BMS Communication Parameters 1 | Cell Voltage 141 | Float | mV |  | 0 | 1
Unity | 502 | 1 | 1244 | 2 | 0 | BMS Communication Parameters 1 | Cell Voltage 142 | Float | mV |  | 0 | 1
Unity | 502 | 1 | 1246 | 2 | 0 | BMS Communication Parameters 1 | Cell Voltage 143 | Float | mV |  | 0 | 1
Unity | 502 | 1 | 1248 | 2 | 0 | BMS Communication Parameters 1 | Cell Voltage 144 | Float | mV |  | 0 | 1
Unity | 502 | 1 | 1250 | 2 | 0 | BMS Communication Parameters 1 | Cell Voltage 145 | Float | mV |  | 0 | 1
Unity | 502 | 1 | 1252 | 2 | 0 | BMS Communication Parameters 1 | Cell Voltage 146 | Float | mV |  | 0 | 1
Unity | 502 | 1 | 1254 | 2 | 0 | BMS Communication Parameters 1 | Cell Voltage 147 | Float | mV |  | 0 | 1
Unity | 502 | 1 | 1256 | 2 | 0 | BMS Communication Parameters 1 | Cell Voltage 148 | Float | mV |  | 0 | 1
Unity | 502 | 1 | 1258 | 2 | 0 | BMS Communication Parameters 1 | Cell Voltage 149 | Float | mV |  | 0 | 1
Unity | 502 | 1 | 1260 | 2 | 0 | BMS Communication Parameters 1 | Cell Voltage 150 | Float | mV |  | 0 | 1
Unity | 502 | 1 | 1262 | 2 | 0 | BMS Communication Parameters 1 | Cell Voltage 151 | Float | mV |  | 0 | 1
Unity | 502 | 1 | 1264 | 2 | 0 | BMS Communication Parameters 1 | Cell Voltage 152 | Float | mV |  | 0 | 1
Unity | 502 | 1 | 1266 | 2 | 0 | BMS Communication Parameters 1 | Cell Voltage 153 | Float | mV |  | 0 | 1
Unity | 502 | 1 | 1268 | 2 | 0 | BMS Communication Parameters 1 | Cell Voltage 154 | Float | mV |  | 0 | 1
Unity | 502 | 1 | 1270 | 2 | 0 | BMS Communication Parameters 1 | Cell Voltage 155 | Float | mV |  | 0 | 1
Unity | 502 | 1 | 1272 | 2 | 0 | BMS Communication Parameters 1 | Cell Voltage 156 | Float | mV |  | 0 | 1
Unity | 502 | 1 | 1274 | 2 | 0 | BMS Communication Parameters 1 | Cell Voltage 157 | Float | mV |  | 0 | 1
Unity | 502 | 1 | 1276 | 2 | 0 | BMS Communication Parameters 1 | Cell Voltage 158 | Float | mV |  | 0 | 1
Unity | 502 | 1 | 1278 | 2 | 0 | BMS Communication Parameters 1 | Cell Voltage 159 | Float | mV |  | 0 | 1
Unity | 502 | 1 | 1280 | 2 | 0 | BMS Communication Parameters 1 | Cell Voltage 160 | Float | mV |  | 0 | 1
Unity | 502 | 1 | 1282 | 2 | 0 | BMS Communication Parameters 1 | Cell Voltage 161 | Float | mV |  | 0 | 1
Unity | 502 | 1 | 1284 | 2 | 0 | BMS Communication Parameters 1 | Cell Voltage 162 | Float | mV |  | 0 | 1
Unity | 502 | 1 | 1286 | 2 | 0 | BMS Communication Parameters 1 | Cell Voltage 163 | Float | mV |  | 0 | 1
Unity | 502 | 1 | 1288 | 2 | 0 | BMS Communication Parameters 1 | Cell Voltage 164 | Float | mV |  | 0 | 1
Unity | 502 | 1 | 1290 | 2 | 0 | BMS Communication Parameters 1 | Cell Voltage 165 | Float | mV |  | 0 | 1
Unity | 502 | 1 | 1292 | 2 | 0 | BMS Communication Parameters 1 | Cell Voltage 166 | Float | mV |  | 0 | 1
Unity | 502 | 1 | 1294 | 2 | 0 | BMS Communication Parameters 1 | Cell Voltage 167 | Float | mV |  | 0 | 1
Unity | 502 | 1 | 1296 | 2 | 0 | BMS Communication Parameters 1 | Cell Voltage 168 | Float | mV |  | 0 | 1
Unity | 502 | 1 | 1298 | 2 | 0 | BMS Communication Parameters 1 | Cell Voltage 169 | Float | mV |  | 0 | 1
Unity | 502 | 1 | 1300 | 2 | 0 | BMS Communication Parameters 1 | Cell Voltage 170 | Float | mV |  | 0 | 1
Unity | 502 | 1 | 1302 | 2 | 0 | BMS Communication Parameters 1 | Cell Voltage 171 | Float | mV |  | 0 | 1
Unity | 502 | 1 | 1304 | 2 | 0 | BMS Communication Parameters 1 | Cell Voltage 172 | Float | mV |  | 0 | 1
Unity | 502 | 1 | 1306 | 2 | 0 | BMS Communication Parameters 1 | Cell Voltage 173 | Float | mV |  | 0 | 1
Unity | 502 | 1 | 1308 | 2 | 0 | BMS Communication Parameters 1 | Cell Voltage 174 | Float | mV |  | 0 | 1
Unity | 502 | 1 | 1310 | 2 | 0 | BMS Communication Parameters 1 | Cell Voltage 175 | Float | mV |  | 0 | 1
Unity | 502 | 1 | 1312 | 2 | 0 | BMS Communication Parameters 1 | Cell Voltage 176 | Float | mV |  | 0 | 1
Unity | 502 | 1 | 1314 | 2 | 0 | BMS Communication Parameters 1 | Cell Voltage 177 | Float | mV |  | 0 | 1
Unity | 502 | 1 | 1316 | 2 | 0 | BMS Communication Parameters 1 | Cell Voltage 178 | Float | mV |  | 0 | 1
Unity | 502 | 1 | 1318 | 2 | 0 | BMS Communication Parameters 1 | Cell Voltage 179 | Float | mV |  | 0 | 1
Unity | 502 | 1 | 1320 | 2 | 0 | BMS Communication Parameters 1 | Cell Voltage 180 | Float | mV |  | 0 | 1
Unity | 502 | 1 | 1322 | 2 | 0 | BMS Communication Parameters 1 | Cell Voltage 181 | Float | mV |  | 0 | 1
Unity | 502 | 1 | 1324 | 2 | 0 | BMS Communication Parameters 1 | Cell Voltage 182 | Float | mV |  | 0 | 1
Unity | 502 | 1 | 1326 | 2 | 0 | BMS Communication Parameters 1 | Cell Voltage 183 | Float | mV |  | 0 | 1
Unity | 502 | 1 | 1328 | 2 | 0 | BMS Communication Parameters 1 | Cell Voltage 184 | Float | mV |  | 0 | 1
Unity | 502 | 1 | 1330 | 2 | 0 | BMS Communication Parameters 1 | Cell Voltage 185 | Float | mV |  | 0 | 1
Unity | 502 | 1 | 1332 | 2 | 0 | BMS Communication Parameters 1 | Cell Voltage 186 | Float | mV |  | 0 | 1
Unity | 502 | 1 | 1334 | 2 | 0 | BMS Communication Parameters 1 | Cell Voltage 187 | Float | mV |  | 0 | 1
Unity | 502 | 1 | 1336 | 2 | 0 | BMS Communication Parameters 1 | Cell Voltage 188 | Float | mV |  | 0 | 1
Unity | 502 | 1 | 1338 | 2 | 0 | BMS Communication Parameters 1 | Cell Voltage 189 | Float | mV |  | 0 | 1
Unity | 502 | 1 | 1340 | 2 | 0 | BMS Communication Parameters 1 | Cell Voltage 190 | Float | mV |  | 0 | 1
Unity | 502 | 1 | 1342 | 2 | 0 | BMS Communication Parameters 1 | Cell Voltage 191 | Float | mV |  | 0 | 1
Unity | 502 | 1 | 1344 | 2 | 0 | BMS Communication Parameters 1 | Cell Voltage 192 | Float | mV |  | 0 | 1
Unity | 502 | 1 | 1346 | 2 | 0 | BMS Communication Parameters 1 | Cell Voltage 193 | Float | mV |  | 0 | 1
Unity | 502 | 1 | 1348 | 2 | 0 | BMS Communication Parameters 1 | Cell Voltage 194 | Float | mV |  | 0 | 1
Unity | 502 | 1 | 1350 | 2 | 0 | BMS Communication Parameters 1 | Cell Voltage 195 | Float | mV |  | 0 | 1
Unity | 502 | 1 | 1352 | 2 | 0 | BMS Communication Parameters 1 | Cell Voltage 196 | Float | mV |  | 0 | 1
Unity | 502 | 1 | 1354 | 2 | 0 | BMS Communication Parameters 1 | Cell Voltage 197 | Float | mV |  | 0 | 1
Unity | 502 | 1 | 1356 | 2 | 0 | BMS Communication Parameters 1 | Cell Voltage 198 | Float | mV |  | 0 | 1
Unity | 502 | 1 | 1358 | 2 | 0 | BMS Communication Parameters 1 | Cell Voltage 199 | Float | mV |  | 0 | 1
Unity | 502 | 1 | 1360 | 2 | 0 | BMS Communication Parameters 1 | Cell Voltage 200 | Float | mV |  | 0 | 1
Unity | 502 | 1 | 1362 | 2 | 0 | BMS Communication Parameters 1 | Cell Voltage 201 | Float | mV |  | 0 | 1
Unity | 502 | 1 | 1364 | 2 | 0 | BMS Communication Parameters 1 | Cell Voltage 202 | Float | mV |  | 0 | 1
Unity | 502 | 1 | 1366 | 2 | 0 | BMS Communication Parameters 1 | Cell Voltage 203 | Float | mV |  | 0 | 1
Unity | 502 | 1 | 1368 | 2 | 0 | BMS Communication Parameters 1 | Cell Voltage 204 | Float | mV |  | 0 | 1
Unity | 502 | 1 | 1370 | 2 | 0 | BMS Communication Parameters 1 | Cell Voltage 205 | Float | mV |  | 0 | 1
Unity | 502 | 1 | 1372 | 2 | 0 | BMS Communication Parameters 1 | Cell Voltage 206 | Float | mV |  | 0 | 1
Unity | 502 | 1 | 1374 | 2 | 0 | BMS Communication Parameters 1 | Cell Voltage 207 | Float | mV |  | 0 | 1
Unity | 502 | 1 | 1376 | 2 | 0 | BMS Communication Parameters 1 | Cell Voltage 208 | Float | mV |  | 0 | 1
Unity | 502 | 1 | 1378 | 2 | 0 | BMS Communication Parameters 1 | Cell Voltage 209 | Float | mV |  | 0 | 1
Unity | 502 | 1 | 1380 | 2 | 0 | BMS Communication Parameters 1 | Cell Voltage 210 | Float | mV |  | 0 | 1
Unity | 502 | 1 | 1382 | 2 | 0 | BMS Communication Parameters 1 | Cell Voltage 211 | Float | mV |  | 0 | 1
Unity | 502 | 1 | 1384 | 2 | 0 | BMS Communication Parameters 1 | Cell Voltage 212 | Float | mV |  | 0 | 1
Unity | 502 | 1 | 1386 | 2 | 0 | BMS Communication Parameters 1 | Cell Voltage 213 | Float | mV |  | 0 | 1
Unity | 502 | 1 | 1388 | 2 | 0 | BMS Communication Parameters 1 | Cell Voltage 214 | Float | mV |  | 0 | 1
Unity | 502 | 1 | 1390 | 2 | 0 | BMS Communication Parameters 1 | Cell Voltage 215 | Float | mV |  | 0 | 1
Unity | 502 | 1 | 1392 | 2 | 0 | BMS Communication Parameters 1 | Cell Voltage 216 | Float | mV |  | 0 | 1
Unity | 502 | 1 | 1394 | 2 | 0 | BMS Communication Parameters 1 | Cell Voltage 217 | Float | mV |  | 0 | 1
Unity | 502 | 1 | 1396 | 2 | 0 | BMS Communication Parameters 1 | Cell Voltage 218 | Float | mV |  | 0 | 1
Unity | 502 | 1 | 1398 | 2 | 0 | BMS Communication Parameters 1 | Cell Voltage 219 | Float | mV |  | 0 | 1
Unity | 502 | 1 | 1400 | 2 | 0 | BMS Communication Parameters 1 | Cell Voltage 220 | Float | mV |  | 0 | 1
Unity | 502 | 1 | 1402 | 2 | 0 | BMS Communication Parameters 1 | Cell Voltage 221 | Float | mV |  | 0 | 1
Unity | 502 | 1 | 1404 | 2 | 0 | BMS Communication Parameters 1 | Cell Voltage 222 | Float | mV |  | 0 | 1
Unity | 502 | 1 | 1406 | 2 | 0 | BMS Communication Parameters 1 | Cell Voltage 223 | Float | mV |  | 0 | 1
Unity | 502 | 1 | 1408 | 2 | 0 | BMS Communication Parameters 1 | Cell Voltage 224 | Float | mV |  | 0 | 1
Unity | 502 | 1 | 1410 | 2 | 0 | BMS Communication Parameters 1 | Cell Voltage 225 | Float | mV |  | 0 | 1
Unity | 502 | 1 | 1412 | 2 | 0 | BMS Communication Parameters 1 | Cell Voltage 226 | Float | mV |  | 0 | 1
Unity | 502 | 1 | 1414 | 2 | 0 | BMS Communication Parameters 1 | Cell Voltage 227 | Float | mV |  | 0 | 1
Unity | 502 | 1 | 1416 | 2 | 0 | BMS Communication Parameters 1 | Cell Voltage 228 | Float | mV |  | 0 | 1
Unity | 502 | 1 | 1418 | 2 | 0 | BMS Communication Parameters 1 | Cell Voltage 229 | Float | mV |  | 0 | 1
Unity | 502 | 1 | 1420 | 2 | 0 | BMS Communication Parameters 1 | Cell Voltage 230 | Float | mV |  | 0 | 1
Unity | 502 | 1 | 1422 | 2 | 0 | BMS Communication Parameters 1 | Cell Voltage 231 | Float | mV |  | 0 | 1
Unity | 502 | 1 | 1424 | 2 | 0 | BMS Communication Parameters 1 | Cell Voltage 232 | Float | mV |  | 0 | 1
Unity | 502 | 1 | 1426 | 2 | 0 | BMS Communication Parameters 1 | Cell Voltage 233 | Float | mV |  | 0 | 1
Unity | 502 | 1 | 1428 | 2 | 0 | BMS Communication Parameters 1 | Cell Voltage 234 | Float | mV |  | 0 | 1
Unity | 502 | 1 | 1430 | 2 | 0 | BMS Communication Parameters 1 | Cell Voltage 235 | Float | mV |  | 0 | 1
Unity | 502 | 1 | 1432 | 2 | 0 | BMS Communication Parameters 1 | Cell Voltage 236 | Float | mV |  | 0 | 1
Unity | 502 | 1 | 1434 | 2 | 0 | BMS Communication Parameters 1 | Cell Voltage 237 | Float | mV |  | 0 | 1
Unity | 502 | 1 | 1436 | 2 | 0 | BMS Communication Parameters 1 | Cell Voltage 238 | Float | mV |  | 0 | 1
Unity | 502 | 1 | 1438 | 2 | 0 | BMS Communication Parameters 1 | Cell Voltage 239 | Float | mV |  | 0 | 1
Unity | 502 | 1 | 1440 | 2 | 0 | BMS Communication Parameters 1 | Cell Voltage 240 | Float | mV |  | 0 | 1
Unity | 502 | 1 | 1442 | 2 | 0 | BMS Communication Parameters 1 | Cell Voltage 241 | Float | mV |  | 0 | 1
Unity | 502 | 1 | 1444 | 2 | 0 | BMS Communication Parameters 1 | Cell Voltage 242 | Float | mV |  | 0 | 1
Unity | 502 | 1 | 1446 | 2 | 0 | BMS Communication Parameters 1 | Cell Voltage 243 | Float | mV |  | 0 | 1
Unity | 502 | 1 | 1448 | 2 | 0 | BMS Communication Parameters 1 | Cell Voltage 244 | Float | mV |  | 0 | 1
Unity | 502 | 1 | 1450 | 2 | 0 | BMS Communication Parameters 1 | Cell Voltage 245 | Float | mV |  | 0 | 1
Unity | 502 | 1 | 1452 | 2 | 0 | BMS Communication Parameters 1 | Cell Voltage 246 | Float | mV |  | 0 | 1
Unity | 502 | 1 | 1454 | 2 | 0 | BMS Communication Parameters 1 | Cell Voltage 247 | Float | mV |  | 0 | 1
Unity | 502 | 1 | 1456 | 2 | 0 | BMS Communication Parameters 1 | Cell Voltage 248 | Float | mV |  | 0 | 1
Unity | 502 | 1 | 1458 | 2 | 0 | BMS Communication Parameters 1 | Cell Voltage 249 | Float | mV |  | 0 | 1
Unity | 502 | 1 | 1460 | 2 | 0 | BMS Communication Parameters 1 | Cell Voltage 250 | Float | mV |  | 0 | 1
Unity | 502 | 1 | 1462 | 2 | 0 | BMS Communication Parameters 1 | Cell Voltage 251 | Float | mV |  | 0 | 1
Unity | 502 | 1 | 1464 | 2 | 0 | BMS Communication Parameters 1 | Cell Voltage 252 | Float | mV |  | 0 | 1
Unity | 502 | 1 | 1466 | 2 | 0 | BMS Communication Parameters 1 | Cell Voltage 253 | Float | mV |  | 0 | 1
Unity | 502 | 1 | 1468 | 2 | 0 | BMS Communication Parameters 1 | Cell Voltage 254 | Float | mV |  | 0 | 1
Unity | 502 | 1 | 1470 | 2 | 0 | BMS Communication Parameters 1 | Cell Voltage 255 | Float | mV |  | 0 | 1
Unity | 502 | 1 | 1472 | 2 | 0 | BMS Communication Parameters 1 | Cell Voltage 256 | Float | mV |  | 0 | 1
Unity | 502 | 1 | 1474 | 2 | 0 | BMS Communication Parameters 1 | Cell Voltage 257 | Float | mV |  | 0 | 1
Unity | 502 | 1 | 1476 | 2 | 0 | BMS Communication Parameters 1 | Cell Voltage 258 | Float | mV |  | 0 | 1
Unity | 502 | 1 | 1478 | 2 | 0 | BMS Communication Parameters 1 | Cell Voltage 259 | Float | mV |  | 0 | 1
Unity | 502 | 1 | 1480 | 2 | 0 | BMS Communication Parameters 1 | Cell Voltage 260 | Float | mV |  | 0 | 1
Unity | 502 | 1 | 1482 | 2 | 0 | BMS Communication Parameters 1 | Battery Temperature 1 | Float | ℃ |  | 0 | 1
Unity | 502 | 1 | 1484 | 2 | 0 | BMS Communication Parameters 1 | Battery Temperature 2 | Float | ℃ |  | 0 | 1
Unity | 502 | 1 | 1486 | 2 | 0 | BMS Communication Parameters 1 | Battery Temperature 3 | Float | ℃ |  | 0 | 1
Unity | 502 | 1 | 1488 | 2 | 0 | BMS Communication Parameters 1 | Battery Temperature 4 | Float | ℃ |  | 0 | 1
Unity | 502 | 1 | 1490 | 2 | 0 | BMS Communication Parameters 1 | Battery Temperature 5 | Float | ℃ |  | 0 | 1
Unity | 502 | 1 | 1492 | 2 | 0 | BMS Communication Parameters 1 | Battery Temperature 6 | Float | ℃ |  | 0 | 1
Unity | 502 | 1 | 1494 | 2 | 0 | BMS Communication Parameters 1 | Battery Temperature 7 | Float | ℃ |  | 0 | 1
Unity | 502 | 1 | 1496 | 2 | 0 | BMS Communication Parameters 1 | Battery Temperature 8 | Float | ℃ |  | 0 | 1
Unity | 502 | 1 | 1498 | 2 | 0 | BMS Communication Parameters 1 | Battery Temperature 9 | Float | ℃ |  | 0 | 1
Unity | 502 | 1 | 1500 | 2 | 0 | BMS Communication Parameters 1 | Battery Temperature 10 | Float | ℃ |  | 0 | 1
Unity | 502 | 1 | 1502 | 2 | 0 | BMS Communication Parameters 1 | Battery Temperature 11 | Float | ℃ |  | 0 | 1
Unity | 502 | 1 | 1504 | 2 | 0 | BMS Communication Parameters 1 | Battery Temperature 12 | Float | ℃ |  | 0 | 1
Unity | 502 | 1 | 1506 | 2 | 0 | BMS Communication Parameters 1 | Battery Temperature 13 | Float | ℃ |  | 0 | 1
Unity | 502 | 1 | 1508 | 2 | 0 | BMS Communication Parameters 1 | Battery Temperature 14 | Float | ℃ |  | 0 | 1
Unity | 502 | 1 | 1510 | 2 | 0 | BMS Communication Parameters 1 | Battery Temperature 15 | Float | ℃ |  | 0 | 1
Unity | 502 | 1 | 1512 | 2 | 0 | BMS Communication Parameters 1 | Battery Temperature 16 | Float | ℃ |  | 0 | 1
Unity | 502 | 1 | 1514 | 2 | 0 | BMS Communication Parameters 1 | Battery Temperature 17 | Float | ℃ |  | 0 | 1
Unity | 502 | 1 | 1516 | 2 | 0 | BMS Communication Parameters 1 | Battery Temperature 18 | Float | ℃ |  | 0 | 1
Unity | 502 | 1 | 1518 | 2 | 0 | BMS Communication Parameters 1 | Battery Temperature 19 | Float | ℃ |  | 0 | 1
Unity | 502 | 1 | 1520 | 2 | 0 | BMS Communication Parameters 1 | Battery Temperature 20 | Float | ℃ |  | 0 | 1
Unity | 502 | 1 | 1522 | 2 | 0 | BMS Communication Parameters 1 | Battery Temperature 21 | Float | ℃ |  | 0 | 1
Unity | 502 | 1 | 1524 | 2 | 0 | BMS Communication Parameters 1 | Battery Temperature 22 | Float | ℃ |  | 0 | 1
Unity | 502 | 1 | 1526 | 2 | 0 | BMS Communication Parameters 1 | Battery Temperature 23 | Float | ℃ |  | 0 | 1
Unity | 502 | 1 | 1528 | 2 | 0 | BMS Communication Parameters 1 | Battery Temperature 24 | Float | ℃ |  | 0 | 1
Unity | 502 | 1 | 1530 | 2 | 0 | BMS Communication Parameters 1 | Battery Temperature 25 | Float | ℃ |  | 0 | 1
Unity | 502 | 1 | 1532 | 2 | 0 | BMS Communication Parameters 1 | Battery Temperature 26 | Float | ℃ |  | 0 | 1
Unity | 502 | 1 | 1534 | 2 | 0 | BMS Communication Parameters 1 | Battery Temperature 27 | Float | ℃ |  | 0 | 1
Unity | 502 | 1 | 1536 | 2 | 0 | BMS Communication Parameters 1 | Battery Temperature 28 | Float | ℃ |  | 0 | 1
Unity | 502 | 1 | 1538 | 2 | 0 | BMS Communication Parameters 1 | Battery Temperature 29 | Float | ℃ |  | 0 | 1
Unity | 502 | 1 | 1540 | 2 | 0 | BMS Communication Parameters 1 | Battery Temperature 30 | Float | ℃ |  | 0 | 1
Unity | 502 | 1 | 1542 | 2 | 0 | BMS Communication Parameters 1 | Battery Temperature 31 | Float | ℃ |  | 0 | 1
Unity | 502 | 1 | 1544 | 2 | 0 | BMS Communication Parameters 1 | Battery Temperature 32 | Float | ℃ |  | 0 | 1
Unity | 502 | 1 | 1546 | 2 | 0 | BMS Communication Parameters 1 | Battery Temperature 33 | Float | ℃ |  | 0 | 1
Unity | 502 | 1 | 1548 | 2 | 0 | BMS Communication Parameters 1 | Battery Temperature 34 | Float | ℃ |  | 0 | 1
Unity | 502 | 1 | 1550 | 2 | 0 | BMS Communication Parameters 1 | Battery Temperature 35 | Float | ℃ |  | 0 | 1
Unity | 502 | 1 | 1552 | 2 | 0 | BMS Communication Parameters 1 | Battery Temperature 36 | Float | ℃ |  | 0 | 1
Unity | 502 | 1 | 1554 | 2 | 0 | BMS Communication Parameters 1 | Battery Temperature 37 | Float | ℃ |  | 0 | 1
Unity | 502 | 1 | 1556 | 2 | 0 | BMS Communication Parameters 1 | Battery Temperature 38 | Float | ℃ |  | 0 | 1
Unity | 502 | 1 | 1558 | 2 | 0 | BMS Communication Parameters 1 | Battery Temperature 39 | Float | ℃ |  | 0 | 1
Unity | 502 | 1 | 1560 | 2 | 0 | BMS Communication Parameters 1 | Battery Temperature 40 | Float | ℃ |  | 0 | 1
Unity | 502 | 1 | 1562 | 2 | 0 | BMS Communication Parameters 1 | Battery Temperature 41 | Float | ℃ |  | 0 | 1
Unity | 502 | 1 | 1564 | 2 | 0 | BMS Communication Parameters 1 | Battery Temperature 42 | Float | ℃ |  | 0 | 1
Unity | 502 | 1 | 1566 | 2 | 0 | BMS Communication Parameters 1 | Battery Temperature 43 | Float | ℃ |  | 0 | 1
Unity | 502 | 1 | 1568 | 2 | 0 | BMS Communication Parameters 1 | Battery Temperature 44 | Float | ℃ |  | 0 | 1
Unity | 502 | 1 | 1570 | 2 | 0 | BMS Communication Parameters 1 | Battery Temperature 45 | Float | ℃ |  | 0 | 1
Unity | 502 | 1 | 1572 | 2 | 0 | BMS Communication Parameters 1 | Battery Temperature 46 | Float | ℃ |  | 0 | 1
Unity | 502 | 1 | 1574 | 2 | 0 | BMS Communication Parameters 1 | Battery Temperature 47 | Float | ℃ |  | 0 | 1
Unity | 502 | 1 | 1576 | 2 | 0 | BMS Communication Parameters 1 | Battery Temperature 48 | Float | ℃ |  | 0 | 1
Unity | 502 | 1 | 1578 | 2 | 0 | BMS Communication Parameters 1 | Battery Temperature 49 | Float | ℃ |  | 0 | 1
Unity | 502 | 1 | 1580 | 2 | 0 | BMS Communication Parameters 1 | Battery Temperature 50 | Float | ℃ |  | 0 | 1
Unity | 502 | 1 | 1582 | 2 | 0 | BMS Communication Parameters 1 | Battery Temperature 51 | Float | ℃ |  | 0 | 1
Unity | 502 | 1 | 1584 | 2 | 0 | BMS Communication Parameters 1 | Battery Temperature 52 | Float | ℃ |  | 0 | 1
Unity | 502 | 1 | 1586 | 2 | 0 | BMS Communication Parameters 1 | Battery Temperature 53 | Float | ℃ |  | 0 | 1
Unity | 502 | 1 | 1588 | 2 | 0 | BMS Communication Parameters 1 | Battery Temperature 54 | Float | ℃ |  | 0 | 1
Unity | 502 | 1 | 1590 | 2 | 0 | BMS Communication Parameters 1 | Battery Temperature 55 | Float | ℃ |  | 0 | 1
Unity | 502 | 1 | 1592 | 2 | 0 | BMS Communication Parameters 1 | Battery Temperature 56 | Float | ℃ |  | 0 | 1
Unity | 502 | 1 | 1594 | 2 | 0 | BMS Communication Parameters 1 | Battery Temperature 57 | Float | ℃ |  | 0 | 1
Unity | 502 | 1 | 1596 | 2 | 0 | BMS Communication Parameters 1 | Battery Temperature 58 | Float | ℃ |  | 0 | 1
Unity | 502 | 1 | 1598 | 2 | 0 | BMS Communication Parameters 1 | Battery Temperature 59 | Float | ℃ |  | 0 | 1
Unity | 502 | 1 | 1600 | 2 | 0 | BMS Communication Parameters 1 | Battery Temperature 60 | Float | ℃ |  | 0 | 1
Unity | 502 | 1 | 1602 | 2 | 0 | BMS Communication Parameters 1 | Battery Temperature 61 | Float | ℃ |  | 0 | 1
Unity | 502 | 1 | 1604 | 2 | 0 | BMS Communication Parameters 1 | Battery Temperature 62 | Float | ℃ |  | 0 | 1
Unity | 502 | 1 | 1606 | 2 | 0 | BMS Communication Parameters 1 | Battery Temperature 63 | Float | ℃ |  | 0 | 1
Unity | 502 | 1 | 1608 | 2 | 0 | BMS Communication Parameters 1 | Battery Temperature 64 | Float | ℃ |  | 0 | 1
Unity | 502 | 1 | 1610 | 2 | 0 | BMS Communication Parameters 1 | Battery Temperature 65 | Float | ℃ |  | 0 | 1
Unity | 502 | 1 | 1612 | 2 | 0 | BMS Communication Parameters 1 | Battery Temperature 66 | Float | ℃ |  | 0 | 1
Unity | 502 | 1 | 1614 | 2 | 0 | BMS Communication Parameters 1 | Battery Temperature 67 | Float | ℃ |  | 0 | 1
Unity | 502 | 1 | 1616 | 2 | 0 | BMS Communication Parameters 1 | Battery Temperature 68 | Float | ℃ |  | 0 | 1
Unity | 502 | 1 | 1618 | 2 | 0 | BMS Communication Parameters 1 | Battery Temperature 69 | Float | ℃ |  | 0 | 1
Unity | 502 | 1 | 1620 | 2 | 0 | BMS Communication Parameters 1 | Battery Temperature 70 | Float | ℃ |  | 0 | 1
Unity | 502 | 1 | 1622 | 2 | 0 | BMS Communication Parameters 1 | Battery Temperature 71 | Float | ℃ |  | 0 | 1
Unity | 502 | 1 | 1624 | 2 | 0 | BMS Communication Parameters 1 | Battery Temperature 72 | Float | ℃ |  | 0 | 1
Unity | 502 | 1 | 1626 | 2 | 0 | BMS Communication Parameters 1 | Battery Temperature 73 | Float | ℃ |  | 0 | 1
Unity | 502 | 1 | 1628 | 2 | 0 | BMS Communication Parameters 1 | Battery Temperature 74 | Float | ℃ |  | 0 | 1
Unity | 502 | 1 | 1630 | 2 | 0 | BMS Communication Parameters 1 | Battery Temperature 75 | Float | ℃ |  | 0 | 1
Unity | 502 | 1 | 1632 | 2 | 0 | BMS Communication Parameters 1 | Battery Temperature 76 | Float | ℃ |  | 0 | 1
Unity | 502 | 1 | 1634 | 2 | 0 | BMS Communication Parameters 1 | Battery Temperature 77 | Float | ℃ |  | 0 | 1
Unity | 502 | 1 | 1636 | 2 | 0 | BMS Communication Parameters 1 | Battery Temperature 78 | Float | ℃ |  | 0 | 1
Unity | 502 | 1 | 1638 | 2 | 0 | BMS Communication Parameters 1 | Battery Temperature 79 | Float | ℃ |  | 0 | 1
Unity | 502 | 1 | 1640 | 2 | 0 | BMS Communication Parameters 1 | Battery Temperature 80 | Float | ℃ |  | 0 | 1
Unity | 502 | 1 | 1642 | 2 | 0 | BMS Communication Parameters 1 | Battery Temperature 81 | Float | ℃ |  | 0 | 1
Unity | 502 | 1 | 1644 | 2 | 0 | BMS Communication Parameters 1 | Battery Temperature 82 | Float | ℃ |  | 0 | 1
Unity | 502 | 1 | 1646 | 2 | 0 | BMS Communication Parameters 1 | Battery Temperature 83 | Float | ℃ |  | 0 | 1
Unity | 502 | 1 | 1648 | 2 | 0 | BMS Communication Parameters 1 | Battery Temperature 84 | Float | ℃ |  | 0 | 1
Unity | 502 | 1 | 1650 | 2 | 0 | BMS Communication Parameters 1 | Battery Temperature 85 | Float | ℃ |  | 0 | 1
Unity | 502 | 1 | 1652 | 2 | 0 | BMS Communication Parameters 1 | Battery Temperature 86 | Float | ℃ |  | 0 | 1
Unity | 502 | 1 | 1654 | 2 | 0 | BMS Communication Parameters 1 | Battery Temperature 87 | Float | ℃ |  | 0 | 1
Unity | 502 | 1 | 1656 | 2 | 0 | BMS Communication Parameters 1 | Battery Temperature 88 | Float | ℃ |  | 0 | 1
Unity | 502 | 1 | 1658 | 2 | 0 | BMS Communication Parameters 1 | Battery Temperature 89 | Float | ℃ |  | 0 | 1
Unity | 502 | 1 | 1660 | 2 | 0 | BMS Communication Parameters 1 | Battery Temperature 90 | Float | ℃ |  | 0 | 1
Unity | 502 | 1 | 1662 | 2 | 0 | BMS Communication Parameters 1 | Battery Temperature 91 | Float | ℃ |  | 0 | 1
Unity | 502 | 1 | 1664 | 2 | 0 | BMS Communication Parameters 1 | Battery Temperature 92 | Float | ℃ |  | 0 | 1
Unity | 502 | 1 | 1666 | 2 | 0 | BMS Communication Parameters 1 | Battery Temperature 93 | Float | ℃ |  | 0 | 1
Unity | 502 | 1 | 1668 | 2 | 0 | BMS Communication Parameters 1 | Battery Temperature 94 | Float | ℃ |  | 0 | 1
Unity | 502 | 1 | 1670 | 2 | 0 | BMS Communication Parameters 1 | Battery Temperature 95 | Float | ℃ |  | 0 | 1
Unity | 502 | 1 | 1672 | 2 | 0 | BMS Communication Parameters 1 | Battery Temperature 96 | Float | ℃ |  | 0 | 1
Unity | 502 | 1 | 1674 | 2 | 0 | BMS Communication Parameters 1 | Battery Temperature 97 | Float | ℃ |  | 0 | 1
Unity | 502 | 1 | 1676 | 2 | 0 | BMS Communication Parameters 1 | Battery Temperature 98 | Float | ℃ |  | 0 | 1
Unity | 502 | 1 | 1678 | 2 | 0 | BMS Communication Parameters 1 | Battery Temperature 99 | Float | ℃ |  | 0 | 1
Unity | 502 | 1 | 1680 | 2 | 0 | BMS Communication Parameters 1 | Battery Temperature 100 | Float | ℃ |  | 0 | 1
Unity | 502 | 1 | 1682 | 2 | 0 | BMS Communication Parameters 1 | Battery Temperature 101 | Float | ℃ |  | 0 | 1
Unity | 502 | 1 | 1684 | 2 | 0 | BMS Communication Parameters 1 | Battery Temperature 102 | Float | ℃ |  | 0 | 1
Unity | 502 | 1 | 1686 | 2 | 0 | BMS Communication Parameters 1 | Battery Temperature 103 | Float | ℃ |  | 0 | 1
Unity | 502 | 1 | 1688 | 2 | 0 | BMS Communication Parameters 1 | Battery Temperature 104 | Float | ℃ |  | 0 | 1
Unity | 502 | 1 | 1690 | 2 | 0 | BMS Communication Parameters 1 | Battery Temperature 105 | Float | ℃ |  | 0 | 1
Unity | 502 | 1 | 1692 | 2 | 0 | BMS Communication Parameters 1 | Battery Temperature 106 | Float | ℃ |  | 0 | 1
Unity | 502 | 1 | 1694 | 2 | 0 | BMS Communication Parameters 1 | Battery Temperature 107 | Float | ℃ |  | 0 | 1
Unity | 502 | 1 | 1696 | 2 | 0 | BMS Communication Parameters 1 | Battery Temperature 108 | Float | ℃ |  | 0 | 1
Unity | 502 | 1 | 1698 | 2 | 0 | BMS Communication Parameters 1 | Battery Temperature 109 | Float | ℃ |  | 0 | 1
Unity | 502 | 1 | 1700 | 2 | 0 | BMS Communication Parameters 1 | Battery Temperature 110 | Float | ℃ |  | 0 | 1
Unity | 502 | 1 | 1702 | 2 | 0 | BMS Communication Parameters 1 | Battery Temperature 111 | Float | ℃ |  | 0 | 1
Unity | 502 | 1 | 1704 | 2 | 0 | BMS Communication Parameters 1 | Battery Temperature 112 | Float | ℃ |  | 0 | 1
Unity | 502 | 1 | 1706 | 2 | 0 | BMS Communication Parameters 1 | Battery Temperature 113 | Float | ℃ |  | 0 | 1
Unity | 502 | 1 | 1708 | 2 | 0 | BMS Communication Parameters 1 | Battery Temperature 114 | Float | ℃ |  | 0 | 1
Unity | 502 | 1 | 1710 | 2 | 0 | BMS Communication Parameters 1 | Battery Temperature 115 | Float | ℃ |  | 0 | 1
Unity | 502 | 1 | 1712 | 2 | 0 | BMS Communication Parameters 1 | Battery Temperature 116 | Float | ℃ |  | 0 | 1
Unity | 502 | 1 | 1714 | 2 | 0 | BMS Communication Parameters 1 | Battery Temperature 117 | Float | ℃ |  | 0 | 1
Unity | 502 | 1 | 1716 | 2 | 0 | BMS Communication Parameters 1 | Battery Temperature 118 | Float | ℃ |  | 0 | 1
Unity | 502 | 1 | 1718 | 2 | 0 | BMS Communication Parameters 1 | Battery Temperature 119 | Float | ℃ |  | 0 | 1
Unity | 502 | 1 | 1720 | 2 | 0 | BMS Communication Parameters 1 | Battery Temperature 120 | Float | ℃ |  | 0 | 1
Unity | 502 | 1 | 1722 | 2 | 0 | BMS Communication Parameters 1 | Battery Temperature 121 | Float | ℃ |  | 0 | 1
Unity | 502 | 1 | 1724 | 2 | 0 | BMS Communication Parameters 1 | Battery Temperature 122 | Float | ℃ |  | 0 | 1
Unity | 502 | 1 | 1726 | 2 | 0 | BMS Communication Parameters 1 | Battery Temperature 123 | Float | ℃ |  | 0 | 1
Unity | 502 | 1 | 1728 | 2 | 0 | BMS Communication Parameters 1 | Battery Temperature 124 | Float | ℃ |  | 0 | 1
Unity | 502 | 1 | 1730 | 2 | 0 | BMS Communication Parameters 1 | Battery Temperature 125 | Float | ℃ |  | 0 | 1
Unity | 502 | 1 | 1732 | 2 | 0 | BMS Communication Parameters 1 | Battery Temperature 126 | Float | ℃ |  | 0 | 1
Unity | 502 | 1 | 1734 | 2 | 0 | BMS Communication Parameters 1 | Battery Temperature 127 | Float | ℃ |  | 0 | 1
Unity | 502 | 1 | 1736 | 2 | 0 | BMS Communication Parameters 1 | Battery Temperature 128 | Float | ℃ |  | 0 | 1
Unity | 502 | 1 | 1738 | 2 | 0 | BMS Communication Parameters 1 | Battery Temperature 129 | Float | ℃ |  | 0 | 1
Unity | 502 | 1 | 1740 | 2 | 0 | BMS Communication Parameters 1 | Battery Temperature 130 | Float | ℃ |  | 0 | 1
Unity | 502 | 1 | 1742 | 2 | 0 | BMS Communication Parameters 1 | Battery Temperature 131 | Float | ℃ |  | 0 | 1
Unity | 502 | 1 | 1744 | 2 | 0 | BMS Communication Parameters 1 | Battery Temperature 132 | Float | ℃ |  | 0 | 1
Unity | 502 | 1 | 1746 | 2 | 0 | BMS Communication Parameters 1 | Battery Temperature 133 | Float | ℃ |  | 0 | 1
Unity | 502 | 1 | 1748 | 2 | 0 | BMS Communication Parameters 1 | Battery Temperature 134 | Float | ℃ |  | 0 | 1
Unity | 502 | 1 | 1750 | 2 | 0 | BMS Communication Parameters 1 | Battery Temperature 135 | Float | ℃ |  | 0 | 1
Unity | 502 | 1 | 1752 | 2 | 0 | BMS Communication Parameters 1 | Battery Temperature 136 | Float | ℃ |  | 0 | 1
Unity | 502 | 1 | 1754 | 2 | 0 | BMS Communication Parameters 1 | Battery Temperature 137 | Float | ℃ |  | 0 | 1
Unity | 502 | 1 | 1756 | 2 | 0 | BMS Communication Parameters 1 | Battery Temperature 138 | Float | ℃ |  | 0 | 1
Unity | 502 | 1 | 1758 | 2 | 0 | BMS Communication Parameters 1 | Battery Temperature 139 | Float | ℃ |  | 0 | 1
Unity | 502 | 1 | 1760 | 2 | 0 | BMS Communication Parameters 1 | Battery Temperature 140 | Float | ℃ |  | 0 | 1
Unity | 502 | 1 | 1762 | 2 | 0 | BMS Communication Parameters 1 | Battery Temperature 141 | Float | ℃ |  | 0 | 1
Unity | 502 | 1 | 1764 | 2 | 0 | BMS Communication Parameters 1 | Battery Temperature 142 | Float | ℃ |  | 0 | 1
Unity | 502 | 1 | 1766 | 2 | 0 | BMS Communication Parameters 1 | Battery Temperature 143 | Float | ℃ |  | 0 | 1
Unity | 502 | 1 | 1768 | 2 | 0 | BMS Communication Parameters 1 | Battery Temperature 144 | Float | ℃ |  | 0 | 1
Unity | 502 | 1 | 1770 | 2 | 0 | BMS Communication Parameters 1 | Battery Temperature 145 | Float | ℃ |  | 0 | 1
Unity | 502 | 1 | 1772 | 2 | 0 | BMS Communication Parameters 1 | Battery Temperature 146 | Float | ℃ |  | 0 | 1
Unity | 502 | 1 | 1774 | 2 | 0 | BMS Communication Parameters 1 | Battery Temperature 147 | Float | ℃ |  | 0 | 1
Unity | 502 | 1 | 1776 | 2 | 0 | BMS Communication Parameters 1 | Battery Temperature 148 | Float | ℃ |  | 0 | 1
Unity | 502 | 1 | 1778 | 2 | 0 | BMS Communication Parameters 1 | Battery Temperature 149 | Float | ℃ |  | 0 | 1
Unity | 502 | 1 | 1780 | 2 | 0 | BMS Communication Parameters 1 | Battery Temperature 150 | Float | ℃ |  | 0 | 1
Unity | 502 | 1 | 1782 | 2 | 0 | BMS Communication Parameters 1 | Battery Temperature 151 | Float | ℃ |  | 0 | 1
Unity | 502 | 1 | 1784 | 2 | 0 | BMS Communication Parameters 1 | Battery Temperature 152 | Float | ℃ |  | 0 | 1
Unity | 502 | 1 | 1786 | 2 | 0 | BMS Communication Parameters 1 | Battery Temperature 153 | Float | ℃ |  | 0 | 1
Unity | 502 | 1 | 1788 | 2 | 0 | BMS Communication Parameters 1 | Battery Temperature 154 | Float | ℃ |  | 0 | 1
Unity | 502 | 1 | 1790 | 2 | 0 | BMS Communication Parameters 1 | Battery Temperature 155 | Float | ℃ |  | 0 | 1
Unity | 502 | 1 | 1792 | 2 | 0 | BMS Communication Parameters 1 | Battery Temperature 156 | Float | ℃ |  | 0 | 1
Unity | 502 | 1 | 1794 | 2 | 0 | BMS Communication Parameters 1 | Battery Temperature 157 | Float | ℃ |  | 0 | 1
Unity | 502 | 1 | 1796 | 2 | 0 | BMS Communication Parameters 1 | Battery Temperature 158 | Float | ℃ |  | 0 | 1
Unity | 502 | 1 | 1798 | 2 | 0 | BMS Communication Parameters 1 | Battery Temperature 159 | Float | ℃ |  | 0 | 1
Unity | 502 | 1 | 1800 | 2 | 0 | BMS Communication Parameters 1 | Battery Temperature 160 | Float | ℃ |  | 0 | 1
Unity | 502 | 1 | 1802 | 2 | 0 | BMS Communication Parameters 1 | Rack Cell Over-Voltage L3 Alarm Limit (Early Warning) | Float | mV |  | 0 | 1
Unity | 502 | 1 | 1804 | 2 | 0 | BMS Communication Parameters 1 | Rack Cell Over-Voltage L3 Recovery Limit (Early Warning) | Float | mV |  | 0 | 1
Unity | 502 | 1 | 1806 | 2 | 0 | BMS Communication Parameters 1 | Rack Cell Under-Voltage L3 Alarm Limit (Early Warning) | Float | mV |  | 0 | 1
Unity | 502 | 1 | 1808 | 2 | 0 | BMS Communication Parameters 1 | Rack Cell Under-Voltage L3 Recovery Limit (Early Warning) | Float | mV |  | 0 | 1
Unity | 502 | 1 | 1810 | 2 | 0 | BMS Communication Parameters 1 | Rack Total Voltage Over-Voltage L3 Alarm Limit (Early Warning) | Float | V |  | 0 | 1
Unity | 502 | 1 | 1812 | 2 | 0 | BMS Communication Parameters 1 | Rack Total Voltage Over-Voltage L3 Recovery Limit (Early Warning) | Float | V |  | 0 | 1
Unity | 502 | 1 | 1814 | 2 | 0 | BMS Communication Parameters 1 | Rack Total Voltage Under-Voltage L3 Alarm Limit (Early Warning) | Float | V |  | 0 | 1
Unity | 502 | 1 | 1816 | 2 | 0 | BMS Communication Parameters 1 | Rack Total Voltage Under-Voltage L3 Recovery Limit (Early Warning) | Float | V |  | 0 | 1
Unity | 502 | 1 | 1818 | 2 | 0 | BMS Communication Parameters 1 | Rack Charge Over-Current L3 Alarm Limit (Early Warning) | Float | A |  | 0 | 1
Unity | 502 | 1 | 1820 | 2 | 0 | BMS Communication Parameters 1 | Rack Charge Over-Current L3 Recovery Limit (Early Warning) | Float | A |  | 0 | 1
Unity | 502 | 1 | 1822 | 2 | 0 | BMS Communication Parameters 1 | Rack Discharge Over-Current L3 Alarm Limit (Early Warning) | Float | A |  | 0 | 1
Unity | 502 | 1 | 1824 | 2 | 0 | BMS Communication Parameters 1 | Rack Discharge Over-Current L3 Recovery Limit (Early Warning) | Float | A |  | 0 | 1
Unity | 502 | 1 | 1826 | 2 | 0 | BMS Communication Parameters 1 | Rack Charge Temp Over-High L3 Alarm Limit (Early Warning) | Float | ℃ |  | 0 | 1
Unity | 502 | 1 | 1828 | 2 | 0 | BMS Communication Parameters 1 | Rack Charge Temp Over-High L3 Recovery Limit (Early Warning) | Float | ℃ |  | 0 | 1
Unity | 502 | 1 | 1830 | 2 | 0 | BMS Communication Parameters 1 | Rack Charge Temp Too Low L3 Alarm Limit (Early Warning) | Float | ℃ |  | 0 | 1
Unity | 502 | 1 | 1832 | 2 | 0 | BMS Communication Parameters 1 | Rack Charge Temp Too Low L3 Recovery Limit (Early Warning) | Float | ℃ |  | 0 | 1
Unity | 502 | 1 | 1834 | 2 | 0 | BMS Communication Parameters 1 | Rack SOC Too Low L3 Alarm Limit (Early Warning) | Float | % |  | 0 | 1
Unity | 502 | 1 | 1836 | 2 | 0 | BMS Communication Parameters 1 | Rack SOC Too Low L3 Recovery Limit (Early Warning) | Float | % |  | 0 | 1
Unity | 502 | 1 | 1838 | 2 | 0 | BMS Communication Parameters 1 | Rack Pole Temp Over-High L3 Alarm Limit (Early Warning) | Float | ℃ |  | 0 | 1
Unity | 502 | 1 | 1840 | 2 | 0 | BMS Communication Parameters 1 | Rack Pole Temp Over-High L3 Recovery Limit (Early Warning) | Float | ℃ |  | 0 | 1
Unity | 502 | 1 | 1842 | 2 | 0 | BMS Communication Parameters 1 | Rack Insulation Failure L3 Alarm Limit (Early Warning) | Float | Ω/V |  | 0 | 1
Unity | 502 | 1 | 1844 | 2 | 0 | BMS Communication Parameters 1 | Rack Insulation Failure L3 Recovery Limit (Early Warning) | Float | Ω/V |  | 0 | 1
Unity | 502 | 1 | 1846 | 2 | 0 | BMS Communication Parameters 1 | Rack Cell Voltage Diff Over-High L3 Alarm Limit (Early Warning) | Float | mV |  | 0 | 1
Unity | 502 | 1 | 1848 | 2 | 0 | BMS Communication Parameters 1 | Rack Cell Voltage Diff Over-High L3 Recovery Limit (Early Warning) | Float | mV |  | 0 | 1
Unity | 502 | 1 | 1850 | 2 | 0 | BMS Communication Parameters 1 | Rack Total Voltage Diff Over-High L3 Alarm Limit (Early Warning) | Float | V |  | 0 | 1
Unity | 502 | 1 | 1852 | 2 | 0 | BMS Communication Parameters 1 | Rack Total Voltage Diff Over-High L3 Recovery Limit (Early Warning) | Float | V |  | 0 | 1
Unity | 502 | 1 | 1854 | 2 | 0 | BMS Communication Parameters 1 | Rack Discharge Over-Temp L3 Alarm Limit (Early Warning) | Float | ℃ |  | 0 | 1
Unity | 502 | 1 | 1856 | 2 | 0 | BMS Communication Parameters 1 | Rack Discharge Over-Temp L3 Recovery Limit (Early Warning) | Float | ℃ |  | 0 | 1
Unity | 502 | 1 | 1858 | 2 | 0 | BMS Communication Parameters 1 | Rack Discharge Under-Temp L3 Alarm Limit (Early Warning) | Float | ℃ |  | 0 | 1
Unity | 502 | 1 | 1860 | 2 | 0 | BMS Communication Parameters 1 | Rack Discharge Under-Temp L3 Recovery Limit (Early Warning) | Float | ℃ |  | 0 | 1
Unity | 502 | 1 | 1862 | 2 | 0 | BMS Communication Parameters 1 | Rack Temp Diff Over-High L3 Alarm Limit (Early Warning) | Float | ℃ |  | 0 | 1
Unity | 502 | 1 | 1864 | 2 | 0 | BMS Communication Parameters 1 | Rack Temp Diff Over-High L3 Recovery Limit (Early Warning) | Float | ℃ |  | 0 | 1
Unity | 502 | 1 | 1866 | 2 | 0 | BMS Communication Parameters 1 | Rack HV Box Connector Temp Over-High L3 Alarm Limit (Early Warning) | Float | ℃ |  | 0 | 1
Unity | 502 | 1 | 1868 | 2 | 0 | BMS Communication Parameters 1 | Rack HV Box Connector Temp Over-High L3 Recovery Limit (Early Warning) | Float | ℃ |  | 0 | 1
Unity | 502 | 1 | 1870 | 2 | 0 | BMS Communication Parameters 1 | Rack Cell Over-Voltage L2 Alarm Limit | Float | mV |  | 0 | 1
Unity | 502 | 1 | 1872 | 2 | 0 | BMS Communication Parameters 1 | Rack Cell Over-Voltage L2 Recovery Limit | Float | mV |  | 0 | 1
Unity | 502 | 1 | 1874 | 2 | 0 | BMS Communication Parameters 1 | Rack Cell Under-Voltage L2 Alarm Limit | Float | mV |  | 0 | 1
Unity | 502 | 1 | 1876 | 2 | 0 | BMS Communication Parameters 1 | Rack Cell Under-Voltage L2 Recovery Limit | Float | mV |  | 0 | 1
Unity | 502 | 1 | 1878 | 2 | 0 | BMS Communication Parameters 1 | Rack Total Voltage Over-Voltage L2 Alarm Limit | Float | V |  | 0 | 1
Unity | 502 | 1 | 1880 | 2 | 0 | BMS Communication Parameters 1 | Rack Total Voltage Over-Voltage L2 Recovery Limit | Float | V |  | 0 | 1
Unity | 502 | 1 | 1882 | 2 | 0 | BMS Communication Parameters 1 | Rack Total Voltage Under-Voltage L2 Alarm Limit | Float | V |  | 0 | 1
Unity | 502 | 1 | 1884 | 2 | 0 | BMS Communication Parameters 1 | Rack Total Voltage Under-Voltage L2 Recovery Limit | Float | V |  | 0 | 1
Unity | 502 | 1 | 1886 | 2 | 0 | BMS Communication Parameters 1 | Rack Charge Over-Current L2 Alarm Limit | Float | A |  | 0 | 1
Unity | 502 | 1 | 1888 | 2 | 0 | BMS Communication Parameters 1 | Rack Charge Over-Current L2 Recovery Limit | Float | A |  | 0 | 1
Unity | 502 | 1 | 1890 | 2 | 0 | BMS Communication Parameters 1 | Rack Discharge Over-Current L2 Alarm Limit | Float | A |  | 0 | 1
Unity | 502 | 1 | 1892 | 2 | 0 | BMS Communication Parameters 1 | Rack Discharge Over-Current L2 Recovery Limit | Float | A |  | 0 | 1
Unity | 502 | 1 | 1894 | 2 | 0 | BMS Communication Parameters 1 | Rack Charge Temp Over-High L2 Alarm Limit | Float | ℃ |  | 0 | 1
Unity | 502 | 1 | 1896 | 2 | 0 | BMS Communication Parameters 1 | Rack Charge Temp Over-High L2 Recovery Limit | Float | ℃ |  | 0 | 1
Unity | 502 | 1 | 1898 | 2 | 0 | BMS Communication Parameters 1 | Rack Charge Temp Too Low L2 Alarm Limit | Float | ℃ |  | 0 | 1
Unity | 502 | 1 | 1900 | 2 | 0 | BMS Communication Parameters 1 | Rack Charge Temp Too Low L2 Recovery Limit | Float | ℃ |  | 0 | 1
Unity | 502 | 1 | 1902 | 2 | 0 | BMS Communication Parameters 1 | Rack SOC Too Low L2 Alarm Limit | Float | % |  | 0 | 1
Unity | 502 | 1 | 1904 | 2 | 0 | BMS Communication Parameters 1 | Rack SOC Too Low L2 Recovery Limit | Float | % |  | 0 | 1
Unity | 502 | 1 | 1906 | 2 | 0 | BMS Communication Parameters 1 | Rack Pole Temp Over-High L2 Alarm Limit | Float | ℃ |  | 0 | 1
Unity | 502 | 1 | 1908 | 2 | 0 | BMS Communication Parameters 1 | Rack Pole Temp Over-High L2 Recovery Limit | Float | ℃ |  | 0 | 1
Unity | 502 | 1 | 1910 | 2 | 0 | BMS Communication Parameters 1 | Rack Insulation Failure L2 Alarm Limit | Float | Ω/V |  | 0 | 1
Unity | 502 | 1 | 1912 | 2 | 0 | BMS Communication Parameters 1 | Rack Insulation Failure L2 Recovery Limit | Float | Ω/V |  | 0 | 1
Unity | 502 | 1 | 1914 | 2 | 0 | BMS Communication Parameters 1 | Rack Cell Voltage Diff Over-High L2 Alarm Limit | Float | mV |  | 0 | 1
Unity | 502 | 1 | 1916 | 2 | 0 | BMS Communication Parameters 1 | Rack Cell Voltage Diff Over-High L2 Recovery Limit | Float | mV |  | 0 | 1
Unity | 502 | 1 | 1918 | 2 | 0 | BMS Communication Parameters 1 | Rack Total Voltage Diff Over-High L2 Alarm Limit | Float | V |  | 0 | 1
Unity | 502 | 1 | 1920 | 2 | 0 | BMS Communication Parameters 1 | Rack Total Voltage Diff Over-High L2 Recovery Limit | Float | V |  | 0 | 1
Unity | 502 | 1 | 1922 | 2 | 0 | BMS Communication Parameters 1 | Rack Discharge Over-Temp L2 Alarm Limit | Float | ℃ |  | 0 | 1
Unity | 502 | 1 | 1924 | 2 | 0 | BMS Communication Parameters 1 | Rack Discharge Over-Temp L2 Recovery Limit | Float | ℃ |  | 0 | 1
Unity | 502 | 1 | 1926 | 2 | 0 | BMS Communication Parameters 1 | Rack Discharge Under-Temp L2 Alarm Limit | Float | ℃ |  | 0 | 1
Unity | 502 | 1 | 1928 | 2 | 0 | BMS Communication Parameters 1 | Rack Discharge Under-Temp L2 Recovery Limit | Float | ℃ |  | 0 | 1
Unity | 502 | 1 | 1930 | 2 | 0 | BMS Communication Parameters 1 | Rack Temp Diff Over-High L2 Alarm Limit | Float | ℃ |  | 0 | 1
Unity | 502 | 1 | 1932 | 2 | 0 | BMS Communication Parameters 1 | Rack Temp Diff Over-High L2 Recovery Limit | Float | ℃ |  | 0 | 1
Unity | 502 | 1 | 1934 | 2 | 0 | BMS Communication Parameters 1 | Rack HV Box Connector Temp Over-High L2 Alarm Limit | Float | ℃ |  | 0 | 1
Unity | 502 | 1 | 1936 | 2 | 0 | BMS Communication Parameters 1 | Rack HV Box Connector Temp Over-High L2 Recovery Limit | Float | ℃ |  | 0 | 1
Unity | 502 | 1 | 1938 | 2 | 0 | BMS Communication Parameters 1 | Rack Cell Over-Voltage L1 Alarm Limit (Critical Alarm) | Float | mV |  | 0 | 1
Unity | 502 | 1 | 1940 | 2 | 0 | BMS Communication Parameters 1 | Rack Cell Over-Voltage L1 Recovery Limit (Critical Alarm) | Float | mV |  | 0 | 1
Unity | 502 | 1 | 1942 | 2 | 0 | BMS Communication Parameters 1 | Rack Cell Under-Voltage L1 Alarm Limit (Critical Alarm) | Float | mV |  | 0 | 1
Unity | 502 | 1 | 1944 | 2 | 0 | BMS Communication Parameters 1 | Rack Cell Under-Voltage L1 Recovery Limit (Critical Alarm) | Float | mV |  | 0 | 1
Unity | 502 | 1 | 1946 | 2 | 0 | BMS Communication Parameters 1 | Rack Total Voltage Over-Voltage L1 Alarm Limit (Critical Alarm) | Float | V |  | 0 | 1
Unity | 502 | 1 | 1948 | 2 | 0 | BMS Communication Parameters 1 | Rack Total Voltage Over-Voltage L1 Recovery Limit (Critical Alarm) | Float | V |  | 0 | 1
Unity | 502 | 1 | 1950 | 2 | 0 | BMS Communication Parameters 1 | Rack Total Voltage Under-Voltage L1 Alarm Limit (Critical Alarm) | Float | V |  | 0 | 1
Unity | 502 | 1 | 1952 | 2 | 0 | BMS Communication Parameters 1 | Rack Total Voltage Under-Voltage L1 Recovery Limit (Critical Alarm) | Float | V |  | 0 | 1
Unity | 502 | 1 | 1954 | 2 | 0 | BMS Communication Parameters 1 | Rack Charge Over-Current L1 Alarm Limit (Critical Alarm) | Float | A |  | 0 | 1
Unity | 502 | 1 | 1956 | 2 | 0 | BMS Communication Parameters 1 | Rack Charge Over-Current L1 Recovery Limit (Critical Alarm) | Float | A |  | 0 | 1
Unity | 502 | 1 | 1958 | 2 | 0 | BMS Communication Parameters 1 | Rack Discharge Over-Current L1 Alarm Limit (Critical Alarm) | Float | A |  | 0 | 1
Unity | 502 | 1 | 1960 | 2 | 0 | BMS Communication Parameters 1 | Rack Discharge Over-Current L1 Recovery Limit (Critical Alarm) | Float | A |  | 0 | 1
Unity | 502 | 1 | 1962 | 2 | 0 | BMS Communication Parameters 1 | Rack Charge Temp Over-High L1 Alarm Limit (Critical Alarm) | Float | ℃ |  | 0 | 1
Unity | 502 | 1 | 1964 | 2 | 0 | BMS Communication Parameters 1 | Rack Charge Temp Over-High L1 Recovery Limit (Critical Alarm) | Float | ℃ |  | 0 | 1
Unity | 502 | 1 | 1966 | 2 | 0 | BMS Communication Parameters 1 | Rack Charge Temp Too Low L1 Alarm Limit (Critical Alarm) | Float | ℃ |  | 0 | 1
Unity | 502 | 1 | 1968 | 2 | 0 | BMS Communication Parameters 1 | Rack Charge Temp Too Low L1 Recovery Limit (Critical Alarm) | Float | ℃ |  | 0 | 1
Unity | 502 | 1 | 1970 | 2 | 0 | BMS Communication Parameters 1 | Rack SOC Too Low L1 Alarm Limit (Critical Alarm) | Float | % |  | 0 | 1
Unity | 502 | 1 | 1972 | 2 | 0 | BMS Communication Parameters 1 | Rack SOC Too Low L1 Recovery Limit (Critical Alarm) | Float | % |  | 0 | 1
Unity | 502 | 1 | 1974 | 2 | 0 | BMS Communication Parameters 1 | Rack Pole Temp Over-High L1 Alarm Limit (Critical Alarm) | Float | ℃ |  | 0 | 1
Unity | 502 | 1 | 1976 | 2 | 0 | BMS Communication Parameters 1 | Rack Pole Temp Over-High L1 Recovery Limit (Critical Alarm) | Float | ℃ |  | 0 | 1
Unity | 502 | 1 | 1978 | 2 | 0 | BMS Communication Parameters 1 | Rack Insulation Failure L1 Alarm Limit (Critical Alarm) | Float | Ω/V |  | 0 | 1
Unity | 502 | 1 | 1980 | 2 | 0 | BMS Communication Parameters 1 | Rack Insulation Failure L1 Recovery Limit (Critical Alarm) | Float | Ω/V |  | 0 | 1
Unity | 502 | 1 | 1982 | 2 | 0 | BMS Communication Parameters 1 | Rack Cell Voltage Diff Over-High L1 Alarm Limit (Critical Alarm) | Float | mV |  | 0 | 1
Unity | 502 | 1 | 1984 | 2 | 0 | BMS Communication Parameters 1 | Rack Cell Voltage Diff Over-High L1 Recovery Limit (Critical Alarm) | Float | mV |  | 0 | 1
Unity | 502 | 1 | 1986 | 2 | 0 | BMS Communication Parameters 1 | Rack Total Voltage Diff Over-High L1 Alarm Limit (Critical Alarm) | Float | V |  | 0 | 1
Unity | 502 | 1 | 1988 | 2 | 0 | BMS Communication Parameters 1 | Rack Total Voltage Diff Over-High L1 Recovery Limit (Critical Alarm) | Float | V |  | 0 | 1
Unity | 502 | 1 | 1990 | 2 | 0 | BMS Communication Parameters 1 | Rack Discharge Over-Temp L1 Alarm Limit (Critical Alarm) | Float | ℃ |  | 0 | 1
Unity | 502 | 1 | 1992 | 2 | 0 | BMS Communication Parameters 1 | Rack Discharge Over-Temp L1 Recovery Limit (Critical Alarm) | Float | ℃ |  | 0 | 1
Unity | 502 | 1 | 1994 | 2 | 0 | BMS Communication Parameters 1 | Rack Discharge Under-Temp L1 Alarm Limit (Critical Alarm) | Float | ℃ |  | 0 | 1
Unity | 502 | 1 | 1996 | 2 | 0 | BMS Communication Parameters 1 | Rack Discharge Under-Temp L1 Recovery Limit (Critical Alarm) | Float | ℃ |  | 0 | 1
Unity | 502 | 1 | 1998 | 2 | 0 | BMS Communication Parameters 1 | Rack Temp Diff Over-High L1 Alarm Limit (Critical Alarm) | Float | ℃ |  | 0 | 1
Unity | 502 | 1 | 2000 | 2 | 0 | BMS Communication Parameters 1 | Rack Temp Diff Over-High L1 Recovery Limit (Critical Alarm) | Float | ℃ |  | 0 | 1
Unity | 502 | 1 | 2002 | 2 | 0 | BMS Communication Parameters 1 | Rack HV Box Connector Temp Over-High L1 Alarm Limit (Critical Alarm) | Float | ℃ |  | 0 | 1
Unity | 502 | 1 | 2004 | 2 | 0 | BMS Communication Parameters 1 | Rack HV Box Connector Temp Over-High L1 Recovery Limit (Critical Alarm) | Float | ℃ |  | 0 | 1
Unity | 502 | 1 | 2006 | 2 | 0 | BMS Communication Parameters 1 | Rack Module Voltage Diff Over-High Alarm L1 Threshold | Float | V |  | 0 | 1
Unity | 502 | 1 | 2008 | 2 | 0 | BMS Communication Parameters 1 | Rack Module Voltage Diff Over-High Alarm L2 Threshold | Float | V |  | 0 | 1
Unity | 502 | 1 | 2010 | 2 | 0 | BMS Communication Parameters 1 | Rack Module Voltage Diff Over-High Alarm L3 Threshold | Float | V |  | 0 | 1
Unity | 502 | 1 | 2012 | 2 | 0 | BMS Communication Parameters 1 | Rack Module Voltage Diff Over-High Alarm L1 Recovery Threshold | Float | V |  | 0 | 1
Unity | 502 | 1 | 2014 | 2 | 0 | BMS Communication Parameters 1 | Rack Module Voltage Diff Over-High Alarm L2 Recovery Threshold | Float | V |  | 0 | 1
Unity | 502 | 1 | 2016 | 2 | 0 | BMS Communication Parameters 1 | Rack Module Voltage Diff Over-High Alarm L3 Recovery Threshold | Float | V |  | 0 | 1
Unity | 502 | 1 | 2018 | 2 | 0 | BMS Communication Parameters 1 | BCU Time | Float |  |  | 0 | 1
Unity | 502 | 1 | 2020 | 2 | 0 | BMS Communication Parameters 1 | Pre-Charge End Voltage Diff | Float | V |  | 0 | 1
Unity | 502 | 1 | 2022 | 2 | 0 | BMS Communication Parameters 1 | Fan Start Temperature | Float | ℃ |  | 0 | 1
Unity | 502 | 1 | 2024 | 2 | 0 | BMS Communication Parameters 1 | Fan Stop Temperature | Float | ℃ |  | 0 | 1
Unity | 502 | 1 | 2026 | 2 | 0 | BMS Communication Parameters 1 | Cell Max Voltage | Float | mV |  | 0 | 1
Unity | 502 | 1 | 2028 | 2 | 0 | BMS Communication Parameters 1 | Cell Max Voltage ID | Float |  |  | 0 | 1
Unity | 502 | 1 | 2030 | 2 | 0 | BMS Communication Parameters 1 | Max Cell Module ID | Float |  |  | 0 | 1
Unity | 502 | 1 | 2032 | 2 | 0 | BMS Communication Parameters 1 | Max Cell ID in Module | Float |  |  | 0 | 1
Unity | 502 | 1 | 2034 | 2 | 0 | BMS Communication Parameters 1 | Cell Min Voltage | Float | mV |  | 0 | 1
Unity | 502 | 1 | 2036 | 2 | 0 | BMS Communication Parameters 1 | Cell Min Voltage ID | Float |  |  | 0 | 1
Unity | 502 | 1 | 2038 | 2 | 0 | BMS Communication Parameters 1 | Min Cell Module ID | Float |  |  | 0 | 1
Unity | 502 | 1 | 2040 | 2 | 0 | BMS Communication Parameters 1 | Min Cell ID in Module | Float |  |  | 0 | 1
Unity | 502 | 1 | 2042 | 2 | 0 | BMS Communication Parameters 1 | Max-Min Cell Voltage Diff | Float | mV |  | 0 | 1
Unity | 502 | 1 | 2044 | 2 | 0 | BMS Communication Parameters 1 | Cell Average Voltage | Float | mV |  | 0 | 1
Unity | 502 | 1 | 2046 | 2 | 0 | BMS Communication Parameters 1 | Battery Max Temperature | Float | ℃ |  | 0 | 1
Unity | 502 | 1 | 2048 | 2 | 0 | BMS Communication Parameters 1 | Battery Max Temperature ID | Float |  |  | 0 | 1
Unity | 502 | 1 | 2050 | 2 | 0 | BMS Communication Parameters 1 | Max Temp Slave ID | Float |  |  | 0 | 1
Unity | 502 | 1 | 2052 | 2 | 0 | BMS Communication Parameters 1 | Max Temp ID in Module | Float |  |  | 0 | 1
Unity | 502 | 1 | 2054 | 2 | 0 | BMS Communication Parameters 1 | Battery Min Temperature | Float | ℃ |  | 0 | 1
Unity | 502 | 1 | 2056 | 2 | 0 | BMS Communication Parameters 1 | Battery Min Temperature ID | Float |  |  | 0 | 1
Unity | 502 | 1 | 2058 | 2 | 0 | BMS Communication Parameters 1 | Min Temp Module ID | Float |  |  | 0 | 1
Unity | 502 | 1 | 2060 | 2 | 0 | BMS Communication Parameters 1 | Min Temp ID in Module | Float |  |  | 0 | 1
Unity | 502 | 1 | 2062 | 2 | 0 | BMS Communication Parameters 1 | Average Temperature | Float | ℃ |  | 0 | 1
Unity | 502 | 1 | 2064 | 2 | 0 | BMS Communication Parameters 1 | Max Pole Temperature | Float | ℃ |  | 0 | 1
Unity | 502 | 1 | 2066 | 2 | 0 | BMS Communication Parameters 1 | Max Pole Module ID | Float |  |  | 0 | 1
Unity | 502 | 1 | 2068 | 2 | 0 | BMS Communication Parameters 1 | Max Acceptable Charge Current | Float | A |  | 0 | 1
Unity | 502 | 1 | 2070 | 2 | 0 | BMS Communication Parameters 1 | Max Acceptable Discharge Current | Float | A |  | 0 | 1
Unity | 502 | 1 | 2072 | 2 | 0 | BMS Communication Parameters 1 | Display SOC | Float | % |  | 0 | 1
Unity | 502 | 1 | 2074 | 2 | 0 | BMS Communication Parameters 1 | SOH | Float | % |  | 0 | 1
Unity | 502 | 1 | 2076 | 2 | 0 | BMS Communication Parameters 1 | Battery Max Temperature Diff | Float | ℃ |  | 0 | 1
Unity | 502 | 1 | 2078 | 2 | 0 | BMS Communication Parameters 1 | Cluster Max Cell Temperature Rise | Float | ℃ |  | 0 | 1
Unity | 502 | 1 | 2080 | 2 | 0 | BMS Communication Parameters 1 | Cluster Max Cell Temp Rise Pack ID | Float |  |  | 0 | 1
Unity | 502 | 1 | 2082 | 2 | 0 | BMS Communication Parameters 1 | Cluster Max Cell Temp Rise Cell Temp ID in Pack | Float |  |  | 0 | 1
Unity | 502 | 1 | 2084 | 2 | 0 | BMS Communication Parameters 1 | Cluster Max Cell Temp Rise ID Among All Cells | Float |  |  | 0 | 1
Unity | 502 | 1 | 2086 | 2 | 0 | BMS Communication Parameters 1 | Cluster Internal SOC | Float | % |  | 0 | 1
Unity | 502 | 1 | 2088 | 2 | 0 | BMS Communication Parameters 1 | Pre-Charge Total Voltage | Float | V |  | 0 | 1
Unity | 502 | 1 | 2090 | 2 | 0 | BMS Communication Parameters 1 | Cell Voltage Sum Total | Float | V |  | 0 | 1
Unity | 502 | 1 | 2092 | 2 | 0 | BMS Communication Parameters 1 | Cluster Total Voltage (Collected) | Float | V |  | 0 | 1
Unity | 502 | 1 | 2094 | 2 | 0 | BMS Communication Parameters 1 | Cluster Total Current | Float | A |  | 0 | 1
Unity | 502 | 1 | 2096 | 2 | 0 | BMS Communication Parameters 1 | K_Total Voltage | Float | V |  | 0 | 1
Unity | 502 | 1 | 2098 | 2 | 0 | BMS Communication Parameters 1 | Shunt Sampling Current | Float | A |  | 0 | 1
Unity | 502 | 1 | 2100 | 2 | 0 | BMS Communication Parameters 1 | CAN Hall Sampling Current | Float | A |  | 0 | 1
Unity | 502 | 1 | 2102 | 2 | 0 | BMS Communication Parameters 1 | Current/Voltage Hall Sampling Current | Float | A |  | 0 | 1
Unity | 502 | 1 | 2104 | 2 | 0 | BMS Communication Parameters 1 | Insulation Resistance | Float | kΩ |  | 0 | 1
Unity | 502 | 1 | 2106 | 2 | 0 | BMS Communication Parameters 1 | Positive End Insulation Resistance | Float | kΩ |  | 0 | 1
Unity | 502 | 1 | 2108 | 2 | 0 | BMS Communication Parameters 1 | Negative End Insulation Resistance | Float | kΩ |  | 0 | 1
Unity | 502 | 1 | 2110 | 2 | 0 | BMS Communication Parameters 1 | Power Supply Sampling Voltage | Float | mV |  | 0 | 1
Unity | 502 | 1 | 2112 | 2 | 0 | BMS Communication Parameters 1 | HV Box Max Temperature | Float | ℃ |  | 0 | 1
Unity | 502 | 1 | 2114 | 2 | 0 | BMS Communication Parameters 1 | HV Box Temperature 1 | Float | ℃ |  | 0 | 1
Unity | 502 | 1 | 2116 | 2 | 0 | BMS Communication Parameters 1 | HV Box Temperature 2 | Float | ℃ |  | 0 | 1
Unity | 502 | 1 | 2118 | 2 | 0 | BMS Communication Parameters 1 | HV Box Temperature 3 | Float | ℃ |  | 0 | 1
Unity | 502 | 1 | 2120 | 2 | 0 | BMS Communication Parameters 1 | HV Box Temperature 4 | Float | ℃ |  | 0 | 1
Unity | 502 | 1 | 2122 | 2 | 0 | BMS Communication Parameters 1 | Battery Cluster Internal Resistance | Float | mΩ |  | 0 | 1
Unity | 502 | 1 | 2124 | 2 | 0 | BMS Communication Parameters 1 | Monthly Cumulative Charge Energy | Float | kWh |  | 0 | 1
Unity | 502 | 1 | 2126 | 2 | 0 | BMS Communication Parameters 1 | Monthly Cumulative Discharge Energy | Float | kWh |  | 0 | 1
Unity | 502 | 1 | 2128 | 2 | 0 | BMS Communication Parameters 1 | Yearly Cumulative Charge Energy | Float | kWh |  | 0 | 1
Unity | 502 | 1 | 2130 | 2 | 0 | BMS Communication Parameters 1 | Yearly Cumulative Discharge Energy | Float | kWh |  | 0 | 1
Unity | 502 | 1 | 2132 | 2 | 0 | BMS Communication Parameters 1 | Total Cumulative Charge Capacity | Float | AH |  | 0 | 1
Unity | 502 | 1 | 2134 | 2 | 0 | BMS Communication Parameters 1 | Total Cumulative Discharge Capacity | Float | AH |  | 0 | 1
Unity | 502 | 1 | 2136 | 2 | 0 | BMS Communication Parameters 1 | Max Voltage Cell ID at Alarm | Float |  |  | 0 | 1
Unity | 502 | 1 | 2138 | 2 | 0 | BMS Communication Parameters 1 | Max Voltage Value at Alarm | Float | mV |  | 0 | 1
Unity | 502 | 1 | 2140 | 2 | 0 | BMS Communication Parameters 1 | Max Voltage Cell ID at Shutdown | Float |  |  | 0 | 1
Unity | 502 | 1 | 2142 | 2 | 0 | BMS Communication Parameters 1 | Max Voltage Value at Shutdown | Float | mV |  | 0 | 1
Unity | 502 | 1 | 2144 | 2 | 0 | BMS Communication Parameters 1 | Min Voltage Cell ID at Alarm | Float |  |  | 0 | 1
Unity | 502 | 1 | 2146 | 2 | 0 | BMS Communication Parameters 1 | Min Voltage Value at Alarm | Float | mV |  | 0 | 1
Unity | 502 | 1 | 2148 | 2 | 0 | BMS Communication Parameters 1 | Min Voltage Cell ID at Shutdown | Float |  |  | 0 | 1
Unity | 502 | 1 | 2150 | 2 | 0 | BMS Communication Parameters 1 | Min Voltage Value at Shutdown | Float | mV |  | 0 | 1
Unity | 502 | 1 | 2152 | 2 | 0 | BMS Communication Parameters 1 | Battery Pack Over-Voltage Alarm Voltage Value | Float | V |  | 0 | 1
Unity | 502 | 1 | 2154 | 2 | 0 | BMS Communication Parameters 1 | Battery Pack Over-Voltage Shutdown Voltage Value | Float | V |  | 0 | 1
Unity | 502 | 1 | 2156 | 2 | 0 | BMS Communication Parameters 1 | Battery Pack Under-Voltage Alarm Voltage Value | Float | V |  | 0 | 1
Unity | 502 | 1 | 2158 | 2 | 0 | BMS Communication Parameters 1 | Battery Pack Under-Voltage Shutdown Voltage Value | Float | V |  | 0 | 1
Unity | 502 | 1 | 2160 | 2 | 0 | BMS Communication Parameters 1 | Battery Charge Over-Current Alarm Current Value | Float | A |  | 0 | 1
Unity | 502 | 1 | 2162 | 2 | 0 | BMS Communication Parameters 1 | Battery Charge Over-Current Shutdown Current Value | Float | A |  | 0 | 1
Unity | 502 | 1 | 2164 | 2 | 0 | BMS Communication Parameters 1 | Battery Discharge Over-Current Alarm Current Value | Float | A |  | 0 | 1
Unity | 502 | 1 | 2166 | 2 | 0 | BMS Communication Parameters 1 | Battery Discharge Over-Current Shutdown Current Value | Float | A |  | 0 | 1
Unity | 502 | 1 | 2168 | 2 | 0 | BMS Communication Parameters 1 | Max Cell Temperature Point ID at Alarm | Float |  |  | 0 | 1
Unity | 502 | 1 | 2170 | 2 | 0 | BMS Communication Parameters 1 | Max Cell Temperature at Alarm | Float | ℃ |  | 0 | 1
Unity | 502 | 1 | 2172 | 2 | 0 | BMS Communication Parameters 1 | Max Cell Temperature Point ID at Shutdown | Float |  |  | 0 | 1
Unity | 502 | 1 | 2174 | 2 | 0 | BMS Communication Parameters 1 | Max Cell Temperature at Shutdown | Float | ℃ |  | 0 | 1
Unity | 502 | 1 | 2176 | 2 | 0 | BMS Communication Parameters 1 | Min Cell Temperature Point ID at Alarm | Float |  |  | 0 | 1
Unity | 502 | 1 | 2178 | 2 | 0 | BMS Communication Parameters 1 | Min Cell Temperature at Alarm | Float | ℃ |  | 0 | 1
Unity | 502 | 1 | 2180 | 2 | 0 | BMS Communication Parameters 1 | Min Cell Temperature Point ID at Shutdown | Float |  |  | 0 | 1
Unity | 502 | 1 | 2182 | 2 | 0 | BMS Communication Parameters 1 | Min Cell Temperature at Shutdown | Float | ℃ |  | 0 | 1
Unity | 502 | 1 | 2184 | 2 | 0 | BMS Communication Parameters 1 | Max HV Box Temperature at Alarm | Float | ℃ |  | 0 | 1
Unity | 502 | 1 | 2186 | 2 | 0 | BMS Communication Parameters 1 | Max HV Box Temperature at Shutdown | Float | ℃ |  | 0 | 1
Unity | 502 | 1 | 2188 | 2 | 0 | BMS Communication Parameters 1 | Temperature Rise Alarm Cell ID | Float |  |  | 0 | 1
Unity | 502 | 1 | 2190 | 2 | 0 | BMS Communication Parameters 1 | Temperature Rise Alarm Value | Float | ℃ |  | 0 | 1
Unity | 502 | 1 | 2192 | 2 | 0 | BMS Communication Parameters 1 | Temperature Rise Shutdown Cell ID | Float |  |  | 0 | 1
Unity | 502 | 1 | 2194 | 2 | 0 | BMS Communication Parameters 1 | Temperature Rise Shutdown Value | Float | ℃ |  | 0 | 1
Unity | 502 | 1 | 2196 | 2 | 0 | BMS Communication Parameters 1 | Max Power Temp Point ID at Alarm (Pole Temp) | Float |  |  | 0 | 1
Unity | 502 | 1 | 2198 | 2 | 0 | BMS Communication Parameters 1 | Max Power Temp Value at Alarm (Pole Temp) | Float | ℃ |  | 0 | 1
Unity | 502 | 1 | 2200 | 2 | 0 | BMS Communication Parameters 1 | Max Power Temp Point ID at Shutdown (Pole Temp) | Float |  |  | 0 | 1
Unity | 502 | 1 | 2202 | 2 | 0 | BMS Communication Parameters 1 | Max Power Temp Value at Shutdown (Pole Temp) | Float | ℃ |  | 0 | 1
Unity | 502 | 1 | 2204 | 2 | 0 | BMS Communication Parameters 1 | Battery Cell Max-Min Voltage Diff Too Large Alarm Diff Value | Float | mV |  | 0 | 1
Unity | 502 | 1 | 2206 | 2 | 0 | BMS Communication Parameters 1 | Battery Cell Max-Min Voltage Diff Too Large Shutdown Diff Value | Float | mV |  | 0 | 1
Unity | 502 | 1 | 2208 | 2 | 0 | BMS Communication Parameters 1 | Insulation Resistance Too Low Alarm Resistance Value | Float | Ω/V |  | 0 | 1
Unity | 502 | 1 | 2210 | 2 | 0 | BMS Communication Parameters 1 | Insulation Resistance Too Low Shutdown Resistance Value | Float | Ω/V |  | 0 | 1
Unity | 502 | 1 | 2212 | 2 | 0 | BMS Communication Parameters 1 | Total Voltage & Slave Total Voltage Diff Too Large Alarm Diff | Float | V |  | 0 | 1
Unity | 502 | 1 | 2214 | 2 | 0 | BMS Communication Parameters 1 | Total Voltage & Slave Total Voltage Diff Too Large Shutdown Diff | Float | V |  | 0 | 1
Unity | 502 | 1 | 2216 | 2 | 0 | BMS Communication Parameters 1 | Battery Cell Max-Min Temp Diff Too Large Alarm Diff Value | Float | ℃ |  | 0 | 1
Unity | 502 | 1 | 2218 | 2 | 0 | BMS Communication Parameters 1 | Battery Cell Max-Min Temp Diff Too Large Shutdown Diff Value | Float | ℃ |  | 0 | 1
Unity | 502 | 1 | 2220 | 2 | 0 | BMS Communication Parameters 1 | Max Module Voltage ID at Alarm | Float |  |  | 0 | 1
Unity | 502 | 1 | 2222 | 2 | 0 | BMS Communication Parameters 1 | Module Voltage Too High Alarm Voltage Value | Float | V |  | 0 | 1
Unity | 502 | 1 | 2224 | 2 | 0 | BMS Communication Parameters 1 | Max Module Voltage ID at Shutdown | Float |  |  | 0 | 1
Unity | 502 | 1 | 2226 | 2 | 0 | BMS Communication Parameters 1 | Module Voltage Too High Shutdown Voltage Value | Float | V |  | 0 | 1
Unity | 502 | 1 | 2228 | 2 | 0 | BMS Communication Parameters 1 | Min Module Voltage ID at Alarm | Float |  |  | 0 | 1
Unity | 502 | 1 | 2230 | 2 | 0 | BMS Communication Parameters 1 | Module Voltage Too Low Alarm Voltage Value | Float | V |  | 0 | 1
Unity | 502 | 1 | 2232 | 2 | 0 | BMS Communication Parameters 1 | Min Module Voltage ID at Shutdown | Float |  |  | 0 | 1
Unity | 502 | 1 | 2234 | 2 | 0 | BMS Communication Parameters 1 | Module Voltage Too Low Shutdown Voltage Value | Float | V |  | 0 | 1
Unity | 502 | 1 | 2236 | 2 | 0 | BMS Communication Parameters 1 | Start Insulation Sampling | Float |  | 0,Reset;1,No Reset | 0 | 1
Unity | 502 | 1 | 2238 | 2 | 0 | BMS Communication Parameters 1 | Pre-Charge Control | Float |  | 1,Start;2,Closed | 0 | 1
Unity | 502 | 1 | 2240 | 2 | 0 | BMS Communication Parameters 1 | Master Control Reset | Float |  | 1,Reset | 0 | 1
Unity | 502 | 1 | 2242 | 2 | 0 | BMS Communication Parameters 1 | Reset Slave ID Enable | Float |  | 1,Enabled;2,Disabled | 0 | 1
Unity | 502 | 1 | 2244 | 2 | 0 | BMS Communication Parameters 1 | Set Master Control Address | Float |  |  | 0 | 1
Unity | 502 | 1 | 2246 | 2 | 0 | BMS Communication Parameters 1 | Fan Force Control Switch | Float |  | 0,No Force Control;1,Force Control On;2,Force Control Off | 0 | 1
Unity | 502 | 1 | 2248 | 2 | 0 | IO | Communication Status | Float |  | 0,Offline;1,Online | 0 | 1
Unity | 502 | 1 | 2250 | 2 | 0 | IO | E-Stop Signal | Float |  | 0,Normal;1,Alarm | 0 | 1
Unity | 502 | 1 | 2252 | 2 | 0 | IO | Water Infiltration Alarm | Float |  | 0,Normal;1,Alarm | 0 | 1
Unity | 502 | 1 | 2254 | 2 | 0 | IO | Circuit Breaker Feedback | Float |  | 0,Open;1,Closed | 0 | 1
Unity | 502 | 1 | 2256 | 2 | 0 | IO | DI4 | Float |  | 0,Open;1,Closed | 0 | 1
Unity | 502 | 1 | 2258 | 2 | 0 | IO | Access Control | Float |  | 0,Open;1,Closed | 0 | 1
Unity | 502 | 1 | 2260 | 2 | 0 | IO | Fire Protection Spraying | Float |  | 0,Normal;1,Alarm | 0 | 1
Unity | 502 | 1 | 2262 | 2 | 0 | IO | PCS Fault | Float |  | 0,Normal;1,Alarm | 0 | 1
Unity | 502 | 1 | 2264 | 2 | 0 | IO | DI8 | Float |  | 0,Open;1,Closed | 0 | 1
Unity | 502 | 1 | 2266 | 2 | 0 | IO | DI9 | Float |  | 0,Open;1,Closed | 0 | 1
Unity | 502 | 1 | 2268 | 2 | 0 | IO | DI10 | Float |  | 0,Open;1,Closed | 0 | 1
Unity | 502 | 1 | 2270 | 2 | 0 | IO | DI11 | Float |  | 0,Open;1,Closed | 0 | 1
Unity | 502 | 1 | 2272 | 2 | 0 | IO | DI12 | Float |  | 0,Open;1,Closed | 0 | 1
Unity | 502 | 1 | 2274 | 2 | 0 | IO | Circuit Breaker Control | Float |  | 0,Normal;1,Trip | 0 | 1
Unity | 502 | 1 | 2276 | 2 | 0 | IO | Running Indicator | Float |  | 0,Open;1,Closed | 0 | 1
Unity | 502 | 1 | 2278 | 2 | 0 | IO | Fault Indicator | Float |  | 0,Open;1,Closed | 0 | 1
Unity | 502 | 1 | 2280 | 2 | 0 | IO | DO4 | Float |  | 0,Open;1,Closed | 0 | 1
Unity | 502 | 1 | 2282 | 2 | 0 | IO | DO5 | Float |  | 0,Open;1,Closed | 0 | 1
Unity | 502 | 1 | 2284 | 2 | 0 | IO | DO6 | Float |  | 0,Open;1,Closed | 0 | 1
Unity | 502 | 1 | 2286 | 2 | 0 | IO | DO7 | Float |  | 0,Open;1,Closed | 0 | 1
Unity | 502 | 1 | 2288 | 2 | 0 | IO | DO8 | Float |  | 0,Open;1,Closed | 0 | 1
Unity | 502 | 1 | 2290 | 2 | 0 | Liquid Cooling Communication Parameters | Online Points | Float |  | 0,Offline;1,Online | 0 | 1
Unity | 502 | 1 | 2292 | 2 | 0 | Liquid Cooling Communication Parameters | Power On/Off | Float |  | 0,Shutdown;1,Power On | 0 | 1
Unity | 502 | 1 | 2294 | 2 | 0 | Liquid Cooling Communication Parameters | Water Temperature Control Target | Float |  | 0,Outlet Water Temperature;1,Inlet Water Temperature | 0 | 1
Unity | 502 | 1 | 2296 | 2 | 0 | Liquid Cooling Communication Parameters | Outlet High Pressure Alarm Value | Float | Bar |  | 0 | 1
Unity | 502 | 1 | 2298 | 2 | 0 | Liquid Cooling Communication Parameters | Inlet Low Pressure Alarm Value | Float | Bar |  | 0 | 1
Unity | 502 | 1 | 2300 | 2 | 0 | Liquid Cooling Communication Parameters | Outlet High Temp Alarm Value | Float | ℃ |  | 0 | 1
Unity | 502 | 1 | 2302 | 2 | 0 | Liquid Cooling Communication Parameters | Outlet Low Temp Alarm Value | Float | ℃ |  | 0 | 1
Unity | 502 | 1 | 2304 | 2 | 0 | Liquid Cooling Communication Parameters | Operating Mode | Float |  | 0,Cooling Control;1,Monitor Temperature;2,Monitor Mode;3,Full-Speed Cooling | 0 | 1
Unity | 502 | 1 | 2306 | 2 | 0 | Liquid Cooling Communication Parameters | Cooling Set Temperature | Float | ℃ |  | 0 | 1
Unity | 502 | 1 | 2308 | 2 | 0 | Liquid Cooling Communication Parameters | Heating Set Temperature | Float | ℃ |  | 0 | 1
Unity | 502 | 1 | 2310 | 2 | 0 | Liquid Cooling Communication Parameters | Cooling Battery Max Temperature | Float | ℃ |  | 0 | 1
Unity | 502 | 1 | 2312 | 2 | 0 | Liquid Cooling Communication Parameters | Cooling Battery Avg Temperature | Float | ℃ |  | 0 | 1
Unity | 502 | 1 | 2314 | 2 | 0 | Liquid Cooling Communication Parameters | Cooling Battery Temp Hysteresis | Float | ℃ |  | 0 | 1
Unity | 502 | 1 | 2316 | 2 | 0 | Liquid Cooling Communication Parameters | Heating Battery Min Temperature | Float | ℃ |  | 0 | 1
Unity | 502 | 1 | 2318 | 2 | 0 | Liquid Cooling Communication Parameters | Heating Battery Avg Temperature | Float | ℃ |  | 0 | 1
Unity | 502 | 1 | 2320 | 2 | 0 | Liquid Cooling Communication Parameters | Heating Battery Temp Hysteresis | Float | ℃ |  | 0 | 1
Unity | 502 | 1 | 2322 | 2 | 0 | Liquid Cooling Communication Parameters | Monitor Mode | Float |  | 0,Shutdown;1,Cooling;2,Heating;3,Self-Circulation;4,Standby | 0 | 1
Unity | 502 | 1 | 2324 | 2 | 0 | Liquid Cooling Communication Parameters | Inlet Water Temperature | Float | ℃ |  | 0 | 1
Unity | 502 | 1 | 2326 | 2 | 0 | Liquid Cooling Communication Parameters | Outlet Water Temperature | Float | ℃ |  | 0 | 1
Unity | 502 | 1 | 2328 | 2 | 0 | Liquid Cooling Communication Parameters | Inlet/Outlet Water Pressure Diff | Float | ℃ |  | 0 | 1
Unity | 502 | 1 | 2330 | 2 | 0 | Liquid Cooling Communication Parameters | Inlet/Outlet Water Temperature Diff | Float | ℃ |  | 0 | 1
Unity | 502 | 1 | 2332 | 2 | 0 | Liquid Cooling Communication Parameters | Inlet Water Pressure | Float | Bar |  | 0 | 1
Unity | 502 | 1 | 2334 | 2 | 0 | Liquid Cooling Communication Parameters | Outlet Water Pressure | Float | Bar |  | 0 | 1
Unity | 502 | 1 | 2336 | 2 | 0 | Liquid Cooling Communication Parameters | Outdoor Temperature | Float | ℃ |  | 0 | 1
Unity | 502 | 1 | 2338 | 2 | 0 | Liquid Cooling Communication Parameters | System Cooling Demand | Float | ℃ |  | 0 | 1
Unity | 502 | 1 | 2340 | 2 | 0 | Liquid Cooling Communication Parameters | System Heating Demand | Float | ℃ |  | 0 | 1
Unity | 502 | 1 | 2342 | 2 | 0 | Liquid Cooling Communication Parameters | Unit Operating Mode | Float |  | 0,Self-Circulation;1,Cooling;2,Heating;3,Standby | 0 | 1
Unity | 502 | 1 | 2344 | 2 | 0 | Liquid Cooling Communication Parameters | Unit Control Mode | Float |  | 0,Shutdown;1,Self-Circulation;2,Standby;3,Cooling;4,Heating;5,Manual;6,Vacuuming;7,Fault Shutdown;8,Group Control Standby;9,Remote Shutdown;10,Auto Exhaust | 0 | 1
Unity | 502 | 1 | 2346 | 2 | 0 | Liquid Cooling Communication Parameters | Power Supply Over-Voltage Alarm | Float |  | 0,Normal;1,Alarm | 0 | 1
Unity | 502 | 1 | 2348 | 2 | 0 | Liquid Cooling Communication Parameters | Power Supply Under-Voltage Alarm | Float |  | 0,Normal;1,Alarm | 0 | 1
Unity | 502 | 1 | 2350 | 2 | 0 | Liquid Cooling Communication Parameters | Power Supply Phase Loss Alarm | Float |  | 0,Normal;1,Alarm | 0 | 1
Unity | 502 | 1 | 2352 | 2 | 0 | Liquid Cooling Communication Parameters | Power Supply Phase Error Alarm | Float |  | 0,Normal;1,Alarm | 0 | 1
Unity | 502 | 1 | 2354 | 2 | 0 | Liquid Cooling Communication Parameters | Switching Power Supply Fault | Float |  | 0,Normal;1,Alarm | 0 | 1
Unity | 502 | 1 | 2356 | 2 | 0 | Liquid Cooling Communication Parameters | Electric Heating Protection Alarm | Float |  | 0,Normal;1,Alarm | 0 | 1
Unity | 502 | 1 | 2358 | 2 | 0 | Liquid Cooling Communication Parameters | Smoke Alarm | Float |  | 0,Normal;1,Alarm | 0 | 1
Unity | 502 | 1 | 2360 | 2 | 0 | Liquid Cooling Communication Parameters | Water Infiltration Alarm | Float |  | 0,Normal;1,Alarm | 0 | 1
Unity | 502 | 1 | 2362 | 2 | 0 | Liquid Cooling Communication Parameters | Low Water Flow Alarm | Float |  | 0,Normal;1,Alarm | 0 | 1
Unity | 502 | 1 | 2364 | 2 | 0 | Liquid Cooling Communication Parameters | Water Tank Low Level Alarm | Float |  | 0,Normal;1,Alarm | 0 | 1
Unity | 502 | 1 | 2366 | 2 | 0 | Liquid Cooling Communication Parameters | Water Flow Meter Communication Fault | Float |  | 0,Normal;1,Alarm | 0 | 1
Unity | 502 | 1 | 2368 | 2 | 0 | Liquid Cooling Communication Parameters | Electric Heating Overload Alarm Lock | Float |  | 0,Normal;1,Alarm | 0 | 1
Unity | 502 | 1 | 2370 | 2 | 0 | Liquid Cooling Communication Parameters | Meter Communication Fault | Float |  | 0,Normal;1,Alarm | 0 | 1
Unity | 502 | 1 | 2372 | 2 | 0 | Liquid Cooling Communication Parameters | Group Control Communication Address Conflict | Float |  | 0,Normal;1,Alarm | 0 | 1
Unity | 502 | 1 | 2374 | 2 | 0 | Liquid Cooling Communication Parameters | Group Control Network Communication Fault | Float |  | 0,Normal;1,Alarm | 0 | 1
Unity | 502 | 1 | 2376 | 2 | 0 | Liquid Cooling Communication Parameters | Indoor Temp Probe Fault | Float |  | 0,Normal;1,Alarm | 0 | 1
Unity | 502 | 1 | 2378 | 2 | 0 | Liquid Cooling Communication Parameters | Indoor Humidity Probe Fault | Float |  | 0,Normal;1,Alarm | 0 | 1
Unity | 502 | 1 | 2380 | 2 | 0 | Liquid Cooling Communication Parameters | Inlet Temp Probe Fault | Float |  | 0,Normal;1,Alarm | 0 | 1
Unity | 502 | 1 | 2382 | 2 | 0 | Liquid Cooling Communication Parameters | Outlet Temp Probe Fault | Float |  | 0,Normal;1,Alarm | 0 | 1
Unity | 502 | 1 | 2384 | 2 | 0 | Liquid Cooling Communication Parameters | Inlet Pressure Probe Fault | Float |  | 0,Normal;1,Alarm | 0 | 1
Unity | 502 | 1 | 2386 | 2 | 0 | Liquid Cooling Communication Parameters | Outlet Pressure Probe Fault | Float |  | 0,Normal;1,Alarm | 0 | 1
Unity | 502 | 1 | 2388 | 2 | 0 | Liquid Cooling Communication Parameters | Inlet High Temp Alarm | Float |  | 0,Normal;1,Alarm | 0 | 1
Unity | 502 | 1 | 2390 | 2 | 0 | Liquid Cooling Communication Parameters | Inlet Low Temp Alarm | Float |  | 0,Normal;1,Alarm | 0 | 1
Unity | 502 | 1 | 2392 | 2 | 0 | Liquid Cooling Communication Parameters | Outlet High Temp Alarm | Float |  | 0,Normal;1,Alarm | 0 | 1
Unity | 502 | 1 | 2394 | 2 | 0 | Liquid Cooling Communication Parameters | Outlet Low Temp Alarm | Float |  | 0,Normal;1,Alarm | 0 | 1
Unity | 502 | 1 | 2396 | 2 | 0 | Liquid Cooling Communication Parameters | SPI Communication Fault | Float |  | 0,Normal;1,Alarm | 0 | 1
Unity | 502 | 1 | 2398 | 2 | 0 | Liquid Cooling Communication Parameters | Outdoor Temp Probe Fault | Float |  | 0,Normal;1,Alarm | 0 | 1
Unity | 502 | 1 | 2400 | 2 | 0 | Liquid Cooling Communication Parameters | Inlet/Outlet Temp Probe Reversed | Float |  | 0,Normal;1,Alarm | 0 | 1
Unity | 502 | 1 | 2402 | 2 | 0 | Liquid Cooling Communication Parameters | Inlet/Outlet Pressure Probe Reversed | Float |  | 0,Normal;1,Alarm | 0 | 1
Unity | 502 | 1 | 2404 | 2 | 0 | Liquid Cooling Communication Parameters | System A/B Suction/Discharge Temp Probe Wiring Abnormal | Float |  | 0,Normal;1,Alarm | 0 | 1
Unity | 502 | 1 | 2406 | 2 | 0 | Liquid Cooling Communication Parameters | CAN Communication Fault | Float |  | 0,Normal;1,Alarm | 0 | 1
Unity | 502 | 1 | 2408 | 2 | 0 | Liquid Cooling Communication Parameters | Outdoor Fan 1 Fault Lock | Float |  | 0,Normal;1,Alarm | 0 | 1
Unity | 502 | 1 | 2410 | 2 | 0 | Liquid Cooling Communication Parameters | Outdoor Fan 2 Fault Lock | Float |  | 0,Normal;1,Alarm | 0 | 1
Unity | 502 | 1 | 2412 | 2 | 0 | Liquid Cooling Communication Parameters | Outdoor Fan 3 Fault Lock | Float |  | 0,Normal;1,Alarm | 0 | 1
Unity | 502 | 1 | 2414 | 2 | 0 | Liquid Cooling Communication Parameters | Outdoor Fan 4 Fault Lock | Float |  | 0,Normal;1,Alarm | 0 | 1
Unity | 502 | 1 | 2416 | 2 | 0 | Liquid Cooling Communication Parameters | Outdoor Fan 5 Fault Lock | Float |  | 0,Normal;1,Alarm | 0 | 1
Unity | 502 | 1 | 2418 | 2 | 0 | Liquid Cooling Communication Parameters | Outdoor Fan 6 Fault Lock | Float |  | 0,Normal;1,Alarm | 0 | 1
Unity | 502 | 1 | 2420 | 2 | 0 | Liquid Cooling Communication Parameters | Inlet Low Pressure Alarm | Float |  | 0,Normal;1,Alarm | 0 | 1
Unity | 502 | 1 | 2422 | 2 | 0 | Liquid Cooling Communication Parameters | Outlet High Pressure Alarm Lock | Float |  | 0,Normal;1,Alarm | 0 | 1
Unity | 502 | 1 | 2424 | 2 | 0 | Liquid Cooling Communication Parameters | Remote RS485 Communication Fault | Float |  | 0,Normal;1,Alarm | 0 | 1
Unity | 502 | 1 | 2426 | 2 | 0 | Liquid Cooling Communication Parameters | System A High Pressure Alarm Lock | Float |  | 0,Normal;1,Alarm | 0 | 1
Unity | 502 | 1 | 2428 | 2 | 0 | Liquid Cooling Communication Parameters | System A Low Pressure Alarm Lock | Float |  | 0,Normal;1,Alarm | 0 | 1
Unity | 502 | 1 | 2430 | 2 | 0 | Liquid Cooling Communication Parameters | System A High Pressure Switch Fault | Float |  | 0,Normal;1,Alarm | 0 | 1
Unity | 502 | 1 | 2432 | 2 | 0 | Liquid Cooling Communication Parameters | System A Low Pressure Switch Fault | Float |  | 0,Normal;1,Alarm | 0 | 1
Unity | 502 | 1 | 2434 | 2 | 0 | Liquid Cooling Communication Parameters | System A Discharge High Temp Lock | Float |  | 0,Normal;1,Alarm | 0 | 1
Unity | 502 | 1 | 2436 | 2 | 0 | Liquid Cooling Communication Parameters | System A Liquid Pipe Temp Sensor Fault | Float |  | 0,Normal;1,Alarm | 0 | 1
Unity | 502 | 1 | 2438 | 2 | 0 | Liquid Cooling Communication Parameters | System A Discharge Temp Probe Fault | Float |  | 0,Normal;1,Alarm | 0 | 1
Unity | 502 | 1 | 2440 | 2 | 0 | Liquid Cooling Communication Parameters | System A Suction Temp Probe Fault | Float |  | 0,Normal;1,Alarm | 0 | 1
Unity | 502 | 1 | 2442 | 2 | 0 | Liquid Cooling Communication Parameters | System A Suction Pressure Probe Fault | Float |  | 0,Normal;1,Alarm | 0 | 1
Unity | 502 | 1 | 2444 | 2 | 0 | Liquid Cooling Communication Parameters | System A Discharge Pressure Probe Fault | Float |  | 0,Normal;1,Alarm | 0 | 1
Unity | 502 | 1 | 2446 | 2 | 0 | Liquid Cooling Communication Parameters | System A Refrigerant Leak or Insufficient | Float |  | 0,Normal;1,Alarm | 0 | 1
Unity | 502 | 1 | 2448 | 2 | 0 | Liquid Cooling Communication Parameters | System A Suction/Discharge Temp Probe Wiring Abnormal | Float |  | 0,Normal;1,Alarm | 0 | 1
Unity | 502 | 1 | 2450 | 2 | 0 | Liquid Cooling Communication Parameters | System A Compressor Communication Fault | Float |  | 0,Normal;1,Alarm | 0 | 1
Unity | 502 | 1 | 2452 | 2 | 0 | Liquid Cooling Communication Parameters | System A Compressor Frequency Abnormal | Float |  | 0,Normal;1,Alarm | 0 | 1
Unity | 502 | 1 | 2454 | 2 | 0 | Liquid Cooling Communication Parameters | System A Pump Communication Fault | Float |  | 0,Normal;1,Alarm | 0 | 1
Unity | 502 | 1 | 2456 | 2 | 0 | Liquid Cooling Communication Parameters | System A Outdoor Unit Communication Fault | Float |  | 0,Normal;1,Alarm | 0 | 1
Unity | 502 | 1 | 2458 | 2 | 0 | Liquid Cooling Communication Parameters | System A Compressor Drive Fault Alarm Lock | Float |  | 0,Normal;1,Alarm | 0 | 1
Unity | 502 | 1 | 2460 | 2 | 0 | Liquid Cooling Communication Parameters | System A Outdoor Fan Drive Fault Alarm Lock | Float |  | 0,Normal;1,Alarm | 0 | 1
Unity | 502 | 1 | 2462 | 2 | 0 | Liquid Cooling Communication Parameters | Circulating Water Pump 1 Drive Fault Alarm Lock | Float |  | 0,Normal;1,Alarm | 0 | 1
Unity | 502 | 1 | 2464 | 2 | 0 | Liquid Cooling Communication Parameters | Circulating Water Pump 1 Overload Alarm | Float |  | 0,Normal;1,Alarm | 0 | 1
Unity | 502 | 1 | 2466 | 2 | 0 | Liquid Cooling Communication Parameters | Circulating Water Pump 1 Overload Alarm Lock | Float |  | 0,Normal;1,Alarm | 0 | 1
Unity | 502 | 1 | 2468 | 2 | 0 | Liquid Cooling Communication Parameters | System B High Pressure Alarm Lock | Float |  | 0,Normal;1,Alarm | 0 | 1
Unity | 502 | 1 | 2470 | 2 | 0 | Liquid Cooling Communication Parameters | System B Low Pressure Alarm Lock | Float |  | 0,Normal;1,Alarm | 0 | 1
Unity | 502 | 1 | 2472 | 2 | 0 | Liquid Cooling Communication Parameters | System B High Pressure Switch Fault | Float |  | 0,Normal;1,Alarm | 0 | 1
Unity | 502 | 1 | 2474 | 2 | 0 | Liquid Cooling Communication Parameters | System B Low Pressure Switch Fault | Float |  | 0,Normal;1,Alarm | 0 | 1
Unity | 502 | 1 | 2476 | 2 | 0 | Liquid Cooling Communication Parameters | System B Discharge High Temp Alarm | Float |  | 0,Normal;1,Alarm | 0 | 1
Unity | 502 | 1 | 2478 | 2 | 0 | Liquid Cooling Communication Parameters | System B Discharge High Temp Lock | Float |  | 0,Normal;1,Alarm | 0 | 1
Unity | 502 | 1 | 2480 | 2 | 0 | Liquid Cooling Communication Parameters | System B Liquid Pipe Temp Sensor Fault | Float |  | 0,Normal;1,Alarm | 0 | 1
Unity | 502 | 1 | 2482 | 2 | 0 | Liquid Cooling Communication Parameters | System B Discharge Temp Probe Fault | Float |  | 0,Normal;1,Alarm | 0 | 1
Unity | 502 | 1 | 2484 | 2 | 0 | Liquid Cooling Communication Parameters | System B Suction Temp Probe Fault | Float |  | 0,Normal;1,Alarm | 0 | 1
Unity | 502 | 1 | 2486 | 2 | 0 | Liquid Cooling Communication Parameters | System B Suction Pressure Probe Fault | Float |  | 0,Normal;1,Alarm | 0 | 1
Unity | 502 | 1 | 2488 | 2 | 0 | Liquid Cooling Communication Parameters | System B Discharge Pressure Probe Fault | Float |  | 0,Normal;1,Alarm | 0 | 1
Unity | 502 | 1 | 2490 | 2 | 0 | Liquid Cooling Communication Parameters | System B Refrigerant Leak or Insufficient | Float |  | 0,Normal;1,Alarm | 0 | 1
Unity | 502 | 1 | 2492 | 2 | 0 | Liquid Cooling Communication Parameters | System B Suction/Discharge Temp Probe Wiring Abnormal | Float |  | 0,Normal;1,Alarm | 0 | 1
Unity | 502 | 1 | 2494 | 2 | 0 | Liquid Cooling Communication Parameters | System B Compressor Communication Fault | Float |  | 0,Normal;1,Alarm | 0 | 1
Unity | 502 | 1 | 2496 | 2 | 0 | Liquid Cooling Communication Parameters | System B Compressor Frequency Abnormal | Float |  | 0,Normal;1,Alarm | 0 | 1
Unity | 502 | 1 | 2498 | 2 | 0 | Liquid Cooling Communication Parameters | System B Pump Communication Fault | Float |  | 0,Normal;1,Alarm | 0 | 1
Unity | 502 | 1 | 2500 | 2 | 0 | Liquid Cooling Communication Parameters | System B Outdoor Unit Communication Fault | Float |  | 0,Normal;1,Alarm | 0 | 1
Unity | 502 | 1 | 2502 | 2 | 0 | Liquid Cooling Communication Parameters | System B Compressor Drive Fault Alarm Lock | Float |  | 0,Normal;1,Alarm | 0 | 1
Unity | 502 | 1 | 2504 | 2 | 0 | Liquid Cooling Communication Parameters | System B Outdoor Fan Drive Fault Alarm Lock | Float |  | 0,Normal;1,Alarm | 0 | 1
Unity | 502 | 1 | 2506 | 2 | 0 | Liquid Cooling Communication Parameters | Circulating Water Pump 2 Drive Fault Alarm Lock | Float |  | 0,Normal;1,Alarm | 0 | 1
Unity | 502 | 1 | 2508 | 2 | 0 | Liquid Cooling Communication Parameters | Circulating Water Pump 2 Overload Alarm | Float |  | 0,Normal;1,Alarm | 0 | 1
Unity | 502 | 1 | 2510 | 2 | 0 | Liquid Cooling Communication Parameters | Circulating Water Pump 2 Overload Alarm Lock | Float |  | 0,Normal;1,Alarm | 0 | 1
Unity | 502 | 1 | 2512 | 2 | 0 | Liquid Cooling Communication Parameters | System A Compressor Frequency | Float | Hz |  | 0 | 1
Unity | 502 | 1 | 2514 | 2 | 0 | Liquid Cooling Communication Parameters | System B Compressor Frequency | Float | Hz |  | 0 | 1
Unity | 502 | 1 | 2516 | 2 | 0 | Fire Protection Communication Parameters | Communication Status | Float |  | 0,Offline;1,Online | 0 | 1
Unity | 502 | 1 | 2518 | 2 | 0 | Fire Protection Communication Parameters | Fault_CO | Float |  | 0,Normal;1,Alarm | 0 | 1
Unity | 502 | 1 | 2520 | 2 | 0 | Fire Protection Communication Parameters | Fault_Temperature | Float |  | 0,Normal;1,Alarm | 0 | 1
Unity | 502 | 1 | 2522 | 2 | 0 | Fire Protection Communication Parameters | Fault_Start | Float |  | 0,Normal;1,Alarm | 0 | 1
Unity | 502 | 1 | 2524 | 2 | 0 | Fire Protection Communication Parameters | Fault_Feedback | Float |  | 0,Normal;1,Alarm | 0 | 1
Unity | 502 | 1 | 2526 | 2 | 0 | Fire Protection Communication Parameters | Fault_IR | Float |  | 0,Normal;1,Alarm | 0 | 1
Unity | 502 | 1 | 2528 | 2 | 0 | Fire Protection Communication Parameters | Fire Alarm_CO | Float |  | 0,Normal;1,Alarm | 0 | 1
Unity | 502 | 1 | 2530 | 2 | 0 | Fire Protection Communication Parameters | Fire Alarm_Temperature | Float |  | 0,Normal;1,Alarm | 0 | 1
Unity | 502 | 1 | 2532 | 2 | 0 | Fire Protection Communication Parameters | Fire Alarm_Start | Float |  | 0,Normal;1,Alarm | 0 | 1
Unity | 502 | 1 | 2534 | 2 | 0 | Fire Protection Communication Parameters | Fire Alarm_Feedback | Float |  | 0,Normal;1,Feedback | 0 | 1
Unity | 502 | 1 | 2536 | 2 | 0 | Fire Protection Communication Parameters | Fire Alarm_IR | Float |  | 0,Normal;1,Alarm | 0 | 1
Unity | 502 | 1 | 2538 | 2 | 0 | Fire Protection Communication Parameters | Temperature Value | Float | ℃ |  | 0 | 1
Unity | 502 | 1 | 2540 | 2 | 0 | Fire Protection Communication Parameters | CO1 | Float |  |  | 0 | 1
Unity | 502 | 1 | 2542 | 2 | 0 | Fire Protection Communication Parameters | CO2 | Float |  |  | 0 | 1
Unity | 502 | 1 | 2544 | 2 | 0 | Fire Protection Communication Parameters | CO3 | Float |  |  | 0 | 1
Unity | 502 | 1 | 2546 | 2 | 0 | Fire Protection Communication Parameters | IR High Position | Float |  |  | 0 | 1
Unity | 502 | 1 | 2548 | 2 | 0 | Fire Protection Communication Parameters | IR Low Position | Float |  |  | 0 | 1
Unity | 502 | 1 | 2550 | 2 | 0 | Fire Protection Communication Parameters | Fault | Float |  | 0,No Fault;1,Fire Extinguisher Activated;2,Sensor Fault;3,2+ Alarms | 0 | 1
Unity | 502 | 1 | 2552 | 2 | 0 | Fire Protection Communication Parameters | Fire Alarm | Float |  | 0,No Fire Alarm;1,CO Fire Alarm;2,Temperature Fire Alarm;3,2+ Fire Alarms;4,Fire Extinguisher Activated | 0 | 1
Unity | 502 | 1 | 2554 | 2 | 0 | Fire Protection Communication Parameters | Fan/Damper Control Module_Fire Alarm | Float |  | 0,Normal;1,Fire Alarm | 0 | 1
Unity | 502 | 1 | 2556 | 2 | 0 | Fire Protection Communication Parameters | Fan/Damper Control Module_Status | Float |  | 0,Stop;8,Open | 0 | 1
Unity | 502 | 1 | 2558 | 2 | 0 | Fire Protection Communication Parameters | Sound/Light Alarm Module_Fire Alarm | Float |  | 0,Normal;1,Fire Alarm | 0 | 1
Unity | 502 | 1 | 2560 | 2 | 0 | Fire Protection Communication Parameters | Sound/Light Alarm Module_Status | Float |  | 0,Stop;8,Open | 0 | 1
Unity | 502 | 1 | 2562 | 2 | 0 | Dehumidifier Communication Parameters | Online Points | Float |  | 0,Offline;1,Online | 0 | 1
Unity | 502 | 1 | 2564 | 2 | 0 | Dehumidifier Communication Parameters | Operating Mode | Float |  | 0,Cooling Type;1,Heating Type | 0 | 1
Unity | 502 | 1 | 2566 | 2 | 0 | Dehumidifier Communication Parameters | Temperature Setting | Float | ℃ |  | 0 | 1
Unity | 502 | 1 | 2568 | 2 | 0 | Dehumidifier Communication Parameters | Temperature Hysteresis | Float | ℃ |  | 0 | 1
Unity | 502 | 1 | 2570 | 2 | 0 | Dehumidifier Communication Parameters | Humidity Setting | Float | % |  | 0 | 1
Unity | 502 | 1 | 2572 | 2 | 0 | Dehumidifier Communication Parameters | Humidity Hysteresis | Float | % |  | 0 | 1
Unity | 502 | 1 | 2574 | 2 | 0 | Dehumidifier Communication Parameters | Communication Device No. | Float |  |  | 0 | 1
Unity | 502 | 1 | 2576 | 2 | 0 | Dehumidifier Communication Parameters | Communication Baud Rate | Float |  |  | 0 | 1
Unity | 502 | 1 | 2578 | 2 | 0 | Dehumidifier Communication Parameters | Controller Internal Temperature | Float | ℃ |  | 0 | 1
Unity | 502 | 1 | 2580 | 2 | 0 | Dehumidifier Communication Parameters | Temperature Control Status | Float |  | 0,Closed;1,Open | 0 | 1
Unity | 502 | 1 | 2582 | 2 | 0 | Dehumidifier Communication Parameters | Humidity Control Method | Float |  | 0,Auto;1,Manual | 0 | 1
Unity | 502 | 1 | 2584 | 2 | 0 | Dehumidifier Communication Parameters | Dehumidification Status | Float |  | 0,Stop;1,Running | 0 | 1
Unity | 502 | 1 | 2586 | 2 | 0 | Dehumidifier Communication Parameters | Current Temperature | Float | ℃ |  | 0 | 1
Unity | 502 | 1 | 2588 | 2 | 0 | Dehumidifier Communication Parameters | Current Humidity | Float | % |  | 0 | 1
Unity | 502 | 1 | 2590 | 2 | 0 | Dehumidifier Communication Parameters | Alarm Status | Float |  | 0,Normal;1,Alarm | 0 | 1
Unity | 502 | 1 | 2592 | 2 | 0 | Dehumidifier Communication Parameters | Dehumidification Switch Control Bit | Float |  | 0,Open;1,Closed | 0 | 1
Unity | 502 | 1 | 2594 | 2 | 0 | Remote Control | Remote Mode | Float |  | 0,Local;1,Remote | 0 | 1
Unity | 502 | 1 | 2596 | 2 | 0 | Remote Control | Remote Control Mode | Float |  | 1,Shutdown;2,Standby;3,Charge;4,Discharge | 0 | 1
Unity | 502 | 1 | 2598 | 2 | 0 | Remote Control | Remote Mode SOC Limit Enable | Float |  | 0,Disabled;1,Enabled | 0 | 1
Unity | 502 | 1 | 2600 | 2 | 0 | Remote Control | Remote Mode Charge Cutoff SOC | Float | % |  | 0 | 1
Unity | 502 | 1 | 2602 | 2 | 0 | Remote Control | Remote Mode Discharge Cutoff SOC | Float | % |  | 0 | 1
Unity | 502 | 1 | 2604 | 2 | 0 | Remote Control | Time Period 1-Start Hour | Float | h |  | 0 | 1
Unity | 502 | 1 | 2606 | 2 | 0 | Remote Control | Time Period 1-Start Minute | Float | min |  | 0 | 1
Unity | 502 | 1 | 2608 | 2 | 0 | Remote Control | Time Period 1-End Hour | Float | h |  | 0 | 1
Unity | 502 | 1 | 2610 | 2 | 0 | Remote Control | Time Period 1-End Minute | Float | min |  | 0 | 1
Unity | 502 | 1 | 2612 | 2 | 0 | Remote Control | Time Period 1 Active Power | Float | kW |  | 0 | 1
Unity | 502 | 1 | 2614 | 2 | 0 | Remote Control | Time Period 2-Start Hour | Float | h |  | 0 | 1
Unity | 502 | 1 | 2616 | 2 | 0 | Remote Control | Time Period 2-Start Minute | Float | min |  | 0 | 1
Unity | 502 | 1 | 2618 | 2 | 0 | Remote Control | Time Period 2-End Hour | Float | h |  | 0 | 1
Unity | 502 | 1 | 2620 | 2 | 0 | Remote Control | Time Period 2-End Minute | Float | min |  | 0 | 1
Unity | 502 | 1 | 2622 | 2 | 0 | Remote Control | Time Period 2 Active Power | Float | kW |  | 0 | 1
Unity | 502 | 1 | 2624 | 2 | 0 | Remote Control | Time Period 3-Start Hour | Float | h |  | 0 | 1
Unity | 502 | 1 | 2626 | 2 | 0 | Remote Control | Time Period 3-Start Minute | Float | min |  | 0 | 1
Unity | 502 | 1 | 2628 | 2 | 0 | Remote Control | Time Period 3-End Hour | Float | h |  | 0 | 1
Unity | 502 | 1 | 2630 | 2 | 0 | Remote Control | Time Period 3-End Minute | Float | min |  | 0 | 1
Unity | 502 | 1 | 2632 | 2 | 0 | Remote Control | Time Period 3 Active Power | Float | kW |  | 0 | 1
Unity | 502 | 1 | 2634 | 2 | 0 | Remote Control | Time Period 4-Start Hour | Float | h |  | 0 | 1
Unity | 502 | 1 | 2636 | 2 | 0 | Remote Control | Time Period 4-Start Minute | Float | min |  | 0 | 1
Unity | 502 | 1 | 2638 | 2 | 0 | Remote Control | Time Period 4-End Hour | Float | h |  | 0 | 1
Unity | 502 | 1 | 2640 | 2 | 0 | Remote Control | Time Period 4-End Minute | Float | min |  | 0 | 1
Unity | 502 | 1 | 2642 | 2 | 0 | Remote Control | Time Period 4 Active Power | Float | kW |  | 0 | 1
Unity | 502 | 1 | 2644 | 2 | 0 | Remote Control | Time Period 5-Start Hour | Float | h |  | 0 | 1
Unity | 502 | 1 | 2646 | 2 | 0 | Remote Control | Time Period 5-Start Minute | Float | min |  | 0 | 1
Unity | 502 | 1 | 2648 | 2 | 0 | Remote Control | Time Period 5-End Hour | Float | h |  | 0 | 1
Unity | 502 | 1 | 2650 | 2 | 0 | Remote Control | Time Period 5-End Minute | Float | min |  | 0 | 1
Unity | 502 | 1 | 2652 | 2 | 0 | Remote Control | Time Period 5 Active Power | Float | kW |  | 0 | 1
Unity | 502 | 1 | 2654 | 2 | 0 | Remote Control | Time Period 6-Start Hour | Float | h |  | 0 | 1
Unity | 502 | 1 | 2656 | 2 | 0 | Remote Control | Time Period 6-Start Minute | Float | min |  | 0 | 1
Unity | 502 | 1 | 2658 | 2 | 0 | Remote Control | Time Period 6-End Hour | Float | h |  | 0 | 1
Unity | 502 | 1 | 2660 | 2 | 0 | Remote Control | Time Period 6-End Minute | Float | min |  | 0 | 1
Unity | 502 | 1 | 2662 | 2 | 0 | Remote Control | Time Period 6 Active Power | Float | kW |  | 0 | 1
Unity | 502 | 1 | 2664 | 2 | 0 | Remote Control | Time Period 7-Start Hour | Float | h |  | 0 | 1
Unity | 502 | 1 | 2666 | 2 | 0 | Remote Control | Time Period 7-Start Minute | Float | min |  | 0 | 1
Unity | 502 | 1 | 2668 | 2 | 0 | Remote Control | Time Period 7-End Hour | Float | h |  | 0 | 1
Unity | 502 | 1 | 2670 | 2 | 0 | Remote Control | Time Period 7-End Minute | Float | min |  | 0 | 1
Unity | 502 | 1 | 2672 | 2 | 0 | Remote Control | Time Period 7 Active Power | Float | kW |  | 0 | 1
Unity | 502 | 1 | 2674 | 2 | 0 | Remote Control | Time Period 8-Start Hour | Float | h |  | 0 | 1
Unity | 502 | 1 | 2676 | 2 | 0 | Remote Control | Time Period 8-Start Minute | Float | min |  | 0 | 1
Unity | 502 | 1 | 2678 | 2 | 0 | Remote Control | Time Period 8-End Hour | Float | h |  | 0 | 1
Unity | 502 | 1 | 2680 | 2 | 0 | Remote Control | Time Period 8-End Minute | Float | min |  | 0 | 1
Unity | 502 | 1 | 2682 | 2 | 0 | Remote Control | Time Period 8 Active Power | Float | kW |  | 0 | 1
Unity | 502 | 1 | 2684 | 2 | 0 | Remote Control | Time Period 9-Start Hour | Float | h |  | 0 | 1
Unity | 502 | 1 | 2686 | 2 | 0 | Remote Control | Time Period 9-Start Minute | Float | min |  | 0 | 1
Unity | 502 | 1 | 2688 | 2 | 0 | Remote Control | Time Period 9-End Hour | Float | h |  | 0 | 1
Unity | 502 | 1 | 2690 | 2 | 0 | Remote Control | Time Period 9-End Minute | Float | min |  | 0 | 1
Unity | 502 | 1 | 2692 | 2 | 0 | Remote Control | Time Period 9 Active Power | Float | kW |  | 0 | 1
Unity | 502 | 1 | 2694 | 2 | 0 | Remote Control | Time Period 10-Start Hour | Float | h |  | 0 | 1
Unity | 502 | 1 | 2696 | 2 | 0 | Remote Control | Time Period 10-Start Minute | Float | min |  | 0 | 1
Unity | 502 | 1 | 2698 | 2 | 0 | Remote Control | Time Period 10-End Hour | Float | h |  | 0 | 1
Unity | 502 | 1 | 2700 | 2 | 0 | Remote Control | Time Period 10-End Minute | Float | min |  | 0 | 1
Unity | 502 | 1 | 2702 | 2 | 0 | Remote Control | Time Period 10 Active Power | Float | kW |  | 0 | 1
Unity | 502 | 1 | 2704 | 2 | 0 | Remote Control | System Fault Reset | Float |  | 0,Normal;1,Reset | 0 | 1
Unity | 502 | 1 | 2706 | 2 | 0 | Grid Meter Communication Parameters | Communication Status | Float |  | 0,Offline;1,Online | 0 | 1
Unity | 502 | 1 | 2708 | 2 | 0 | Grid Meter Communication Parameters | Phase A Voltage | Float | V |  | 0 | 1
Unity | 502 | 1 | 2710 | 2 | 0 | Grid Meter Communication Parameters | Phase B Voltage | Float | V |  | 0 | 1
Unity | 502 | 1 | 2712 | 2 | 0 | Grid Meter Communication Parameters | Phase C Voltage | Float | V |  | 0 | 1
Unity | 502 | 1 | 2714 | 2 | 0 | Grid Meter Communication Parameters | AB Line Voltage | Float | V |  | 0 | 1
Unity | 502 | 1 | 2716 | 2 | 0 | Grid Meter Communication Parameters | BC Line Voltage | Float | V |  | 0 | 1
Unity | 502 | 1 | 2718 | 2 | 0 | Grid Meter Communication Parameters | CA Line Voltage | Float | V |  | 0 | 1
Unity | 502 | 1 | 2720 | 2 | 0 | Grid Meter Communication Parameters | Phase A Current | Float | A |  | 0 | 1
Unity | 502 | 1 | 2722 | 2 | 0 | Grid Meter Communication Parameters | Phase B Current | Float | A |  | 0 | 1
Unity | 502 | 1 | 2724 | 2 | 0 | Grid Meter Communication Parameters | Phase C Current | Float | A |  | 0 | 1
Unity | 502 | 1 | 2726 | 2 | 0 | Grid Meter Communication Parameters | Phase N Current | Float | A |  | 0 | 1
Unity | 502 | 1 | 2728 | 2 | 0 | Grid Meter Communication Parameters | Phase A Active Power | Float | kW |  | 0 | 1
Unity | 502 | 1 | 2730 | 2 | 0 | Grid Meter Communication Parameters | Phase B Active Power | Float | kW |  | 0 | 1
Unity | 502 | 1 | 2732 | 2 | 0 | Grid Meter Communication Parameters | Phase C Active Power | Float | kW |  | 0 | 1
Unity | 502 | 1 | 2734 | 2 | 0 | Grid Meter Communication Parameters | Total Active Power | Float | kW |  | 0 | 1
Unity | 502 | 1 | 2736 | 2 | 0 | Grid Meter Communication Parameters | Phase A Reactive Power | Float | kvar |  | 0 | 1
Unity | 502 | 1 | 2738 | 2 | 0 | Grid Meter Communication Parameters | Phase B Reactive Power | Float | kvar |  | 0 | 1
Unity | 502 | 1 | 2740 | 2 | 0 | Grid Meter Communication Parameters | Phase C Reactive Power | Float | kvar |  | 0 | 1
Unity | 502 | 1 | 2742 | 2 | 0 | Grid Meter Communication Parameters | Total Reactive Power | Float | kvar |  | 0 | 1
Unity | 502 | 1 | 2744 | 2 | 0 | Grid Meter Communication Parameters | Phase A Apparent Power | Float | kVA |  | 0 | 1
Unity | 502 | 1 | 2746 | 2 | 0 | Grid Meter Communication Parameters | Phase B Apparent Power | Float | kVA |  | 0 | 1
Unity | 502 | 1 | 2748 | 2 | 0 | Grid Meter Communication Parameters | Phase C Apparent Power | Float | kVA |  | 0 | 1
Unity | 502 | 1 | 2750 | 2 | 0 | Grid Meter Communication Parameters | Total Apparent Power | Float | kVA |  | 0 | 1
Unity | 502 | 1 | 2752 | 2 | 0 | Grid Meter Communication Parameters | Phase A Power Factor | Float |  |  | 0 | 1
Unity | 502 | 1 | 2754 | 2 | 0 | Grid Meter Communication Parameters | Phase B Power Factor | Float |  |  | 0 | 1
Unity | 502 | 1 | 2756 | 2 | 0 | Grid Meter Communication Parameters | Phase C Power Factor | Float |  |  | 0 | 1
Unity | 502 | 1 | 2758 | 2 | 0 | Grid Meter Communication Parameters | Total Power Factor | Float |  |  | 0 | 1
Unity | 502 | 1 | 2760 | 2 | 0 | Grid Meter Communication Parameters | Frequency | Float | Hz |  | 0 | 1
Unity | 502 | 1 | 2762 | 2 | 0 | Grid Meter Communication Parameters | Reserved Phase Voltage Average | Float | V |  | 0 | 1
Unity | 502 | 1 | 2764 | 2 | 0 | Grid Meter Communication Parameters | Reserved Line Voltage Average | Float | V |  | 0 | 1
Unity | 502 | 1 | 2766 | 2 | 0 | Grid Meter Communication Parameters | Reserved Current Average | Float | V |  | 0 | 1
Unity | 502 | 1 | 2768 | 2 | 0 | Grid Meter Communication Parameters | Voltage Unbalance | Float | % |  | 0 | 1
Unity | 502 | 1 | 2770 | 2 | 0 | Grid Meter Communication Parameters | Current Unbalance | Float | % |  | 0 | 1
Unity | 502 | 1 | 2772 | 2 | 0 | Grid Meter Communication Parameters | Reserved Zero-Sequence Voltage | Float | V |  | 0 | 1
Unity | 502 | 1 | 2774 | 2 | 0 | Grid Meter Communication Parameters | Reserved Zero-Sequence Current | Float | A |  | 0 | 1
Unity | 502 | 1 | 2776 | 2 | 0 | Grid Meter Communication Parameters | Reserved Phase A Power Angle | Float | ° |  | 0 | 1
Unity | 502 | 1 | 2778 | 2 | 0 | Grid Meter Communication Parameters | Reserved Phase B Power Angle | Float | ° |  | 0 | 1
Unity | 502 | 1 | 2780 | 2 | 0 | Grid Meter Communication Parameters | Reserved Phase C Power Angle | Float | ° |  | 0 | 1
Unity | 502 | 1 | 2782 | 2 | 0 | Grid Meter Communication Parameters | Phase A Voltage Angle | Float | ° |  | 0 | 1
Unity | 502 | 1 | 2784 | 2 | 0 | Grid Meter Communication Parameters | Phase B Voltage Angle | Float | ° |  | 0 | 1
Unity | 502 | 1 | 2786 | 2 | 0 | Grid Meter Communication Parameters | Phase C Voltage Angle | Float | ° |  | 0 | 1
Unity | 502 | 1 | 2788 | 2 | 0 | Grid Meter Communication Parameters | Phase A Current Angle | Float | ° |  | 0 | 1
Unity | 502 | 1 | 2790 | 2 | 0 | Grid Meter Communication Parameters | Phase B Current Angle | Float | ° |  | 0 | 1
Unity | 502 | 1 | 2792 | 2 | 0 | Grid Meter Communication Parameters | Phase C Current Angle | Float | ° |  | 0 | 1
Unity | 502 | 1 | 2794 | 2 | 0 | Grid Meter Communication Parameters | Reserved Internal Temperature | Float | ℃ |  | 0 | 1
Unity | 502 | 1 | 2796 | 2 | 0 | Grid Meter Communication Parameters | Temperature 1 | Float | ℃ |  | 0 | 1
Unity | 502 | 1 | 2798 | 2 | 0 | Grid Meter Communication Parameters | Temperature 2 | Float | ℃ |  | 0 | 1
Unity | 502 | 1 | 2800 | 2 | 0 | Grid Meter Communication Parameters | Temperature 3 | Float | ℃ |  | 0 | 1
Unity | 502 | 1 | 2802 | 2 | 0 | Grid Meter Communication Parameters | Temperature 4 | Float | ℃ |  | 0 | 1
Unity | 502 | 1 | 2804 | 2 | 0 | Grid Meter Communication Parameters | Leakage 1 | Float | A |  | 0 | 1
Unity | 502 | 1 | 2806 | 2 | 0 | Grid Meter Communication Parameters | Total Active Energy | Float | kWh |  | 0 | 1
Unity | 502 | 1 | 2808 | 2 | 0 | Grid Meter Communication Parameters | Forward Total Active Energy | Float | kWh |  | 0 | 1
Unity | 502 | 1 | 2810 | 2 | 0 | Grid Meter Communication Parameters | Reverse Total Active Energy | Float | kWh |  | 0 | 1
Unity | 502 | 1 | 2812 | 2 | 0 | Grid Meter Communication Parameters | Over-Voltage Alarm | Float |  | 0,Normal;1,Alarm | 0 | 1
Unity | 502 | 1 | 2814 | 2 | 0 | Grid Meter Communication Parameters | Under-Voltage Alarm | Float |  | 0,Normal;1,Alarm | 0 | 1
Unity | 502 | 1 | 2816 | 2 | 0 | Grid Meter Communication Parameters | Over-Current Alarm | Float |  | 0,Normal;1,Alarm | 0 | 1
Unity | 502 | 1 | 2818 | 2 | 0 | Grid Meter Communication Parameters | Under-Current Alarm | Float |  | 0,Normal;1,Alarm | 0 | 1
Unity | 502 | 1 | 2820 | 2 | 0 | Grid Meter Communication Parameters | Over-Power Alarm | Float |  | 0,Normal;1,Alarm | 0 | 1
Unity | 502 | 1 | 2822 | 2 | 0 | Grid Meter Communication Parameters | Under-Power Alarm | Float |  | 0,Normal;1,Alarm | 0 | 1
Unity | 502 | 1 | 2824 | 2 | 0 | Grid Meter Communication Parameters | DO1 Alarm Output | Float |  | 0,Normal;1,Alarm | 0 | 1
Unity | 502 | 1 | 2826 | 2 | 0 | Grid Meter Communication Parameters | DO2 Alarm Output | Float |  | 0,Normal;1,Alarm | 0 | 1
Unity | 502 | 1 | 2828 | 2 | 0 | Grid Meter Communication Parameters | Phase A Loss-of-Current Alarm | Float |  | 0,Normal;1,Alarm | 0 | 1
Unity | 502 | 1 | 2830 | 2 | 0 | Grid Meter Communication Parameters | Phase B Loss-of-Current Alarm | Float |  | 0,Normal;1,Alarm | 0 | 1
Unity | 502 | 1 | 2832 | 2 | 0 | Grid Meter Communication Parameters | Phase C Loss-of-Current Alarm | Float |  | 0,Normal;1,Alarm | 0 | 1
Unity | 502 | 1 | 2834 | 2 | 0 | Grid Meter Communication Parameters | Phase A Loss-of-Voltage Alarm | Float |  | 0,Normal;1,Alarm | 0 | 1
Unity | 502 | 1 | 2836 | 2 | 0 | Grid Meter Communication Parameters | Phase B Loss-of-Voltage Alarm | Float |  | 0,Normal;1,Alarm | 0 | 1
Unity | 502 | 1 | 2838 | 2 | 0 | Grid Meter Communication Parameters | Phase C Loss-of-Voltage Alarm | Float |  | 0,Normal;1,Alarm | 0 | 1
Unity | 502 | 1 | 2840 | 2 | 0 | Grid Meter Communication Parameters | Phase Sequence Error Alarm | Float |  | 0,Normal;1,Alarm | 0 | 1
Unity | 502 | 1 | 2842 | 2 | 0 | Grid Meter Communication Parameters | Power-Off Report | Float |  | 0,Invalid;1,Valid | 0 | 1