## History Record
History Record
Time | Version | Modify Content | Modifier | Approver
2025-03-12 | V01 | 1st release
2025-03-14 | V02 | Setting sheet, Holding Register Address 9 & 10 Meaning; Register address Hex value Rack Data sheet, Rack data address 20 & 21 Notes;
3-28-2025 | V03 | Add Alarm state-Temp&Humidity; Fault code, supply&return-Inlet&Outlet-Chiller;Fault reset description
4-2-2025 | V04 | Temp&Humidity, Alarm State, add value 3 = temp and humi to remark
2025-04-14 |  | Precision added
4-17-2025 | V05 | add 20 chiller's parameters to softare interface,delete CoolTemp_Up_Limit_Lev1

## System Data
Register Type | Register Address |  | Attributes | Meaning | Data Types | Coefficient | Offset | Units | Decimal pointPrecision required | Unit | Remarks | 说明
| Hexadecimal | Decimal
Battery system data (Modbus address is 1, input register, Function code 0x04) | 0000 | 0 | RO | Protocol version | UINT16
| 0001 | 1 | RO | Battery system state/Container state | UINT16 | [5 empty] | 0x1111:NoChg 0x2222:NoDchg 0x5555:Standby 0xAAAA:Fault 0xBBBB:Normal 0xCCCC:Warn
| 0002 | 2 | RO | Installed battery racks no./ How many racks are installed | UINT16 | [5 empty] | Value Range: 1 ~ 16
| 0003 | 3 | RO | Operate battery racks no./ How many racks are operating | UINT16 | [5 empty] | Value Range: 1 ~ 16
| 0004 | 4 | RO | Flag of operate racks/ Rack position, which rack are operating or not | UINT16 | [5 empty] | Bit0:rack1..rack15:rack16 | 0-未投入，1-投入 0- not operating，1- operating
| 0005 | 5 | RO | Max SOC rack no. | UINT16 | [5 empty] | Value Range: 1 ~ 16
| 0006 | 6 | RO | Min SOC rack no. | UINT16 | [5 empty] | Value Range: 1 ~ 16
| 0007 | 7 | RO | Max Volt rack no. | UINT16 | [5 empty] | Value Range: 1 ~ 16
| 0008 | 8 | RO | Min Volt rack no. | UINT16 | [5 empty] | Value Range: 1 ~ 16
| 0009 | 9 | RO | Max cell voltage rack no. | UINT16 | [5 empty] | Value Range: 1 ~ 16
| 000A | 10 | RO | Max cell voltage cell no. in a rack | UINT16 | [5 empty] | Value Range: 1 ~ 600
| 000B | 11 | RO | Min cell voltage rack no. | UINT16 | [5 empty] | Value Range: 1 ~ 16
| 000C | 12 | RO | Min cell voltage cell no. in a rack | UINT16 | [5 empty] | Value Range: 1 ~ 600
| 000D | 13 | RO | Max cell temperature rack no. | UINT16 | [5 empty] | Value Range: 1 ~ 16
| 000E | 14 | RO | Max cell temperature cell no. in a rack | UINT16 | [5 empty] | Value Range: 1 ~ 600
| 000F | 15 | RO | Min cell temperature rack no. | UINT16 | [5 empty] | Value Range: 1 ~ 16
| 0010 | 16 | RO | Min cell temperature cell no. in a rack | UINT16 | [5 empty] | Value Range: 1 ~ 600
| 0011 | 17 | RO | reserve | UINT16 | [5 empty] | 1--close， 0--open
| 0012 | 18 | RO | reserve | UINT16 | [5 empty] | 1--close， 0--open
| 0013 | 19 | RO | Digital input 2, Emergency stop | UINT16 | [5 empty] | 1--close， 0--open
| 0014 | 20 | RO | Digital input 3, Busbar cabinet door | UINT16 | [5 empty] | 1--close， 0--open
| 0015 | 21 | RO | Digital input 4, 220V switch feedback | UINT16 | [5 empty] | 1--close， 0--open
| 0016 | 22 | RO | Digital input 5, 220V switch alarm | UINT16 | [5 empty] | 1--close， 0--open
| 0017 | 23 | RO | Digital input 6, Container door | UINT16 | [5 empty] | 1--close， 0--open
| 0018 | 24 | RO | Digital input 7, UPS fault dry contact | UINT16 | [5 empty] | 1--close， 0--open
| 0019 | 25 | RO | Digital input 8, FSS Warn | UINT16 | [5 empty] | 1--close， 0--open
| 001A | 26 | RO | Digital input 9, FSS Alarm | UINT16 | [5 empty] | 1--close， 0--open
| 001B | 27 | RO | Digital input 10, FSS Malfunction | UINT16 | [5 empty] | 1--close， 0--open
| 001C | 28 | RO | Digital input 11, Fan Malfunction | UINT16 | [5 empty] | 1--close， 0--open
| 001D | 29 | RO | Digital input 12, Gas detector Malfunction | UINT16 | [5 empty] | 1--close， 0--open
| 001E | 30 | RO | Digital input 13, Aerosol Spray Feedback | UINT16 | [5 empty] | 1--close， 0--open
| 001F | 31 | RO | reserve | UINT16 | [5 empty] | 1--close， 0--open
| 0020 | 32 | RO | reserve | UINT16 | [5 empty] | 1--close， 0--open
The Above is the data of the UINT16 type , and the following is the data of the FLOAT Type
| 0033 | 51 | RO | System total voltage | FLOAT | 1 | 0 | V | 0.1 | V | average
| 0035 | 53 | RO | System total current | FLOAT | 1 | 0 | A | 0.1 | A | sum of each rack
| 0037 | 55 | RO | System SOC | FLOAT | 1 | 0 | % | 1 | % | average
| 0039 | 57 | RO | System SOH | FLOAT | 1 | 0 | % | 1 | % | average
| 003B | 59 | RO | Capacity during charing | FLOAT | 1 | 0 | kWh | 0.1 | kwh
| 003D | 61 | RO | Capacity during discharging | FLOAT | 1 | 0 | kWh | 0.1 | kwh
| 003F | 63 | RO | Capacity full charge | FLOAT | 1 | 0 | kWh | 0.1 | kwh
| 0041 | 65 | RO | Capacity full discharge | FLOAT | 1 | 0 | kWh | 0.1 | kwh
| 0043 | 67 | RO | Accumulated charge capacity | FLOAT | 1 | 0 | kWh | 0.1 | kwh
| 0045 | 69 | RO | Accumulated discharge capacity | FLOAT | 1 | 0 | kWh | 0.1 | kwh
| 0047 | 71 | RO | Cell volt difference between system/ all the cells | FLOAT | 1 | 0 | V | 0.1 | V
| 0049 | 73 | RO | Max cell voltage in system | FLOAT | 1 | 0 | V | 0.001 | V
| 004B | 75 | RO | Min cell voltage in system | FLOAT | 1 | 0 | V | 0.001 | V
| 004D | 77 | RO | Cell temp. difference between system/ all the cells | FLOAT | 1 | 0 | ℃ | 0.1 | ℃
| 004F | 79 | RO | Max cell temp. in system | FLOAT | 1 | 0 | ℃ | 0.1 | ℃
| 0051 | 81 | RO | Min cell temp. in system | FLOAT | 1 | 0 | ℃ | 0.1 | ℃
| 0053 | 83 | RO | Rack SOC difference between system/ all the racks | FLOAT | 1 | 0 | % | 1 | %
| 0055 | 85 | RO | Max rack SOC in system | FLOAT | 1 | 0 | % | 1 | %
| 0057 | 87 | RO | Min rack SOC in system | FLOAT | 1 | 0 | % | 1 | %
| 0059 | 89 | RO | Rack volt difference between system/ all the racks | FLOAT | 1 | 0 | V | 0.1 | V
| 005B | 91 | RO | Max rack volt in system | FLOAT | 1 | 0 | V | 0.1 | V
| 005D | 93 | RO | Min rack volt in system | FLOAT | 1 | 0 | V | 0.1 | V
| 005F | 95 | RO | Max power will system allow for charging (settable value) | FLOAT | 1 | 0 | kW | 0.1 | kw
| 0061 | 97 | RO | Max power will system allow for discharging (settable value) | FLOAT | 1 | 0 | kW | 0.1 | kw
| 0063 | 99 | RO | Max current will system allow for charging (settable value) | FLOAT | 1 | 0 | A | 0.1 | A
| 0065 | 101 | RO | Max current will system allow for discharging (settable value) | FLOAT | 1 | 0 | A | 0.1 | A
1. BAMS transfer data is divided into 4 parts: System data, System alarm, Rack data, Rack alarm and Cell data.
2. System data, system alarm Mobus address is 1.
3. Rack data, Rack alarm, Cell data use one Modbus address per rack (starting from 2).
For example, if system has16 battery racks, the Modbus addresses of the 16 racks are 2, 3, 4, 5, 6, 7, 8, 9, 10, 11, 12, 13, 14, 15, 16, 17.
4. Discrete input register Modbus function code 0x02, save register Modbus function code 0x03, input register Modbus function code 0x04
5. Support Modbus TCP and Modbus RTU protocols.
6. UINT16 is 1 register and 2 bytes, FLOAT is 2 registers and 4 bytes.

## System Alarm
Register Type | Register Address |  | Attributes | Meaning | Data Types | Coefficient | Offset | Units | Remarks
| Hexadecimal | Decimal
System Alarm (Modbus address 1, discrete register, function code 0x02) | 1 | 1 | RO | Emergency stop |  |  |  |  | 0--normal，1--emergency stop
| 2 | 2 | RO | [5 empty] | 0--normal，1--warning
| 3 | 3 | RO | Fire start |  |  |  |  | 0--normal，1--start
| 4 | 4 | RO | Fire fault |  |  |  |  | 0--normal，1--fault
| 5 | 5 | RO | Water alarm |  |  |  |  | 0--normal，1--alarm
| 6 | 6 | RO | Combustible gas alarm |  |  |  |  | 0--normal，1--alarm
| 7 | 7 | RO | Access control status/ Container door |  |  |  |  | 0--normal，1--alarm
| 8 | 8 | RO | PCS communication fault |  |  |  |  | 0--normal，1--fault
| 9 | 9 | RO | EMS communication fault |  |  |  |  | 0--normal，1--fault
| 000A | 10 | RO | State of busbar switch at DC Combiner |  |  |  |  | 0--normal，1--close
| 000B | 11 | RO | Extra IO module communication fault |  |  |  |  | 0--normal，1--fault
|  | 12 |  | Digital input 3, Busbar cabinet door
|  | 13 |  | Digital input 4, 220V switch feedback
|  | 14 |  | Digital input 5, 220V switch alarm
|  | 15 |  | Digital input 7, UPS fault dry contact
|  | 16 |  | Digital input 11, Fan Malfunction
|  | 17 |  | Digital input 13, Aerosol Spray Feedback
|  | 18 |  | reserve
|  | 19 |  | reserve
|  | 20 |  | reserve
|  | 21 |  | reserve

## Rack Data
Register Type | Register Address |  | Attributes | Meaning | Data Types | Coefficient | Offset | Units | Decimal pointPrecision required | Unit | Remarks
| Hexadecimal | Decimal
Rack data (each Modbus address independent, starting from 2, input register,function code 0x04) | 1 | 1 | RO | Rack state | UINT16 | 1 | 0 |  |  |  | 0x1111:NoChg 0x2222:NoDchg 0x5555:Standby 0xAAAA:Fault 0xBBBB:Normal 0xCCCC:Warn
| 2 | 2 | RO | Rack state of charge and dischage | UINT16 | 1 | 0 |  |  |  | 1 - Open 2 - standby(Stby) 3 - charge(Chg) 4 - discharge(Dchg)
| 3 | 3 | RO | No. cell in a rack | UINT16 | 1 | 0 |  |  |  | Value Range: 1 ~ 600
| 4 | 4 | RO | No. cell temp. sensor in a rack | UINT16 | 1 | 0 |  |  |  | Value Range: 1 ~ 600
| 5 | 5 | RO | No. pack in a rack | UINT16 | 1 | 0 |  |  |  | Value Range: 1 ~ 50
| 6 | 6 | RO | Rack Charge count no's | UINT16 | 1 | 0 |  |  |  | 5 min charging +1
| 7 | 7 | RO | Rack Discharge count no's | UINT16 | 1 | 0 |  |  |  | 5 min discharging +1
| 8 | 8 | RO | Each individual rack will show cell no. of max cell voltage | UINT16 | 1 | 0 |  |  |  | Value Range: 1 ~ 600
| 9 | 9 | RO | Each individual rack will show cell no. of min cell voltage | UINT16 | 1 | 0 |  |  |  | Value Range: 1 ~ 600
| 000A | 10 | RO | Each individual rack will show cell no. of max cell temp. | UINT16 | 1 | 0 |  |  |  | Value Range: 1 ~ 600
| 000B | 11 | RO | Each individual rack will show cell no. of min cell temp. | UINT16 | 1 | 0 |  |  |  | Value Range: 1 ~ 600
| 000C | 12 | RO | Each individual rack will show cell no. of max cell internal resistance | UINT16 | 1 | 0 |  |  |  | Value Range: 1 ~ 600
| 000D | 13 | RO | Each individual rack will show cell no. of min cell internal resistance | UINT16 | 1 | 0 |  |  |  | Value Range: 1 ~ 600
| 000E | 14 | RO | Each individual rack will show cell no. of max cell SOC | UINT16 | 1 | 0 |  |  |  | Value Range: 1 ~ 600
| 000F | 15 | RO | Each individual rack will show cell no. of min cell SOC | UINT16 | 1 | 0 |  |  |  | Value Range: 1 ~ 600
| 10 | 16 | RO | Each individual rack will show cell no. of max cell SOH | UINT16 | 1 | 0 |  |  |  | Value Range: 1 ~ 600
| 11 | 17 | RO | Each individual rack will show cell no. of min cell SOH | UINT16 | 1 | 0 |  |  |  | Value Range: 1 ~ 600
| 12 | 18 | RO | Digital input 1 of BCMU | UINT16 | 1 | 0 |  |  |  | 1--close, 0--open | Positive DC contactor state feedback
| 13 | 19 | RO | Digital input 2 of BCMU | UINT16 | 1 | 0 |  |  |  | 1--close, 0--open | Negative DC contactor state feedback
| 14 | 20 | RO | Digital input 3 of BCMU | UINT16 | 1 | 0 |  |  |  | 1--close, 0--open | MCB state feedback
| 15 | 21 | RO | Digital input 4 of BCMU | UINT16 | 1 | 0 |  |  |  | 1--close, 0--open | Fuse feedback
| 16 | 22 | RO | Digital input 5 of BCMU | UINT16 | 1 | 0 |  |  |  | 1--close, 0--open
| 17 | 23 | RO | Digital input 6 of BCMU | UINT16 | 1 | 0 |  |  |  | 1--close, 0--open
| 18 | 24 | RO | reserve | UINT16 | [5 empty] | 1--close, 0--open
| 19 | 25 | RO | reserve | UINT16 | [5 empty] | 1--close, 0--open
| 001A | 26 | RO | reserve | UINT16 | [5 empty] | 1--close, 0--open
| 001B | 27 | RO | reserve | UINT16 | [5 empty] | 1--close, 0--open
| 001C | 28 | RO | reserve | UINT16 | [5 empty] | 1--close, 0--open
The Above is the data of the UINT16 type , and the following is the data of the FLOAT Type
| 33 | 51 | RO | Each individual racks will show total rack voltage | FLOAT | 1 | 0 | V | 0.1 | V
| 35 | 53 | RO | Each individual racks will show total rack Current | FLOAT | 1 | 0 | A | 0.1 | A
| 37 | 55 | RO | Each individual racks will show total rack SOC | FLOAT | 1 | 0 | % | 1 | %
| 39 | 57 | RO | Each individual racks will show total rack SOH | FLOAT | 1 | 0 | % | 1 | %
| 003B | 59 | RO | HV box ambient temp | FLOAT | 1 | 0 | ℃ | 0.1 | ℃
| 003D | 61 | RO | Rack positive insulation resistance | FLOAT | 1 | 0 | MΩ | 1 | MΩ
| 003F | 63 | RO | Rack negative insulation resistance | FLOAT | 1 | 0 | MΩ | 1 | MΩ
| 41 | 65 | RO | Capacity during charing | FLOAT | 1 | 0 | kWh | 0.1 | kwh
| 43 | 67 | RO | Capacity during discharging | FLOAT | 1 | 0 | kWh | 0.1 | kwh
| 45 | 69 | RO | Capacity full charge | FLOAT | 1 | 0 | kWh | 0.1 | kwh
| 47 | 71 | RO | Capacity full discharge | FLOAT | 1 | 0 | kWh | 0.1 | kwh
| 49 | 73 | RO | Accumulated charge capacity | FLOAT | 1 | 0 | kWh | 0.1 | kwh
| 004B | 75 | RO | Accumulated discharge capacity | FLOAT | 1 | 0 | kWh | 0.1 | kwh
| 004D | 77 | RO | Cell volt difference between rack | FLOAT | 1 | 0 | V | 0.001 | V
| 004F | 79 | RO | Average cell voltage | FLOAT | 1 | 0 | V | 0.001 | V
| 51 | 81 | RO | Max cell voltage | FLOAT | 1 | 0 | V | 0.001 | V
| 53 | 83 | RO | Min cell voltage | FLOAT | 1 | 0 | V | 0.001 | V
| 55 | 85 | RO | Cell temp. difference between rack | FLOAT | 1 | 0 | ℃ | 0.1 | ℃
| 57 | 87 | RO | Avg cell temp | FLOAT | 1 | 0 | ℃ | 0.1 | ℃
| 59 | 89 | RO | Max cell temp | FLOAT | 1 | 0 | ℃ | 0.1 | ℃
| 005B | 91 | RO | Min cell temp | FLOAT | 1 | 0 | ℃ | 0.1 | ℃
| 005D | 93 | RO | Avg cell internal resistance | FLOAT | 1 | 0 | mΩ | 1 | mΩ
| 005F | 95 | RO | Max cell internal resistance | FLOAT | 1 | 0 | mΩ | 1 | mΩ
| 61 | 97 | RO | Min cell internal resistance | FLOAT | 1 | 0 | mΩ | 1 | mΩ
| 63 | 99 | RO | Avg cell SOC | FLOAT | 1 | 0 | % | 1 | %
| 65 | 101 | RO | Max cell SOC | FLOAT | 1 | 0 | % | 1 | %
| 67 | 103 | RO | Min cell SOC | FLOAT | 1 | 0 | % | 1 | %
| 69 | 105 | RO | Avg cell SOH | FLOAT | 1 | 0 | % | 1 | %
| 006B | 107 | RO | Max cell SOH | FLOAT | 1 | 0 | % | 1 | %
| 006D | 109 | RO | Min cell SOH | FLOAT | 1 | 0 | % | 1 | %
| 006F | 111 | RO | Max power will rack allow for charging (settable value) | FLOAT | 1 | 0 | kW | 0.1 | kw | BMS power down use
| 71 | 113 | RO | Max power will rack allow for discharging (settable value) | FLOAT | 1 | 0 | kW | 0.1 | kw | BMS power down use
| 73 | 115 | RO | Max current will rack allow for charging (settable value) | FLOAT | 1 | 0 | A | 0.1 | A | BMS power down use
| 75 | 117 | RO | Max current will rack allow for discharging (settable value) | FLOAT | 1 | 0 | A | 0.1 | A | BMS power down use
| 77 | 119 | RO | HV box ambient temp 2 | FLOAT | 1 | 0 | ℃
| 79 | 121 | RO | HV box ambient temp 3 | FLOAT | 1 | 0 | ℃
| 007B | 123 | RO | HV box ambient temp 4 | FLOAT | 1 | 0 | ℃

## Rack Alarm
Register Type | Register Address |  | Attributes | Meaning | Data Types | Coefficient | Offset | Units | Remarks
| Hexadecimal | Decimal
Rack alarm (each Modbus address independent, starting from 2, discrete input registers, function code 0x02) | 0001 | 1 | RO | rack voltage upper limit warning |  |  |  |  | 0--no alarm, 1--alarm
| 0002 | 2 | RO | rack voltage lower limit warning |  |  |  |  | 0--no alarm, 1--alarm
| 0003 | 3 | RO | charge current upper limit warning |  |  |  |  | 0--no alarm, 1--alarm
| 0004 | 4 | RO | discharge current upper limit warning |  |  |  |  | 0--no alarm, 1--alarm
| 0005 | 5 | RO | cell voltage upper limit warning |  |  |  |  | 0--no alarm, 1--alarm
| 0006 | 6 | RO | cell voltage lower limit warning |  |  |  |  | 0--no alarm, 1--alarm
| 0007 | 7 | RO | charge temperature upper limit warning |  |  |  |  | 0--no alarm, 1--alarm
| 0008 | 8 | RO | charge temperature lower limit warning |  |  |  |  | 0--no alarm, 1--alarm
| 0009 | 9 | RO | discharge temperature upper limit warning |  |  |  |  | 0--no alarm, 1--alarm
| 000A | 10 | RO | discharge temperature lower limit warning |  |  |  |  | 0--no alarm, 1--alarm
| 000B | 11 | RO | cell temperature upper limit warning |  |  |  |  | 0--no alarm, 1--alarm
| 000C | 12 | RO | cell temperature lower limit warning |  |  |  |  | 0--no alarm, 1--alarm
| 000D | 13 | RO | ambient temperature upper limit warning |  |  |  |  | 0--no alarm, 1--alarm
| 000E | 14 | RO | ambient temperature lower limit warning |  |  |  |  | 0--no alarm, 1--alarm
| 000F | 15 | RO | pack pole temperature upper limit warning |  |  |  |  | 0--no alarm, 1--alarm
| 0010 | 16 | RO | rack SOC upper limit warning |  |  |  |  | 0--no alarm, 1--alarm
| 0011 | 17 | RO | rack SOC lower limit warning |  |  |  |  | 0--no alarm, 1--alarm
| 0012 | 18 | RO | rack positive insulation resistance lower limit warning |  |  |  |  | 0--no alarm, 1--alarm
| 0013 | 19 | RO | rack negative insulation resistance lower limit warning |  |  |  |  | 0--no alarm, 1--alarm
| 0014 | 20 | RO | reserve |  |  |  |  | 0--no alarm, 1--alarm
| 0015 | 21 | RO | reserve |  |  |  |  | 0--no alarm, 1--alarm
| 0016 | 22 | RO | rack voltage upper limit alarm |  |  |  |  | 0--no alarm, 1--alarm
| 0017 | 23 | RO | rack voltage lower limit alarm |  |  |  |  | 0--no alarm, 1--alarm
| 0018 | 24 | RO | charge current upper limit alarm |  |  |  |  | 0--no alarm, 1--alarm
| 0019 | 25 | RO | discharge current upper limit alarm |  |  |  |  | 0--no alarm, 1--alarm
| 001A | 26 | RO | cell voltage upper limit alarm |  |  |  |  | 0--no alarm, 1--alarm
| 001B | 27 | RO | cell voltage lower limit alarm |  |  |  |  | 0--no alarm, 1--alarm
| 001C | 28 | RO | charge temperature upper limit alarm |  |  |  |  | 0--no alarm, 1--alarm
| 001D | 29 | RO | charge temperature lower limit alarm |  |  |  |  | 0--no alarm, 1--alarm
| 001E | 30 | RO | discharge temperature upper limit alarm |  |  |  |  | 0--no alarm, 1--alarm
| 001F | 31 | RO | discharge temperature lower limit alarm |  |  |  |  | 0--no alarm, 1--alarm
| 0020 | 32 | RO | cell temperature upper limit alarm |  |  |  |  | 0--no alarm, 1--alarm
| 0021 | 33 | RO | cell temperature lower limit alarm |  |  |  |  | 0--no alarm, 1--alarm
| 0022 | 34 | RO | ambient temperature upper limit alarm |  |  |  |  | 0--no alarm, 1--alarm
| 0023 | 35 | RO | ambient temperature lower limit alarm |  |  |  |  | 0--no alarm, 1--alarm
| 0024 | 36 | RO | pack pole temperature upper limit alarm |  |  |  |  | 0--no alarm, 1--alarm
| 0025 | 37 | RO | rack SOC upper limit alarm |  |  |  |  | 0--no alarm, 1--alarm
| 0026 | 38 | RO | rack SOC lower limit alarm |  |  |  |  | 0--no alarm, 1--alarm
| 0027 | 39 | RO | rack positive insulation resistance lower limit alarm |  |  |  |  | 0--no alarm, 1--alarm
| 0028 | 40 | RO | rack negative insulation resistance lower limit alarm |  |  |  |  | 0--no alarm, 1--alarm
| 0029 | 41 | RO | reserve |  |  |  |  | 0--no alarm, 1--alarm
| 002A | 42 | RO | reserve |  |  |  |  | 0--no alarm, 1--alarm
| 002B | 43 | RO | rack voltage upper limit protection |  |  |  |  | 0--no alarm, 1--alarm
| 002C | 44 | RO | rack voltage lower limit protection |  |  |  |  | 0--no alarm, 1--alarm
| 002D | 45 | RO | charge current upper limit protection |  |  |  |  | 0--no alarm, 1--alarm
| 002E | 46 | RO | discharge current upper limit protection |  |  |  |  | 0--no alarm, 1--alarm
| 002F | 47 | RO | cell voltage upper limit protection |  |  |  |  | 0--no alarm, 1--alarm
| 0030 | 48 | RO | cell voltage lower limit protection |  |  |  |  | 0--no alarm, 1--alarm
| 0031 | 49 | RO | charge temperature upper limit protection |  |  |  |  | 0--no alarm, 1--alarm
| 0032 | 50 | RO | charge temperature lower limit protection |  |  |  |  | 0--no alarm, 1--alarm
| 0033 | 51 | RO | discharge temperature upper limit protection |  |  |  |  | 0--no alarm, 1--alarm
| 0034 | 52 | RO | discharge temperature lower limit protection |  |  |  |  | 0--no alarm, 1--alarm
| 0035 | 53 | RO | cell temperature upper limit protection |  |  |  |  | 0--no alarm, 1--alarm
| 0036 | 54 | RO | cell temperature lower limit protection |  |  |  |  | 0--no alarm, 1--alarm
| 0037 | 55 | RO | ambient temperature upper limit protection |  |  |  |  | 0--no alarm, 1--alarm
| 0038 | 56 | RO | ambient temperature lower limit protection |  |  |  |  | 0--no alarm, 1--alarm
| 0039 | 57 | RO | pack pole temperature upper limit protection |  |  |  |  | 0--no alarm, 1--alarm
| 003A | 58 | RO | rack SOC upper limit protection |  |  |  |  | 0--no alarm, 1--alarm
| 003B | 59 | RO | rack SOC lower limit protection |  |  |  |  | 0--no alarm, 1--alarm
| 003C | 60 | RO | rack positive insulation resistance lower limit protection |  |  |  |  | 0--no alarm, 1--alarm
| 003D | 61 | RO | rack negative insulation resistance lower limit protection |  |  |  |  | 0--no alarm, 1--alarm
| 003E | 62 | RO | reserve |  |  |  |  | 0--no alarm, 1--alarm
| 003F | 63 | RO | reserve |  |  |  |  | 0--no alarm, 1--alarm
| 0040 | 64 | RO | cell temperature rises too fast/ more than 5⁰C/min |  |  |  |  | 0--no alarm, 1--alarm
| 0041 | 65 | RO | pack pole temperatur rises too fast/ more than 5⁰C/min |  |  |  |  | 0--no alarm, 1--alarm
| 0042 | 66 | RO | BMU communication fault |  |  |  |  | 0--no alarm, 1--alarm
| 0043 | 67 | RO | BCMU communication fault |  |  |  |  | 0--no alarm, 1--alarm
| 0044 | 68 | RO | cell voltage acquisition line fault |  |  |  |  | 0--no alarm, 1--alarm
| 0045 | 69 | RO | rack voltage acquisition line fault |  |  |  |  | 0--no alarm, 1--alarm
| 0046 | 70 | RO | current acquisition line fault |  |  |  |  | 0--no alarm, 1--alarm
| 0047 | 71 | RO | temperature acquisition line broken |  |  |  |  | 0--no alarm, 1--alarm
| 0048 | 72 | RO | temperature acquisition short circuit |  |  |  |  | 0--no alarm, 1--alarm
| 0049 | 73 | RO | BMS fault |  |  |  |  | 0--no alarm, 1--alarm
| 004A | 74 | RO | cell voltage invalid |  |  |  |  | 0--no alarm, 1--alarm
| 004B | 75 | RO | cell temperature invalid |  |  |  |  | 0--no alarm, 1--alarm
| 004C | 76 | RO | rack voltage invalid |  |  |  |  | 0--no alarm, 1--alarm
| 004D | 77 | RO | rack current invalid |  |  |  |  | 0--no alarm, 1--alarm | circuit breaker trips
| 004E | 78 | RO | positive contactor open fault |  |  |  |  | 0--no alarm, 1--alarm
| 004F | 79 | RO | negative contactor open fault |  |  |  |  | 0--no alarm, 1--alarm
| 0050 | 80 | RO | pre-charge contactor open fault |  |  |  |  | 0--no alarm, 1--alarm
| 0051 | 81 | RO | positive contactor close fault |  |  |  |  | 0--no alarm, 1--alarm
| 0052 | 82 | RO | negative contactor close fault |  |  |  |  | 0--no alarm, 1--alarm
| 0053 | 83 | RO | pre-charge contactor close fault |  |  |  |  | 0--no alarm, 1--alarm
| 0054 | 84 | RO | hall communication fault |  |  |  |  | 0--no alarm, 1--alarm
| 0055 | 85 | RO | hall acquisition fault |  |  |  |  | 0--no alarm, 1--alarm
| 0056 | 86 | RO | positive fuse open fault |  |  |  |  | 0--no alarm, 1--alarm
| 0057 | 87 | RO | negative fuse open fault |  |  |  |  | 0--no alarm, 1--alarm
| 0058 | 88 | RO | rack voltage acquisition fault |  |  |  |  | 0--no alarm, 1--alarm
| 0059 | 89 | RO | pack voltage upper limit warning |  |  |  |  | 0--no alarm, 1--alarm
| 005A | 90 | RO | pack voltage lower limit warning |  |  |  |  | 0--no alarm, 1--alarm
| 005B | 91 | RO | pack voltage upper limit alarm |  |  |  |  | 0--no alarm, 1--alarm
| 005C | 92 | RO | pack voltage lower limit alarm |  |  |  |  | 0--no alarm, 1--alarm
| 005D | 93 | RO | pack voltage upper limit protection |  |  |  |  | 0--no alarm, 1--alarm
| 005E | 94 | RO | pack voltage lower limit protection |  |  |  |  | 0--no alarm, 1--alarm
| 005F | 95 | RO | cell voltage difference upper limit warning in rack |  |  |  |  | 0--no alarm, 1--alarm
| 0060 | 96 | RO | cell voltage difference upper limit alarm in rack |  |  |  |  | 0--no alarm, 1--alarm
| 0061 | 97 | RO | cell voltage difference upper limit protection in rack |  |  |  |  | 0--no alarm, 1--alarm
| 0062 | 98 | RO | cell temperature difference upper limit warning in rack |  |  |  |  | 0--no alarm, 1--alarm
| 0063 | 99 | RO | cell temperature difference upper limit alarm in rack |  |  |  |  | 0--no alarm, 1--alarm
| 0064 | 100 | RO | cell temperature difference upper limit protection in rack |  |  |  |  | 0--no alarm, 1--alarm
| 0065 | 101 | RO | pack voltage difference upper limit warning in rack |  |  |  |  | 0--no alarm, 1--alarm
| 0066 | 102 | RO | pack voltage difference upper limit alarm in rack |  |  |  |  | 0--no alarm, 1--alarm
| 0067 | 103 | RO | pack voltage difference upper limit protection in rack |  |  |  |  | 0--no alarm, 1--alarm
| 0068 | 104 | RO | high-voltage power line temperature limit warning |  |  |  |  | 0--no alarm, 1--alarm
| 0069 | 105 | RO | high-voltage power line temperature limit alarm |  |  |  |  | 0--no alarm, 1--alarm
| 006A | 106 | RO | high-voltage power line temperature limit protection |  |  |  |  | 0--no alarm, 1--alarm
| 006B | 107 | RO | inter rack circulation warning |  |  |  |  | 0--no alarm, 1--alarm
| 006C | 108 | RO | inter rack circulation alarm |  |  |  |  | 0--no alarm, 1--alarm
| 006D | 109 | RO | inter rack circulation protection |  |  |  |  | 0--no alarm, 1--alarm
| 006E | 110 | RO | sudden voltage change warning |  |  |  |  | 0--no alarm, 1--alarm
| 006F | 111 | RO | sudden voltage change alarm |  |  |  |  | 0--no alarm, 1--alarm
| 0070 | 112 | RO | sudden voltage change protection |  |  |  |  | 0--no alarm, 1--alarm
| 0071 | 113 | RO | internal resistance abnormal alarm |  |  |  |  | 0--no alarm, 1--alarm
| 0072 | 114 | RO | pre-charge abnormal alarm |  |  |  |  | 0--no alarm, 1--alarm
| 0073 | 115 | RO | reserve |  |  |  |  | 0--no alarm, 1--alarm

## Cell Temp
Register Type | Register Address |  | Attributes | Meaning | Data Types | Coefficient | Offset | Units | Remarks(actually) | Remarks(show) | Decimal pointPrecision required | Units
| Hexadecimal | Decimal
Cell temperature data (Each rack Modbus address independent, starting from 2, discrete input registers,function code 0x04, same Modbus address as rack data, same function code, different register addresses) | 579 | 1401 | RO | 1# cell temperature | FLOAT | 1 | 0 | ℃ | T1： Cell 1# | T1： Cell 1# | 0.1 | ℃
| 057B | 1403 | RO | 2# cell temperature | FLOAT | 1 | 0 | ℃ | T2： Cell 2# & 3# | T2： Cell 2# | 0.1 | ℃
| 057D | 1405 | RO | 3# cell temperature | FLOAT | 1 | 0 | ℃ | T3： Cell 4# & 5# | T2： Cell 3# | 0.1 | ℃
| 057F | 1407 | RO | 4# cell temperature | FLOAT | 1 | 0 | ℃ | T4： Cell 6# & 7# | T3： Cell 4# | 0.1 | ℃
| 581 | 1409 | RO | 5# cell temperature | FLOAT | 1 | 0 | ℃ | T5： Cell 8# & 9# | T3： Cell 5# | 0.1 | ℃
| 583 | 1411 | RO | 6# cell temperature | FLOAT | 1 | 0 | ℃ | T6： Cell 10# & 11# | T4： Cell 6# | 0.1 | ℃
| 585 | 1413 | RO | 7# cell temperature | FLOAT | 1 | 0 | ℃ | T7： Cell 12# & 13# | T4： Cell 7# | 0.1 | ℃
| 587 | 1415 | RO | 8# cell temperature | FLOAT | 1 | 0 | ℃ | T9： Cell 14# | T5： Cell 8# | 0.1 | ℃
| 589 | 1417 | RO | 9# cell temperature | FLOAT | 1 | 0 | ℃ | T10： Cell 15# & 16# | T5： Cell 9# | 0.1 | ℃
| 058B | 1419 | RO | 10# cell temperature | FLOAT | 1 | 0 | ℃ | T11： Cell 17# & 18# | T6： Cell 10# | 0.1 | ℃
| 058D | 1421 | RO | 11# cell temperature | FLOAT | 1 | 0 | ℃ | T12： Cell 19# & 20# | T6： Cell 11# | 0.1 | ℃
| 058F | 1423 | RO | 12# cell temperature | FLOAT | 1 | 0 | ℃ | T13： Cell 21# & 22# | T7： Cell 12# | 0.1 | ℃
| 591 | 1425 | RO | 13# cell temperature | FLOAT | 1 | 0 | ℃ | T14： Cell 23# & 24# | T7： Cell 13# | 0.1 | ℃
| 593 | 1427 | RO | 14# cell temperature | FLOAT | 1 | 0 | ℃ | T15： Cell 25# & 26# | T9： Cell 14# | 0.1 | ℃
| 595 | 1429 | RO | 15# cell temperature | FLOAT | 1 | 0 | ℃ | T17： Cell 27# | T10： Cell 15# | 0.1 | ℃
| 597 | 1431 | RO | 16# cell temperature | FLOAT | 1 | 0 | ℃ | T18： Cell 28# & 29# | T10： Cell 16# | 0.1 | ℃
| 599 | 1433 | RO | 17# cell temperature | FLOAT | 1 | 0 | ℃ | T19： Cell 30# & 31# | T11： Cell 17# | 0.1 | ℃
| 059B | 1435 | RO | 18# cell temperature | FLOAT | 1 | 0 | ℃ | T20： Cell 32# & 33# | T11： Cell 18# | 0.1 | ℃
| 059D | 1437 | RO | 19# cell temperature | FLOAT | 1 | 0 | ℃ | T21： Cell 34# & 35# | T12： Cell 19# | 0.1 | ℃
| 059F | 1439 | RO | 20# cell temperature | FLOAT | 1 | 0 | ℃ | T22： Cell 36# & 37# | T12： Cell 20# | 0.1 | ℃
| 05A1 | 1441 | RO | 21# cell temperature | FLOAT | 1 | 0 | ℃ | T23： Cell 38# & 39# | T13： Cell 21# | 0.1 | ℃
| 05A3 | 1443 | RO | 22# cell temperature | FLOAT | 1 | 0 | ℃ | T25： Cell 40# | T13： Cell 22# | 0.1 | ℃
| 05A5 | 1445 | RO | 23# cell temperature | FLOAT | 1 | 0 | ℃ | T26： Cell 41# & 42# | T14： Cell 23# | 0.1 | ℃
| 05A7 | 1447 | RO | 24# cell temperature | FLOAT | 1 | 0 | ℃ | T27： Cell 43# & 44# | T14： Cell 24# | 0.1 | ℃
| 05A9 | 1449 | RO | 25# cell temperature | FLOAT | 1 | 0 | ℃ | T28： Cell 45# & 46# | T15： Cell 25# | 0.1 | ℃
| 05AB | 1451 | RO | 26# cell temperature | FLOAT | 1 | 0 | ℃ | T29： Cell 47# & 48# | T15： Cell 26# | 0.1 | ℃
| 05AD | 1453 | RO | 27# cell temperature | FLOAT | 1 | 0 | ℃ | T30： Cell 49# & 50# | T17： Cell 27# | 0.1 | ℃
| 05AF | 1455 | RO | 28# cell temperature | FLOAT | 1 | 0 | ℃ | T31： Cell 51# & 52# | T18： Cell 28# | 0.1 | ℃
| 05B1 | 1457 | RO | 29# cell temperature | FLOAT | 1 | 0 | ℃ |  | T18： Cell 29# | 0.1 | ℃
| 05B3 | 1459 | RO | 30# cell temperature | FLOAT | 1 | 0 | ℃ |  | T19： Cell 30# | 0.1 | ℃
| 05B5 | 1461 | RO | 31# cell temperature | FLOAT | 1 | 0 | ℃ |  | T19： Cell 31# | 0.1 | ℃
| 05B7 | 1463 | RO | 32# cell temperature | FLOAT | 1 | 0 | ℃ |  | T20： Cell 32# | 0.1 | ℃
| 05B9 | 1465 | RO | 33# cell temperature | FLOAT | 1 | 0 | ℃ |  | T20： Cell 33# | 0.1 | ℃
| 05BB | 1467 | RO | 34# cell temperature | FLOAT | 1 | 0 | ℃ |  | T21： Cell 34# | 0.1 | ℃
| 05BD | 1469 | RO | 35# cell temperature | FLOAT | 1 | 0 | ℃ |  | T21： Cell 35# | 0.1 | ℃
| 05BF | 1471 | RO | 36# cell temperature | FLOAT | 1 | 0 | ℃ |  | T22： Cell 36# | 0.1 | ℃
| 05C1 | 1473 | RO | 37# cell temperature | FLOAT | 1 | 0 | ℃ |  | T22： Cell 37# | 0.1 | ℃
| 05C3 | 1475 | RO | 38# cell temperature | FLOAT | 1 | 0 | ℃ |  | T23： Cell 38# | 0.1 | ℃
| 05C5 | 1477 | RO | 39# cell temperature | FLOAT | 1 | 0 | ℃ |  | T23： Cell 39# | 0.1 | ℃
| 05C7 | 1479 | RO | 40# cell temperature | FLOAT | 1 | 0 | ℃ |  | T25： Cell 40# | 0.1 | ℃
| 05C9 | 1481 | RO | 41# cell temperature | FLOAT | 1 | 0 | ℃ |  | T26： Cell 41# | 0.1 | ℃
| 05CB | 1483 | RO | 42# cell temperature | FLOAT | 1 | 0 | ℃ |  | T26： Cell 42# | 0.1 | ℃
| 05CD | 1485 | RO | 43# cell temperature | FLOAT | 1 | 0 | ℃ |  | T27： Cell 43# | 0.1 | ℃
| 05CF | 1487 | RO | 44# cell temperature | FLOAT | 1 | 0 | ℃ |  | T27： Cell 44# | 0.1 | ℃
| 05D1 | 1489 | RO | 45# cell temperature | FLOAT | 1 | 0 | ℃ |  | T28： Cell 45# | 0.1 | ℃
| 05D3 | 1491 | RO | 46# cell temperature | FLOAT | 1 | 0 | ℃ |  | T28： Cell 46# | 0.1 | ℃
| 05D5 | 1493 | RO | 47# cell temperature | FLOAT | 1 | 0 | ℃ |  | T29： Cell 47# | 0.1 | ℃
| 05D7 | 1495 | RO | 48# cell temperature | FLOAT | 1 | 0 | ℃ |  | T29： Cell 48# | 0.1 | ℃
| 05D9 | 1497 | RO | 49# cell temperature | FLOAT | 1 | 0 | ℃ |  | T30： Cell 49# | 0.1 | ℃
| 05DB | 1499 | RO | 50# cell temperature | FLOAT | 1 | 0 | ℃ |  | T30： Cell 50# | 0.1 | ℃
| 05DD | 1501 | RO | 51# cell temperature | FLOAT | 1 | 0 | ℃ |  | T31： Cell 51# | 0.1 | ℃
| 05DF | 1503 | RO | 52# cell temperature | FLOAT | 1 | 0 | ℃ |  | T31： Cell 52# | 0.1 | ℃
| 50 | 1505 | RO | 53# cell temperature | FLOAT | 1 | 0 | ℃ |  |  | 0.1 | ℃
| 5000 | 1507 | RO | 54# cell temperature | FLOAT | 1 | 0 | ℃ |  |  | 0.1 | ℃
| 500000 | 1509 | RO | 55# cell temperature | FLOAT | 1 | 0 | ℃ |  |  | 0.1 | ℃
| 50000000 | 1511 | RO | 56# cell temperature | FLOAT | 1 | 0 | ℃ |  |  | 0.1 | ℃
| 5000000000 | 1513 | RO | 57# cell temperature | FLOAT | 1 | 0 | ℃ |  |  | 0.1 | ℃
| 05EB | 1515 | RO | 58# cell temperature | FLOAT | 1 | 0 | ℃ |  |  | 0.1 | ℃
| 05ED | 1517 | RO | 59# cell temperature | FLOAT | 1 | 0 | ℃ |  |  | 0.1 | ℃
| 05EF | 1519 | RO | 60# cell temperature | FLOAT | 1 | 0 | ℃ |  |  | 0.1 | ℃
| 05F1 | 1521 | RO | 61# cell temperature | FLOAT | 1 | 0 | ℃ |  |  | 0.1 | ℃
| 05F3 | 1523 | RO | 62# cell temperature | FLOAT | 1 | 0 | ℃ |  |  | 0.1 | ℃
| 05F5 | 1525 | RO | 63# cell temperature | FLOAT | 1 | 0 | ℃ |  |  | 0.1 | ℃
| 05F7 | 1527 | RO | 64# cell temperature | FLOAT | 1 | 0 | ℃ |  |  | 0.1 | ℃
| 05F9 | 1529 | RO | 65# cell temperature | FLOAT | 1 | 0 | ℃ |  |  | 0.1 | ℃
| 05FB | 1531 | RO | 66# cell temperature | FLOAT | 1 | 0 | ℃ |  |  | 0.1 | ℃
| 05FD | 1533 | RO | 67# cell temperature | FLOAT | 1 | 0 | ℃ |  |  | 0.1 | ℃
| 05FF | 1535 | RO | 68# cell temperature | FLOAT | 1 | 0 | ℃ |  |  | 0.1 | ℃
| 601 | 1537 | RO | 69# cell temperature | FLOAT | 1 | 0 | ℃ |  |  | 0.1 | ℃
| 603 | 1539 | RO | 70# cell temperature | FLOAT | 1 | 0 | ℃ |  |  | 0.1 | ℃
| 605 | 1541 | RO | 71# cell temperature | FLOAT | 1 | 0 | ℃ |  |  | 0.1 | ℃
| 607 | 1543 | RO | 72# cell temperature | FLOAT | 1 | 0 | ℃ |  |  | 0.1 | ℃
| 609 | 1545 | RO | 73# cell temperature | FLOAT | 1 | 0 | ℃ |  |  | 0.1 | ℃
| 060B | 1547 | RO | 74# cell temperature | FLOAT | 1 | 0 | ℃ |  |  | 0.1 | ℃
| 060D | 1549 | RO | 75# cell temperature | FLOAT | 1 | 0 | ℃ |  |  | 0.1 | ℃
| 060F | 1551 | RO | 76# cell temperature | FLOAT | 1 | 0 | ℃ |  |  | 0.1 | ℃
| 611 | 1553 | RO | 77# cell temperature | FLOAT | 1 | 0 | ℃ |  |  | 0.1 | ℃
| 613 | 1555 | RO | 78# cell temperature | FLOAT | 1 | 0 | ℃ |  |  | 0.1 | ℃
| 615 | 1557 | RO | 79# cell temperature | FLOAT | 1 | 0 | ℃ |  |  | 0.1 | ℃
| 617 | 1559 | RO | 80# cell temperature | FLOAT | 1 | 0 | ℃ |  |  | 0.1 | ℃
| 619 | 1561 | RO | 81# cell temperature | FLOAT | 1 | 0 | ℃ |  |  | 0.1 | ℃
| 061B | 1563 | RO | 82# cell temperature | FLOAT | 1 | 0 | ℃ |  |  | 0.1 | ℃
| 061D | 1565 | RO | 83# cell temperature | FLOAT | 1 | 0 | ℃ |  |  | 0.1 | ℃
| 061F | 1567 | RO | 84# cell temperature | FLOAT | 1 | 0 | ℃ |  |  | 0.1 | ℃
| 621 | 1569 | RO | 85# cell temperature | FLOAT | 1 | 0 | ℃ |  |  | 0.1 | ℃
| 623 | 1571 | RO | 86# cell temperature | FLOAT | 1 | 0 | ℃ |  |  | 0.1 | ℃
| 625 | 1573 | RO | 87# cell temperature | FLOAT | 1 | 0 | ℃ |  |  | 0.1 | ℃
| 627 | 1575 | RO | 88# cell temperature | FLOAT | 1 | 0 | ℃ |  |  | 0.1 | ℃
| 629 | 1577 | RO | 89# cell temperature | FLOAT | 1 | 0 | ℃ |  |  | 0.1 | ℃
| 062B | 1579 | RO | 90# cell temperature | FLOAT | 1 | 0 | ℃ |  |  | 0.1 | ℃
| 062D | 1581 | RO | 91# cell temperature | FLOAT | 1 | 0 | ℃ |  |  | 0.1 | ℃
| 062F | 1583 | RO | 92# cell temperature | FLOAT | 1 | 0 | ℃ |  |  | 0.1 | ℃
| 631 | 1585 | RO | 93# cell temperature | FLOAT | 1 | 0 | ℃ |  |  | 0.1 | ℃
| 633 | 1587 | RO | 94# cell temperature | FLOAT | 1 | 0 | ℃ |  |  | 0.1 | ℃
| 635 | 1589 | RO | 95# cell temperature | FLOAT | 1 | 0 | ℃ |  |  | 0.1 | ℃
| 637 | 1591 | RO | 96# cell temperature | FLOAT | 1 | 0 | ℃ |  |  | 0.1 | ℃
| 639 | 1593 | RO | 97# cell temperature | FLOAT | 1 | 0 | ℃ |  |  | 0.1 | ℃
| 063B | 1595 | RO | 98# cell temperature | FLOAT | 1 | 0 | ℃ |  |  | 0.1 | ℃
| 063D | 1597 | RO | 99# cell temperature | FLOAT | 1 | 0 | ℃ |  |  | 0.1 | ℃
| 063F | 1599 | RO | 100# cell temperature | FLOAT | 1 | 0 | ℃ |  |  | 0.1 | ℃
| 641 | 1601 | RO | 101# cell temperature | FLOAT | 1 | 0 | ℃ |  |  | 0.1 | ℃
| 643 | 1603 | RO | 102# cell temperature | FLOAT | 1 | 0 | ℃ |  |  | 0.1 | ℃
| 645 | 1605 | RO | 103# cell temperature | FLOAT | 1 | 0 | ℃ |  |  | 0.1 | ℃
| 647 | 1607 | RO | 104# cell temperature | FLOAT | 1 | 0 | ℃ |  |  | 0.1 | ℃
| 649 | 1609 | RO | 105# cell temperature | FLOAT | 1 | 0 | ℃ |  |  | 0.1 | ℃
| 064B | 1611 | RO | 106# cell temperature | FLOAT | 1 | 0 | ℃ |  |  | 0.1 | ℃
| 064D | 1613 | RO | 107# cell temperature | FLOAT | 1 | 0 | ℃ |  |  | 0.1 | ℃
| 064F | 1615 | RO | 108# cell temperature | FLOAT | 1 | 0 | ℃ |  |  | 0.1 | ℃
| 651 | 1617 | RO | 109# cell temperature | FLOAT | 1 | 0 | ℃ |  |  | 0.1 | ℃
| 653 | 1619 | RO | 110# cell temperature | FLOAT | 1 | 0 | ℃ |  |  | 0.1 | ℃
| 655 | 1621 | RO | 111# cell temperature | FLOAT | 1 | 0 | ℃ |  |  | 0.1 | ℃
| 657 | 1623 | RO | 112# cell temperature | FLOAT | 1 | 0 | ℃ |  |  | 0.1 | ℃
| 659 | 1625 | RO | 113# cell temperature | FLOAT | 1 | 0 | ℃ |  |  | 0.1 | ℃
| 065B | 1627 | RO | 114# cell temperature | FLOAT | 1 | 0 | ℃ |  |  | 0.1 | ℃
| 065D | 1629 | RO | 115# cell temperature | FLOAT | 1 | 0 | ℃ |  |  | 0.1 | ℃
| 065F | 1631 | RO | 116# cell temperature | FLOAT | 1 | 0 | ℃ |  |  | 0.1 | ℃
| 661 | 1633 | RO | 117# cell temperature | FLOAT | 1 | 0 | ℃ |  |  | 0.1 | ℃
| 663 | 1635 | RO | 118# cell temperature | FLOAT | 1 | 0 | ℃ |  |  | 0.1 | ℃
| 665 | 1637 | RO | 119# cell temperature | FLOAT | 1 | 0 | ℃ |  |  | 0.1 | ℃
| 667 | 1639 | RO | 120# cell temperature | FLOAT | 1 | 0 | ℃ |  |  | 0.1 | ℃
| 669 | 1641 | RO | 121# cell temperature | FLOAT | 1 | 0 | ℃ |  |  | 0.1 | ℃
| 066B | 1643 | RO | 122# cell temperature | FLOAT | 1 | 0 | ℃ |  |  | 0.1 | ℃
| 066D | 1645 | RO | 123# cell temperature | FLOAT | 1 | 0 | ℃ |  |  | 0.1 | ℃
| 066F | 1647 | RO | 124# cell temperature | FLOAT | 1 | 0 | ℃ |  |  | 0.1 | ℃
| 671 | 1649 | RO | 125# cell temperature | FLOAT | 1 | 0 | ℃ |  |  | 0.1 | ℃
| 673 | 1651 | RO | 126# cell temperature | FLOAT | 1 | 0 | ℃ |  |  | 0.1 | ℃
| 675 | 1653 | RO | 127# cell temperature | FLOAT | 1 | 0 | ℃ |  |  | 0.1 | ℃
| 677 | 1655 | RO | 128# cell temperature | FLOAT | 1 | 0 | ℃ |  |  | 0.1 | ℃
| 679 | 1657 | RO | 129# cell temperature | FLOAT | 1 | 0 | ℃ |  |  | 0.1 | ℃
| 067B | 1659 | RO | 130# cell temperature | FLOAT | 1 | 0 | ℃ |  |  | 0.1 | ℃
| 067D | 1661 | RO | 131# cell temperature | FLOAT | 1 | 0 | ℃ |  |  | 0.1 | ℃
| 067F | 1663 | RO | 132# cell temperature | FLOAT | 1 | 0 | ℃ |  |  | 0.1 | ℃
| 681 | 1665 | RO | 133# cell temperature | FLOAT | 1 | 0 | ℃ |  |  | 0.1 | ℃
| 683 | 1667 | RO | 134# cell temperature | FLOAT | 1 | 0 | ℃ |  |  | 0.1 | ℃
| 685 | 1669 | RO | 135# cell temperature | FLOAT | 1 | 0 | ℃ |  |  | 0.1 | ℃
| 687 | 1671 | RO | 136# cell temperature | FLOAT | 1 | 0 | ℃ |  |  | 0.1 | ℃
| 689 | 1673 | RO | 137# cell temperature | FLOAT | 1 | 0 | ℃ |  |  | 0.1 | ℃
| 068B | 1675 | RO | 138# cell temperature | FLOAT | 1 | 0 | ℃ |  |  | 0.1 | ℃
| 068D | 1677 | RO | 139# cell temperature | FLOAT | 1 | 0 | ℃ |  |  | 0.1 | ℃
| 068F | 1679 | RO | 140# cell temperature | FLOAT | 1 | 0 | ℃ |  |  | 0.1 | ℃
| 691 | 1681 | RO | 141# cell temperature | FLOAT | 1 | 0 | ℃ |  |  | 0.1 | ℃
| 693 | 1683 | RO | 142# cell temperature | FLOAT | 1 | 0 | ℃ |  |  | 0.1 | ℃
| 695 | 1685 | RO | 143# cell temperature | FLOAT | 1 | 0 | ℃ |  |  | 0.1 | ℃
| 697 | 1687 | RO | 144# cell temperature | FLOAT | 1 | 0 | ℃ |  |  | 0.1 | ℃
| 699 | 1689 | RO | 145# cell temperature | FLOAT | 1 | 0 | ℃ |  |  | 0.1 | ℃
| 069B | 1691 | RO | 146# cell temperature | FLOAT | 1 | 0 | ℃ |  |  | 0.1 | ℃
| 069D | 1693 | RO | 147# cell temperature | FLOAT | 1 | 0 | ℃ |  |  | 0.1 | ℃
| 069F | 1695 | RO | 148# cell temperature | FLOAT | 1 | 0 | ℃ |  |  | 0.1 | ℃
| 06A1 | 1697 | RO | 149# cell temperature | FLOAT | 1 | 0 | ℃ |  |  | 0.1 | ℃
| 06A3 | 1699 | RO | 150# cell temperature | FLOAT | 1 | 0 | ℃ |  |  | 0.1 | ℃
| 06A5 | 1701 | RO | 151# cell temperature | FLOAT | 1 | 0 | ℃ |  |  | 0.1 | ℃
| 06A7 | 1703 | RO | 152# cell temperature | FLOAT | 1 | 0 | ℃ |  |  | 0.1 | ℃
| 06A9 | 1705 | RO | 153# cell temperature | FLOAT | 1 | 0 | ℃ |  |  | 0.1 | ℃
| 06AB | 1707 | RO | 154# cell temperature | FLOAT | 1 | 0 | ℃ |  |  | 0.1 | ℃
| 06AD | 1709 | RO | 155# cell temperature | FLOAT | 1 | 0 | ℃ |  |  | 0.1 | ℃
| 06AF | 1711 | RO | 156# cell temperature | FLOAT | 1 | 0 | ℃ |  |  | 0.1 | ℃
| 06B1 | 1713 | RO | 157# cell temperature | FLOAT | 1 | 0 | ℃ |  |  | 0.1 | ℃
| 06B3 | 1715 | RO | 158# cell temperature | FLOAT | 1 | 0 | ℃ |  |  | 0.1 | ℃
| 06B5 | 1717 | RO | 159# cell temperature | FLOAT | 1 | 0 | ℃ |  |  | 0.1 | ℃
| 06B7 | 1719 | RO | 160# cell temperature | FLOAT | 1 | 0 | ℃ |  |  | 0.1 | ℃
| 06B9 | 1721 | RO | 161# cell temperature | FLOAT | 1 | 0 | ℃ |  |  | 0.1 | ℃
| 06BB | 1723 | RO | 162# cell temperature | FLOAT | 1 | 0 | ℃ |  |  | 0.1 | ℃
| 06BD | 1725 | RO | 163# cell temperature | FLOAT | 1 | 0 | ℃ |  |  | 0.1 | ℃
| 06BF | 1727 | RO | 164# cell temperature | FLOAT | 1 | 0 | ℃ |  |  | 0.1 | ℃
| 06C1 | 1729 | RO | 165# cell temperature | FLOAT | 1 | 0 | ℃ |  |  | 0.1 | ℃
| 06C3 | 1731 | RO | 166# cell temperature | FLOAT | 1 | 0 | ℃ |  |  | 0.1 | ℃
| 06C5 | 1733 | RO | 167# cell temperature | FLOAT | 1 | 0 | ℃ |  |  | 0.1 | ℃
| 06C7 | 1735 | RO | 168# cell temperature | FLOAT | 1 | 0 | ℃ |  |  | 0.1 | ℃
| 06C9 | 1737 | RO | 169# cell temperature | FLOAT | 1 | 0 | ℃ |  |  | 0.1 | ℃
| 06CB | 1739 | RO | 170# cell temperature | FLOAT | 1 | 0 | ℃ |  |  | 0.1 | ℃
| 06CD | 1741 | RO | 171# cell temperature | FLOAT | 1 | 0 | ℃ |  |  | 0.1 | ℃
| 06CF | 1743 | RO | 172# cell temperature | FLOAT | 1 | 0 | ℃ |  |  | 0.1 | ℃
| 06D1 | 1745 | RO | 173# cell temperature | FLOAT | 1 | 0 | ℃ |  |  | 0.1 | ℃
| 06D3 | 1747 | RO | 174# cell temperature | FLOAT | 1 | 0 | ℃ |  |  | 0.1 | ℃
| 06D5 | 1749 | RO | 175# cell temperature | FLOAT | 1 | 0 | ℃ |  |  | 0.1 | ℃
| 06D7 | 1751 | RO | 176# cell temperature | FLOAT | 1 | 0 | ℃ |  |  | 0.1 | ℃
| 06D9 | 1753 | RO | 177# cell temperature | FLOAT | 1 | 0 | ℃ |  |  | 0.1 | ℃
| 06DB | 1755 | RO | 178# cell temperature | FLOAT | 1 | 0 | ℃ |  |  | 0.1 | ℃
| 06DD | 1757 | RO | 179# cell temperature | FLOAT | 1 | 0 | ℃ |  |  | 0.1 | ℃
| 06DF | 1759 | RO | 180# cell temperature | FLOAT | 1 | 0 | ℃ |  |  | 0.1 | ℃
| 60 | 1761 | RO | 181# cell temperature | FLOAT | 1 | 0 | ℃ |  |  | 0.1 | ℃
| 6000 | 1763 | RO | 182# cell temperature | FLOAT | 1 | 0 | ℃ |  |  | 0.1 | ℃
| 600000 | 1765 | RO | 183# cell temperature | FLOAT | 1 | 0 | ℃ |  |  | 0.1 | ℃
| 60000000 | 1767 | RO | 184# cell temperature | FLOAT | 1 | 0 | ℃ |  |  | 0.1 | ℃
| 6000000000 | 1769 | RO | 185# cell temperature | FLOAT | 1 | 0 | ℃ |  |  | 0.1 | ℃
| 06EB | 1771 | RO | 186# cell temperature | FLOAT | 1 | 0 | ℃ |  |  | 0.1 | ℃
| 06ED | 1773 | RO | 187# cell temperature | FLOAT | 1 | 0 | ℃ |  |  | 0.1 | ℃
| 06EF | 1775 | RO | 188# cell temperature | FLOAT | 1 | 0 | ℃ |  |  | 0.1 | ℃
| 06F1 | 1777 | RO | 189# cell temperature | FLOAT | 1 | 0 | ℃ |  |  | 0.1 | ℃
| 06F3 | 1779 | RO | 190# cell temperature | FLOAT | 1 | 0 | ℃ |  |  | 0.1 | ℃
| 06F5 | 1781 | RO | 191# cell temperature | FLOAT | 1 | 0 | ℃ |  |  | 0.1 | ℃
| 06F7 | 1783 | RO | 192# cell temperature | FLOAT | 1 | 0 | ℃ |  |  | 0.1 | ℃
| 06F9 | 1785 | RO | 193# cell temperature | FLOAT | 1 | 0 | ℃ |  |  | 0.1 | ℃
| 06FB | 1787 | RO | 194# cell temperature | FLOAT | 1 | 0 | ℃ |  |  | 0.1 | ℃
| 06FD | 1789 | RO | 195# cell temperature | FLOAT | 1 | 0 | ℃ |  |  | 0.1 | ℃
| 06FF | 1791 | RO | 196# cell temperature | FLOAT | 1 | 0 | ℃ |  |  | 0.1 | ℃
| 701 | 1793 | RO | 197# cell temperature | FLOAT | 1 | 0 | ℃ |  |  | 0.1 | ℃
| 703 | 1795 | RO | 198# cell temperature | FLOAT | 1 | 0 | ℃ |  |  | 0.1 | ℃
| 705 | 1797 | RO | 199# cell temperature | FLOAT | 1 | 0 | ℃ |  |  | 0.1 | ℃
| 707 | 1799 | RO | 200# cell temperature | FLOAT | 1 | 0 | ℃ |  |  | 0.1 | ℃
| 709 | 1801 | RO | 201# cell temperature | FLOAT | 1 | 0 | ℃ |  |  | 0.1 | ℃
| 070B | 1803 | RO | 202# cell temperature | FLOAT | 1 | 0 | ℃ |  |  | 0.1 | ℃
| 070D | 1805 | RO | 203# cell temperature | FLOAT | 1 | 0 | ℃ |  |  | 0.1 | ℃
| 070F | 1807 | RO | 204# cell temperature | FLOAT | 1 | 0 | ℃ |  |  | 0.1 | ℃
| 711 | 1809 | RO | 205# cell temperature | FLOAT | 1 | 0 | ℃ |  |  | 0.1 | ℃
| 713 | 1811 | RO | 206# cell temperature | FLOAT | 1 | 0 | ℃ |  |  | 0.1 | ℃
| 715 | 1813 | RO | 207# cell temperature | FLOAT | 1 | 0 | ℃ |  |  | 0.1 | ℃
| 717 | 1815 | RO | 208# cell temperature | FLOAT | 1 | 0 | ℃ |  |  | 0.1 | ℃
| 719 | 1817 | RO | 209# cell temperature | FLOAT | 1 | 0 | ℃ |  |  | 0.1 | ℃
| 071B | 1819 | RO | 210# cell temperature | FLOAT | 1 | 0 | ℃ |  |  | 0.1 | ℃
| 071D | 1821 | RO | 211# cell temperature | FLOAT | 1 | 0 | ℃ |  |  | 0.1 | ℃
| 071F | 1823 | RO | 212# cell temperature | FLOAT | 1 | 0 | ℃ |  |  | 0.1 | ℃
| 721 | 1825 | RO | 213# cell temperature | FLOAT | 1 | 0 | ℃ |  |  | 0.1 | ℃
| 723 | 1827 | RO | 214# cell temperature | FLOAT | 1 | 0 | ℃ |  |  | 0.1 | ℃
| 725 | 1829 | RO | 215# cell temperature | FLOAT | 1 | 0 | ℃ |  |  | 0.1 | ℃
| 727 | 1831 | RO | 216# cell temperature | FLOAT | 1 | 0 | ℃ |  |  | 0.1 | ℃
| 729 | 1833 | RO | 217# cell temperature | FLOAT | 1 | 0 | ℃ |  |  | 0.1 | ℃
| 072B | 1835 | RO | 218# cell temperature | FLOAT | 1 | 0 | ℃ |  |  | 0.1 | ℃
| 072D | 1837 | RO | 219# cell temperature | FLOAT | 1 | 0 | ℃ |  |  | 0.1 | ℃
| 072F | 1839 | RO | 220# cell temperature | FLOAT | 1 | 0 | ℃ |  |  | 0.1 | ℃
| 731 | 1841 | RO | 221# cell temperature | FLOAT | 1 | 0 | ℃ |  |  | 0.1 | ℃
| 733 | 1843 | RO | 222# cell temperature | FLOAT | 1 | 0 | ℃ |  |  | 0.1 | ℃
| 735 | 1845 | RO | 223# cell temperature | FLOAT | 1 | 0 | ℃ |  |  | 0.1 | ℃
| 737 | 1847 | RO | 224# cell temperature | FLOAT | 1 | 0 | ℃ |  |  | 0.1 | ℃
| 739 | 1849 | RO | 225# cell temperature | FLOAT | 1 | 0 | ℃ |  |  | 0.1 | ℃
| 073B | 1851 | RO | 226# cell temperature | FLOAT | 1 | 0 | ℃ |  |  | 0.1 | ℃
| 073D | 1853 | RO | 227# cell temperature | FLOAT | 1 | 0 | ℃ |  |  | 0.1 | ℃
| 073F | 1855 | RO | 228# cell temperature | FLOAT | 1 | 0 | ℃ |  |  | 0.1 | ℃
| 741 | 1857 | RO | 229# cell temperature | FLOAT | 1 | 0 | ℃ |  |  | 0.1 | ℃
| 743 | 1859 | RO | 230# cell temperature | FLOAT | 1 | 0 | ℃ |  |  | 0.1 | ℃
| 745 | 1861 | RO | 231# cell temperature | FLOAT | 1 | 0 | ℃ |  |  | 0.1 | ℃
| 747 | 1863 | RO | 232# cell temperature | FLOAT | 1 | 0 | ℃ |  |  | 0.1 | ℃
| 749 | 1865 | RO | 233# cell temperature | FLOAT | 1 | 0 | ℃ |  |  | 0.1 | ℃
| 074B | 1867 | RO | 234# cell temperature | FLOAT | 1 | 0 | ℃ |  |  | 0.1 | ℃
| 074D | 1869 | RO | 235# cell temperature | FLOAT | 1 | 0 | ℃ |  |  | 0.1 | ℃
| 074F | 1871 | RO | 236# cell temperature | FLOAT | 1 | 0 | ℃ |  |  | 0.1 | ℃
| 751 | 1873 | RO | 237# cell temperature | FLOAT | 1 | 0 | ℃ |  |  | 0.1 | ℃
| 753 | 1875 | RO | 238# cell temperature | FLOAT | 1 | 0 | ℃ |  |  | 0.1 | ℃
| 755 | 1877 | RO | 239# cell temperature | FLOAT | 1 | 0 | ℃ |  |  | 0.1 | ℃
| 757 | 1879 | RO | 240# cell temperature | FLOAT | 1 | 0 | ℃ |  |  | 0.1 | ℃
| 759 | 1881 | RO | 241# cell temperature | FLOAT | 1 | 0 | ℃ |  |  | 0.1 | ℃
| 075B | 1883 | RO | 242# cell temperature | FLOAT | 1 | 0 | ℃ |  |  | 0.1 | ℃
| 075D | 1885 | RO | 243# cell temperature | FLOAT | 1 | 0 | ℃ |  |  | 0.1 | ℃
| 075F | 1887 | RO | 244# cell temperature | FLOAT | 1 | 0 | ℃ |  |  | 0.1 | ℃
| 761 | 1889 | RO | 245# cell temperature | FLOAT | 1 | 0 | ℃ |  |  | 0.1 | ℃
| 763 | 1891 | RO | 246# cell temperature | FLOAT | 1 | 0 | ℃ |  |  | 0.1 | ℃
| 765 | 1893 | RO | 247# cell temperature | FLOAT | 1 | 0 | ℃ |  |  | 0.1 | ℃
| 767 | 1895 | RO | 248# cell temperature | FLOAT | 1 | 0 | ℃ |  |  | 0.1 | ℃
| 769 | 1897 | RO | 249# cell temperature | FLOAT | 1 | 0 | ℃ |  |  | 0.1 | ℃
| 076B | 1899 | RO | 250# cell temperature | FLOAT | 1 | 0 | ℃ |  |  | 0.1 | ℃
| 076D | 1901 | RO | 251# cell temperature | FLOAT | 1 | 0 | ℃ |  |  | 0.1 | ℃
| 076F | 1903 | RO | 252# cell temperature | FLOAT | 1 | 0 | ℃ |  |  | 0.1 | ℃
| 771 | 1905 | RO | 253# cell temperature | FLOAT | 1 | 0 | ℃ |  |  | 0.1 | ℃
| 773 | 1907 | RO | 254# cell temperature | FLOAT | 1 | 0 | ℃ |  |  | 0.1 | ℃
| 775 | 1909 | RO | 255# cell temperature | FLOAT | 1 | 0 | ℃ |  |  | 0.1 | ℃
| 777 | 1911 | RO | 256# cell temperature | FLOAT | 1 | 0 | ℃ |  |  | 0.1 | ℃
| 779 | 1913 | RO | 257# cell temperature | FLOAT | 1 | 0 | ℃ |  |  | 0.1 | ℃
| 077B | 1915 | RO | 258# cell temperature | FLOAT | 1 | 0 | ℃ |  |  | 0.1 | ℃
| 077D | 1917 | RO | 259# cell temperature | FLOAT | 1 | 0 | ℃ |  |  | 0.1 | ℃
| 077F | 1919 | RO | 260# cell temperature | FLOAT | 1 | 0 | ℃ |  |  | 0.1 | ℃
| 781 | 1921 | RO | 261# cell temperature | FLOAT | 1 | 0 | ℃ |  |  | 0.1 | ℃
| 783 | 1923 | RO | 262# cell temperature | FLOAT | 1 | 0 | ℃ |  |  | 0.1 | ℃
| 785 | 1925 | RO | 263# cell temperature | FLOAT | 1 | 0 | ℃ |  |  | 0.1 | ℃
| 787 | 1927 | RO | 264# cell temperature | FLOAT | 1 | 0 | ℃ |  |  | 0.1 | ℃
| 789 | 1929 | RO | 265# cell temperature | FLOAT | 1 | 0 | ℃ |  |  | 0.1 | ℃
| 078B | 1931 | RO | 266# cell temperature | FLOAT | 1 | 0 | ℃ |  |  | 0.1 | ℃
| 078D | 1933 | RO | 267# cell temperature | FLOAT | 1 | 0 | ℃ |  |  | 0.1 | ℃
| 078F | 1935 | RO | 268# cell temperature | FLOAT | 1 | 0 | ℃ |  |  | 0.1 | ℃
| 791 | 1937 | RO | 269# cell temperature | FLOAT | 1 | 0 | ℃ |  |  | 0.1 | ℃
| 793 | 1939 | RO | 270# cell temperature | FLOAT | 1 | 0 | ℃ |  |  | 0.1 | ℃
| 795 | 1941 | RO | 271# cell temperature | FLOAT | 1 | 0 | ℃ |  |  | 0.1 | ℃
| 797 | 1943 | RO | 272# cell temperature | FLOAT | 1 | 0 | ℃ |  |  | 0.1 | ℃
| 799 | 1945 | RO | 273# cell temperature | FLOAT | 1 | 0 | ℃ |  |  | 0.1 | ℃
| 079B | 1947 | RO | 274# cell temperature | FLOAT | 1 | 0 | ℃ |  |  | 0.1 | ℃
| 079D | 1949 | RO | 275# cell temperature | FLOAT | 1 | 0 | ℃ |  |  | 0.1 | ℃
| 079F | 1951 | RO | 276# cell temperature | FLOAT | 1 | 0 | ℃ |  |  | 0.1 | ℃
| 07A1 | 1953 | RO | 277# cell temperature | FLOAT | 1 | 0 | ℃ |  |  | 0.1 | ℃
| 07A3 | 1955 | RO | 278# cell temperature | FLOAT | 1 | 0 | ℃ |  |  | 0.1 | ℃
| 07A5 | 1957 | RO | 279# cell temperature | FLOAT | 1 | 0 | ℃ |  |  | 0.1 | ℃
| 07A7 | 1959 | RO | 280# cell temperature | FLOAT | 1 | 0 | ℃ |  |  | 0.1 | ℃
| 07A9 | 1961 | RO | 281# cell temperature | FLOAT | 1 | 0 | ℃ |  |  | 0.1 | ℃
| 07AB | 1963 | RO | 282# cell temperature | FLOAT | 1 | 0 | ℃ |  |  | 0.1 | ℃
| 07AD | 1965 | RO | 283# cell temperature | FLOAT | 1 | 0 | ℃ |  |  | 0.1 | ℃
| 07AF | 1967 | RO | 284# cell temperature | FLOAT | 1 | 0 | ℃ |  |  | 0.1 | ℃
| 07B1 | 1969 | RO | 285# cell temperature | FLOAT | 1 | 0 | ℃ |  |  | 0.1 | ℃
| 07B3 | 1971 | RO | 286# cell temperature | FLOAT | 1 | 0 | ℃ |  |  | 0.1 | ℃
| 07B5 | 1973 | RO | 287# cell temperature | FLOAT | 1 | 0 | ℃ |  |  | 0.1 | ℃
| 07B7 | 1975 | RO | 288# cell temperature | FLOAT | 1 | 0 | ℃ |  |  | 0.1 | ℃
| 07B9 | 1977 | RO | 289# cell temperature | FLOAT | 1 | 0 | ℃ |  |  | 0.1 | ℃
| 07BB | 1979 | RO | 290# cell temperature | FLOAT | 1 | 0 | ℃ |  |  | 0.1 | ℃
| 07BD | 1981 | RO | 291# cell temperature | FLOAT | 1 | 0 | ℃ |  |  | 0.1 | ℃
| 07BF | 1983 | RO | 292# cell temperature | FLOAT | 1 | 0 | ℃ |  |  | 0.1 | ℃
| 07C1 | 1985 | RO | 293# cell temperature | FLOAT | 1 | 0 | ℃ |  |  | 0.1 | ℃
| 07C3 | 1987 | RO | 294# cell temperature | FLOAT | 1 | 0 | ℃ |  |  | 0.1 | ℃
| 07C5 | 1989 | RO | 295# cell temperature | FLOAT | 1 | 0 | ℃ |  |  | 0.1 | ℃
| 07C7 | 1991 | RO | 296# cell temperature | FLOAT | 1 | 0 | ℃ |  |  | 0.1 | ℃
| 07C9 | 1993 | RO | 297# cell temperature | FLOAT | 1 | 0 | ℃ |  |  | 0.1 | ℃
| 07CB | 1995 | RO | 298# cell temperature | FLOAT | 1 | 0 | ℃ |  |  | 0.1 | ℃
| 07CD | 1997 | RO | 299# cell temperature | FLOAT | 1 | 0 | ℃ |  |  | 0.1 | ℃
| 07CF | 1999 | RO | 300# cell temperature | FLOAT | 1 | 0 | ℃ |  |  | 0.1 | ℃
| 07D1 | 2001 | RO | 301# cell temperature | FLOAT | 1 | 0 | ℃ |  |  | 0.1 | ℃
| 07D3 | 2003 | RO | 302# cell temperature | FLOAT | 1 | 0 | ℃ |  |  | 0.1 | ℃
| 07D5 | 2005 | RO | 303# cell temperature | FLOAT | 1 | 0 | ℃ |  |  | 0.1 | ℃
| 07D7 | 2007 | RO | 304# cell temperature | FLOAT | 1 | 0 | ℃ |  |  | 0.1 | ℃
| 07D9 | 2009 | RO | 305# cell temperature | FLOAT | 1 | 0 | ℃ |  |  | 0.1 | ℃
| 07DB | 2011 | RO | 306# cell temperature | FLOAT | 1 | 0 | ℃ |  |  | 0.1 | ℃
| 07DD | 2013 | RO | 307# cell temperature | FLOAT | 1 | 0 | ℃ |  |  | 0.1 | ℃
| 07DF | 2015 | RO | 308# cell temperature | FLOAT | 1 | 0 | ℃ |  |  | 0.1 | ℃
| 70 | 2017 | RO | 309# cell temperature | FLOAT | 1 | 0 | ℃ |  |  | 0.1 | ℃
| 7000 | 2019 | RO | 310# cell temperature | FLOAT | 1 | 0 | ℃ |  |  | 0.1 | ℃
| 700000 | 2021 | RO | 311# cell temperature | FLOAT | 1 | 0 | ℃ |  |  | 0.1 | ℃
| 70000000 | 2023 | RO | 312# cell temperature | FLOAT | 1 | 0 | ℃ |  |  | 0.1 | ℃
| 7000000000 | 2025 | RO | 313# cell temperature | FLOAT | 1 | 0 | ℃ |  |  | 0.1 | ℃
| 07EB | 2027 | RO | 314# cell temperature | FLOAT | 1 | 0 | ℃ |  |  | 0.1 | ℃
| 07ED | 2029 | RO | 315# cell temperature | FLOAT | 1 | 0 | ℃ |  |  | 0.1 | ℃
| 07EF | 2031 | RO | 316# cell temperature | FLOAT | 1 | 0 | ℃ |  |  | 0.1 | ℃
| 07F1 | 2033 | RO | 317# cell temperature | FLOAT | 1 | 0 | ℃ |  |  | 0.1 | ℃
| 07F3 | 2035 | RO | 318# cell temperature | FLOAT | 1 | 0 | ℃ |  |  | 0.1 | ℃
| 07F5 | 2037 | RO | 319# cell temperature | FLOAT | 1 | 0 | ℃ |  |  | 0.1 | ℃
| 07F7 | 2039 | RO | 320# cell temperature | FLOAT | 1 | 0 | ℃ |  |  | 0.1 | ℃
| 07F9 | 2041 | RO | 321# cell temperature | FLOAT | 1 | 0 | ℃ |  |  | 0.1 | ℃
| 07FB | 2043 | RO | 322# cell temperature | FLOAT | 1 | 0 | ℃ |  |  | 0.1 | ℃
| 07FD | 2045 | RO | 323# cell temperature | FLOAT | 1 | 0 | ℃ |  |  | 0.1 | ℃
| 07FF | 2047 | RO | 324# cell temperature | FLOAT | 1 | 0 | ℃ |  |  | 0.1 | ℃
| 801 | 2049 | RO | 325# cell temperature | FLOAT | 1 | 0 | ℃ |  |  | 0.1 | ℃
| 803 | 2051 | RO | 326# cell temperature | FLOAT | 1 | 0 | ℃ |  |  | 0.1 | ℃
| 805 | 2053 | RO | 327# cell temperature | FLOAT | 1 | 0 | ℃ |  |  | 0.1 | ℃
| 807 | 2055 | RO | 328# cell temperature | FLOAT | 1 | 0 | ℃ |  |  | 0.1 | ℃
| 809 | 2057 | RO | 329# cell temperature | FLOAT | 1 | 0 | ℃ |  |  | 0.1 | ℃
| 080B | 2059 | RO | 330# cell temperature | FLOAT | 1 | 0 | ℃ |  |  | 0.1 | ℃
| 080D | 2061 | RO | 331# cell temperature | FLOAT | 1 | 0 | ℃ |  |  | 0.1 | ℃
| 080F | 2063 | RO | 332# cell temperature | FLOAT | 1 | 0 | ℃ |  |  | 0.1 | ℃
| 811 | 2065 | RO | 333# cell temperature | FLOAT | 1 | 0 | ℃ |  |  | 0.1 | ℃
| 813 | 2067 | RO | 334# cell temperature | FLOAT | 1 | 0 | ℃ |  |  | 0.1 | ℃
| 815 | 2069 | RO | 335# cell temperature | FLOAT | 1 | 0 | ℃ |  |  | 0.1 | ℃
| 817 | 2071 | RO | 336# cell temperature | FLOAT | 1 | 0 | ℃ |  |  | 0.1 | ℃
| 819 | 2073 | RO | 337# cell temperature | FLOAT | 1 | 0 | ℃ |  |  | 0.1 | ℃
| 081B | 2075 | RO | 338# cell temperature | FLOAT | 1 | 0 | ℃ |  |  | 0.1 | ℃
| 081D | 2077 | RO | 339# cell temperature | FLOAT | 1 | 0 | ℃ |  |  | 0.1 | ℃
| 081F | 2079 | RO | 340# cell temperature | FLOAT | 1 | 0 | ℃ |  |  | 0.1 | ℃
| 821 | 2081 | RO | 341# cell temperature | FLOAT | 1 | 0 | ℃ |  |  | 0.1 | ℃
| 823 | 2083 | RO | 342# cell temperature | FLOAT | 1 | 0 | ℃ |  |  | 0.1 | ℃
| 825 | 2085 | RO | 343# cell temperature | FLOAT | 1 | 0 | ℃ |  |  | 0.1 | ℃
| 827 | 2087 | RO | 344# cell temperature | FLOAT | 1 | 0 | ℃ |  |  | 0.1 | ℃
| 829 | 2089 | RO | 345# cell temperature | FLOAT | 1 | 0 | ℃ |  |  | 0.1 | ℃
| 082B | 2091 | RO | 346# cell temperature | FLOAT | 1 | 0 | ℃ |  |  | 0.1 | ℃
| 082D | 2093 | RO | 347# cell temperature | FLOAT | 1 | 0 | ℃ |  |  | 0.1 | ℃
| 082F | 2095 | RO | 348# cell temperature | FLOAT | 1 | 0 | ℃ |  |  | 0.1 | ℃
| 831 | 2097 | RO | 349# cell temperature | FLOAT | 1 | 0 | ℃ |  |  | 0.1 | ℃
| 833 | 2099 | RO | 350# cell temperature | FLOAT | 1 | 0 | ℃ |  |  | 0.1 | ℃
| 835 | 2101 | RO | 351# cell temperature | FLOAT | 1 | 0 | ℃ |  |  | 0.1 | ℃
| 837 | 2103 | RO | 352# cell temperature | FLOAT | 1 | 0 | ℃ |  |  | 0.1 | ℃
| 839 | 2105 | RO | 353# cell temperature | FLOAT | 1 | 0 | ℃ |  |  | 0.1 | ℃
| 083B | 2107 | RO | 354# cell temperature | FLOAT | 1 | 0 | ℃ |  |  | 0.1 | ℃
| 083D | 2109 | RO | 355# cell temperature | FLOAT | 1 | 0 | ℃ |  |  | 0.1 | ℃
| 083F | 2111 | RO | 356# cell temperature | FLOAT | 1 | 0 | ℃ |  |  | 0.1 | ℃
| 841 | 2113 | RO | 357# cell temperature | FLOAT | 1 | 0 | ℃ |  |  | 0.1 | ℃
| 843 | 2115 | RO | 358# cell temperature | FLOAT | 1 | 0 | ℃ |  |  | 0.1 | ℃
| 845 | 2117 | RO | 359# cell temperature | FLOAT | 1 | 0 | ℃ |  |  | 0.1 | ℃
| 847 | 2119 | RO | 360# cell temperature | FLOAT | 1 | 0 | ℃ |  |  | 0.1 | ℃
| 849 | 2121 | RO | 361# cell temperature | FLOAT | 1 | 0 | ℃ |  |  | 0.1 | ℃
| 084B | 2123 | RO | 362# cell temperature | FLOAT | 1 | 0 | ℃ |  |  | 0.1 | ℃
| 084D | 2125 | RO | 363# cell temperature | FLOAT | 1 | 0 | ℃ |  |  | 0.1 | ℃
| 084F | 2127 | RO | 364# cell temperature | FLOAT | 1 | 0 | ℃ |  |  | 0.1 | ℃
| 851 | 2129 | RO | 365# cell temperature | FLOAT | 1 | 0 | ℃ |  |  | 0.1 | ℃
| 853 | 2131 | RO | 366# cell temperature | FLOAT | 1 | 0 | ℃ |  |  | 0.1 | ℃
| 855 | 2133 | RO | 367# cell temperature | FLOAT | 1 | 0 | ℃ |  |  | 0.1 | ℃
| 857 | 2135 | RO | 368# cell temperature | FLOAT | 1 | 0 | ℃ |  |  | 0.1 | ℃
| 859 | 2137 | RO | 369# cell temperature | FLOAT | 1 | 0 | ℃ |  |  | 0.1 | ℃
| 085B | 2139 | RO | 370# cell temperature | FLOAT | 1 | 0 | ℃ |  |  | 0.1 | ℃
| 085D | 2141 | RO | 371# cell temperature | FLOAT | 1 | 0 | ℃ |  |  | 0.1 | ℃
| 085F | 2143 | RO | 372# cell temperature | FLOAT | 1 | 0 | ℃ |  |  | 0.1 | ℃
| 861 | 2145 | RO | 373# cell temperature | FLOAT | 1 | 0 | ℃ |  |  | 0.1 | ℃
| 863 | 2147 | RO | 374# cell temperature | FLOAT | 1 | 0 | ℃ |  |  | 0.1 | ℃
| 865 | 2149 | RO | 375# cell temperature | FLOAT | 1 | 0 | ℃ |  |  | 0.1 | ℃
| 867 | 2151 | RO | 376# cell temperature | FLOAT | 1 | 0 | ℃ |  |  | 0.1 | ℃
| 869 | 2153 | RO | 377# cell temperature | FLOAT | 1 | 0 | ℃ |  |  | 0.1 | ℃
| 086B | 2155 | RO | 378# cell temperature | FLOAT | 1 | 0 | ℃ |  |  | 0.1 | ℃
| 086D | 2157 | RO | 379# cell temperature | FLOAT | 1 | 0 | ℃ |  |  | 0.1 | ℃
| 086F | 2159 | RO | 380# cell temperature | FLOAT | 1 | 0 | ℃ |  |  | 0.1 | ℃
| 871 | 2161 | RO | 381# cell temperature | FLOAT | 1 | 0 | ℃ |  |  | 0.1 | ℃
| 873 | 2163 | RO | 382# cell temperature | FLOAT | 1 | 0 | ℃ |  |  | 0.1 | ℃
| 875 | 2165 | RO | 383# cell temperature | FLOAT | 1 | 0 | ℃ |  |  | 0.1 | ℃
| 877 | 2167 | RO | 384# cell temperature | FLOAT | 1 | 0 | ℃ |  |  | 0.1 | ℃
| 879 | 2169 | RO | 385# cell temperature | FLOAT | 1 | 0 | ℃ |  |  | 0.1 | ℃
| 087B | 2171 | RO | 386# cell temperature | FLOAT | 1 | 0 | ℃ |  |  | 0.1 | ℃
| 087D | 2173 | RO | 387# cell temperature | FLOAT | 1 | 0 | ℃ |  |  | 0.1 | ℃
| 087F | 2175 | RO | 388# cell temperature | FLOAT | 1 | 0 | ℃ |  |  | 0.1 | ℃
| 881 | 2177 | RO | 389# cell temperature | FLOAT | 1 | 0 | ℃ |  |  | 0.1 | ℃
| 883 | 2179 | RO | 390# cell temperature | FLOAT | 1 | 0 | ℃ |  |  | 0.1 | ℃
| 885 | 2181 | RO | 391# cell temperature | FLOAT | 1 | 0 | ℃ |  |  | 0.1 | ℃
| 887 | 2183 | RO | 392# cell temperature | FLOAT | 1 | 0 | ℃ |  |  | 0.1 | ℃
| 889 | 2185 | RO | 393# cell temperature | FLOAT | 1 | 0 | ℃ |  |  | 0.1 | ℃
| 088B | 2187 | RO | 394# cell temperature | FLOAT | 1 | 0 | ℃ |  |  | 0.1 | ℃
| 088D | 2189 | RO | 395# cell temperature | FLOAT | 1 | 0 | ℃ |  |  | 0.1 | ℃
| 088F | 2191 | RO | 396# cell temperature | FLOAT | 1 | 0 | ℃ |  |  | 0.1 | ℃
| 891 | 2193 | RO | 397# cell temperature | FLOAT | 1 | 0 | ℃ |  |  | 0.1 | ℃
| 893 | 2195 | RO | 398# cell temperature | FLOAT | 1 | 0 | ℃ |  |  | 0.1 | ℃
| 895 | 2197 | RO | 399# cell temperature | FLOAT | 1 | 0 | ℃ |  |  | 0.1 | ℃
| 897 | 2199 | RO | 400# cell temperature | FLOAT | 1 | 0 | ℃ |  |  | 0.1 | ℃
| 899 | 2201 | RO | 401# cell temperature | FLOAT | 1 | 0 | ℃ |  |  | 0.1 | ℃
| 089B | 2203 | RO | 402# cell temperature | FLOAT | 1 | 0 | ℃ |  |  | 0.1 | ℃
| 089D | 2205 | RO | 403# cell temperature | FLOAT | 1 | 0 | ℃ |  |  | 0.1 | ℃
| 089F | 2207 | RO | 404# cell temperature | FLOAT | 1 | 0 | ℃ |  |  | 0.1 | ℃
| 08A1 | 2209 | RO | 405# cell temperature | FLOAT | 1 | 0 | ℃ |  |  | 0.1 | ℃
| 08A3 | 2211 | RO | 406# cell temperature | FLOAT | 1 | 0 | ℃ |  |  | 0.1 | ℃
| 08A5 | 2213 | RO | 407# cell temperature | FLOAT | 1 | 0 | ℃ |  |  | 0.1 | ℃
| 08A7 | 2215 | RO | 408# cell temperature | FLOAT | 1 | 0 | ℃ |  |  | 0.1 | ℃
| 08A9 | 2217 | RO | 409# cell temperature | FLOAT | 1 | 0 | ℃ |  |  | 0.1 | ℃
| 08AB | 2219 | RO | 410# cell temperature | FLOAT | 1 | 0 | ℃ |  |  | 0.1 | ℃
| 08AD | 2221 | RO | 411# cell temperature | FLOAT | 1 | 0 | ℃ |  |  | 0.1 | ℃
| 08AF | 2223 | RO | 412# cell temperature | FLOAT | 1 | 0 | ℃ |  |  | 0.1 | ℃
| 08B1 | 2225 | RO | 413# cell temperature | FLOAT | 1 | 0 | ℃ |  |  | 0.1 | ℃
| 08B3 | 2227 | RO | 414# cell temperature | FLOAT | 1 | 0 | ℃ |  |  | 0.1 | ℃
| 08B5 | 2229 | RO | 415# cell temperature | FLOAT | 1 | 0 | ℃ |  |  | 0.1 | ℃
| 08B7 | 2231 | RO | 416# cell temperature | FLOAT | 1 | 0 | ℃ |  |  | 0.1 | ℃
| 08B9 | 2233 | RO | reserve | FLOAT
| 08BB | 2235 | RO | reserve | FLOAT
| 08BD | 2237 | RO | reserve | FLOAT
| 08BF | 2239 | RO | reserve | FLOAT
| 08C1 | 2241 | RO | reserve | FLOAT
| 08C3 | 2243 | RO | reserve | FLOAT
| 08C5 | 2245 | RO | reserve | FLOAT
| 08C7 | 2247 | RO | reserve | FLOAT
| 08C9 | 2249 | RO | reserve | FLOAT
| 08CB | 2251 | RO | reserve | FLOAT
| 08CD | 2253 | RO | reserve | FLOAT
| 08CF | 2255 | RO | reserve | FLOAT
| 08D1 | 2257 | RO | reserve | FLOAT
| 08D3 | 2259 | RO | reserve | FLOAT
| 08D5 | 2261 | RO | reserve | FLOAT
| 08D7 | 2263 | RO | reserve | FLOAT
| 08D9 | 2265 | RO | reserve | FLOAT
| 08DB | 2267 | RO | reserve | FLOAT
| 08DD | 2269 | RO | reserve | FLOAT
| 08DF | 2271 | RO | reserve | FLOAT
| 80 | 2273 | RO | reserve | FLOAT
| 8000 | 2275 | RO | reserve | FLOAT
| 800000 | 2277 | RO | reserve | FLOAT
| 80000000 | 2279 | RO | reserve | FLOAT
| 8000000000 | 2281 | RO | reserve | FLOAT
| 08EB | 2283 | RO | reserve | FLOAT
| 08ED | 2285 | RO | reserve | FLOAT
| 08EF | 2287 | RO | reserve | FLOAT
| 08F1 | 2289 | RO | reserve | FLOAT
| 08F3 | 2291 | RO | reserve | FLOAT
| 08F5 | 2293 | RO | reserve | FLOAT
| 08F7 | 2295 | RO | reserve | FLOAT
| 08F9 | 2297 | RO | reserve | FLOAT
| 08FB | 2299 | RO | reserve | FLOAT
| 08FD | 2301 | RO | reserve | FLOAT
| 08FF | 2303 | RO | reserve | FLOAT
| 901 | 2305 | RO | reserve | FLOAT
| 903 | 2307 | RO | reserve | FLOAT
| 905 | 2309 | RO | reserve | FLOAT
| 907 | 2311 | RO | reserve | FLOAT
| 909 | 2313 | RO | reserve | FLOAT
| 090B | 2315 | RO | reserve | FLOAT
| 090D | 2317 | RO | reserve | FLOAT
| 090F | 2319 | RO | reserve | FLOAT
| 911 | 2321 | RO | reserve | FLOAT
| 913 | 2323 | RO | reserve | FLOAT
| 915 | 2325 | RO | reserve | FLOAT
| 917 | 2327 | RO | reserve | FLOAT
| 919 | 2329 | RO | reserve | FLOAT
| 091B | 2331 | RO | reserve | FLOAT
| 091D | 2333 | RO | reserve | FLOAT
| 091F | 2335 | RO | reserve | FLOAT
| 921 | 2337 | RO | reserve | FLOAT
| 923 | 2339 | RO | reserve | FLOAT
| 925 | 2341 | RO | reserve | FLOAT
| 927 | 2343 | RO | reserve | FLOAT
| 929 | 2345 | RO | reserve | FLOAT
| 092B | 2347 | RO | reserve | FLOAT
| 092D | 2349 | RO | reserve | FLOAT
| 092F | 2351 | RO | reserve | FLOAT
| 931 | 2353 | RO | reserve | FLOAT
| 933 | 2355 | RO | reserve | FLOAT
| 935 | 2357 | RO | reserve | FLOAT
| 937 | 2359 | RO | reserve | FLOAT
| 939 | 2361 | RO | reserve | FLOAT
| 093B | 2363 | RO | reserve | FLOAT
| 093D | 2365 | RO | reserve | FLOAT
| 093F | 2367 | RO | reserve | FLOAT
| 941 | 2369 | RO | reserve | FLOAT
| 943 | 2371 | RO | reserve | FLOAT
| 945 | 2373 | RO | reserve | FLOAT
| 947 | 2375 | RO | reserve | FLOAT
| 949 | 2377 | RO | reserve | FLOAT
| 094B | 2379 | RO | reserve | FLOAT
| 094D | 2381 | RO | reserve | FLOAT
| 094F | 2383 | RO | reserve | FLOAT
| 951 | 2385 | RO | reserve | FLOAT
| 953 | 2387 | RO | reserve | FLOAT
| 955 | 2389 | RO | reserve | FLOAT
| 957 | 2391 | RO | reserve | FLOAT
| 959 | 2393 | RO | reserve | FLOAT
| 095B | 2395 | RO | reserve | FLOAT
| 095D | 2397 | RO | reserve | FLOAT
| 095F | 2399 | RO | reserve | FLOAT
| 961 | 2401 | RO | reserve | FLOAT
| 963 | 2403 | RO | reserve | FLOAT
| 965 | 2405 | RO | reserve | FLOAT
| 967 | 2407 | RO | reserve | FLOAT
| 969 | 2409 | RO | reserve | FLOAT
| 096B | 2411 | RO | reserve | FLOAT
| 096D | 2413 | RO | reserve | FLOAT
| 096F | 2415 | RO | reserve | FLOAT
| 971 | 2417 | RO | reserve | FLOAT
| 973 | 2419 | RO | reserve | FLOAT
| 975 | 2421 | RO | reserve | FLOAT
| 977 | 2423 | RO | reserve | FLOAT
| 979 | 2425 | RO | reserve | FLOAT
| 097B | 2427 | RO | reserve | FLOAT
| 097D | 2429 | RO | reserve | FLOAT
| 097F | 2431 | RO | reserve | FLOAT
| 981 | 2433 | RO | reserve | FLOAT
| 983 | 2435 | RO | reserve | FLOAT
| 985 | 2437 | RO | reserve | FLOAT
| 987 | 2439 | RO | reserve | FLOAT
| 989 | 2441 | RO | reserve | FLOAT
| 098B | 2443 | RO | reserve | FLOAT
| 098D | 2445 | RO | reserve | FLOAT
| 098F | 2447 | RO | reserve | FLOAT
| 991 | 2449 | RO | reserve | FLOAT
| 993 | 2451 | RO | reserve | FLOAT
| 995 | 2453 | RO | reserve | FLOAT
| 997 | 2455 | RO | reserve | FLOAT
| 999 | 2457 | RO | reserve | FLOAT
| 099B | 2459 | RO | reserve | FLOAT
| 099D | 2461 | RO | reserve | FLOAT
| 099F | 2463 | RO | reserve | FLOAT
| 09A1 | 2465 | RO | reserve | FLOAT
| 09A3 | 2467 | RO | reserve | FLOAT
| 09A5 | 2469 | RO | reserve | FLOAT
| 09A7 | 2471 | RO | reserve | FLOAT
| 09A9 | 2473 | RO | reserve | FLOAT
| 09AB | 2475 | RO | reserve | FLOAT
| 09AD | 2477 | RO | reserve | FLOAT
| 09AF | 2479 | RO | reserve | FLOAT
| 09B1 | 2481 | RO | reserve | FLOAT
| 09B3 | 2483 | RO | reserve | FLOAT
| 09B5 | 2485 | RO | reserve | FLOAT
| 09B7 | 2487 | RO | reserve | FLOAT
| 09B9 | 2489 | RO | reserve | FLOAT
| 09BB | 2491 | RO | reserve | FLOAT
| 09BD | 2493 | RO | reserve | FLOAT
| 09BF | 2495 | RO | reserve | FLOAT
| 09C1 | 2497 | RO | reserve | FLOAT
| 09C3 | 2499 | RO | reserve | FLOAT
| 09C5 | 2501 | RO | reserve | FLOAT
| 09C7 | 2503 | RO | reserve | FLOAT
| 09C9 | 2505 | RO | reserve | FLOAT
| 09CB | 2507 | RO | reserve | FLOAT
| 09CD | 2509 | RO | reserve | FLOAT
| 09CF | 2511 | RO | reserve | FLOAT
| 09D1 | 2513 | RO | reserve | FLOAT
| 09D3 | 2515 | RO | reserve | FLOAT
| 09D5 | 2517 | RO | reserve | FLOAT
| 09D7 | 2519 | RO | reserve | FLOAT
| 09D9 | 2521 | RO | reserve | FLOAT
| 09DB | 2523 | RO | reserve | FLOAT
| 09DD | 2525 | RO | reserve | FLOAT
| 09DF | 2527 | RO | reserve | FLOAT
| 90 | 2529 | RO | reserve | FLOAT
| 9000 | 2531 | RO | reserve | FLOAT
| 900000 | 2533 | RO | reserve | FLOAT
| 90000000 | 2535 | RO | reserve | FLOAT
| 9000000000 | 2537 | RO | reserve | FLOAT
| 09EB | 2539 | RO | reserve | FLOAT
| 09ED | 2541 | RO | reserve | FLOAT
| 09EF | 2543 | RO | reserve | FLOAT
| 09F1 | 2545 | RO | reserve | FLOAT
| 09F3 | 2547 | RO | reserve | FLOAT
| 09F5 | 2549 | RO | reserve | FLOAT
| 09F7 | 2551 | RO | reserve | FLOAT
| 09F9 | 2553 | RO | reserve | FLOAT
| 09FB | 2555 | RO | reserve | FLOAT
| 09FD | 2557 | RO | reserve | FLOAT
| 09FF | 2559 | RO | reserve | FLOAT
| 0A01 | 2561 | RO | reserve | FLOAT
| 0A03 | 2563 | RO | reserve | FLOAT
| 0A05 | 2565 | RO | reserve | FLOAT
| 0A07 | 2567 | RO | reserve | FLOAT
| 0A09 | 2569 | RO | reserve | FLOAT
| 0A0B | 2571 | RO | reserve | FLOAT
| 0A0D | 2573 | RO | reserve | FLOAT
| 0A0F | 2575 | RO | reserve | FLOAT
| 0A11 | 2577 | RO | reserve | FLOAT
| 0A13 | 2579 | RO | reserve | FLOAT
| 0A15 | 2581 | RO | reserve | FLOAT
| 0A17 | 2583 | RO | reserve | FLOAT
| 0A19 | 2585 | RO | reserve | FLOAT
| 0A1B | 2587 | RO | reserve | FLOAT
| 0A1D | 2589 | RO | reserve | FLOAT
| 0A1F | 2591 | RO | reserve | FLOAT
| 0A21 | 2593 | RO | reserve | FLOAT
| 0A23 | 2595 | RO | reserve | FLOAT
| 0A25 | 2597 | RO | reserve | FLOAT
| 0A27 | 2599 | RO | reserve | FLOAT

## Cell Balance
Register Type | Register Address |  | Attributes | Meaning | Remarks
| Hexadecimal | Decimal
Cell balance data (Each rack Modbus address independent, starting from 2, discrete input registers, function code0x02 same Modbus address as rack data, same function code, different register addresses) | 00C9 | 201 | RO | 1# cell charge balance state | 0--no balance, 1--balance
| 00CA | 202 | RO | 2# cell charge balance state | 0--no balance, 1--balance
| 00CB | 203 | RO | 3# cell charge balance state | 0--no balance, 1--balance
| 00CC | 204 | RO | 4# cell charge balance state | 0--no balance, 1--balance
| 00CD | 205 | RO | 5# cell charge balance state | 0--no balance, 1--balance
| 00CE | 206 | RO | 6# cell charge balance state | 0--no balance, 1--balance
| 00CF | 207 | RO | 7# cell charge balance state | 0--no balance, 1--balance
| 00D0 | 208 | RO | 8# cell charge balance state | 0--no balance, 1--balance
| 00D1 | 209 | RO | 9# cell charge balance state | 0--no balance, 1--balance
| 00D2 | 210 | RO | 10# cell charge balance state | 0--no balance, 1--balance
| 00D3 | 211 | RO | 11# cell charge balance state | 0--no balance, 1--balance
| 00D4 | 212 | RO | 12# cell charge balance state | 0--no balance, 1--balance
| 00D5 | 213 | RO | 13# cell charge balance state | 0--no balance, 1--balance
| 00D6 | 214 | RO | 14# cell charge balance state | 0--no balance, 1--balance
| 00D7 | 215 | RO | 15# cell charge balance state | 0--no balance, 1--balance
| 00D8 | 216 | RO | 16# cell charge balance state | 0--no balance, 1--balance
| 00D9 | 217 | RO | 17# cell charge balance state | 0--no balance, 1--balance
| 00DA | 218 | RO | 18# cell charge balance state | 0--no balance, 1--balance
| 00DB | 219 | RO | 19# cell charge balance state | 0--no balance, 1--balance
| 00DC | 220 | RO | 20# cell charge balance state | 0--no balance, 1--balance
| 00DD | 221 | RO | 21# cell charge balance state | 0--no balance, 1--balance
| 00DE | 222 | RO | 22# cell charge balance state | 0--no balance, 1--balance
| 00DF | 223 | RO | 23# cell charge balance state | 0--no balance, 1--balance
| 00E0 | 224 | RO | 24# cell charge balance state | 0--no balance, 1--balance
| 00E1 | 225 | RO | 25# cell charge balance state | 0--no balance, 1--balance
| 00E2 | 226 | RO | 26# cell charge balance state | 0--no balance, 1--balance
| 00E3 | 227 | RO | 27# cell charge balance state | 0--no balance, 1--balance
| 00E4 | 228 | RO | 28# cell charge balance state | 0--no balance, 1--balance
| 00E5 | 229 | RO | 29# cell charge balance state | 0--no balance, 1--balance
| 00E6 | 230 | RO | 30# cell charge balance state | 0--no balance, 1--balance
| 00E7 | 231 | RO | 31# cell charge balance state | 0--no balance, 1--balance
| 00E8 | 232 | RO | 32# cell charge balance state | 0--no balance, 1--balance
| 00E9 | 233 | RO | 33# cell charge balance state | 0--no balance, 1--balance
| 00EA | 234 | RO | 34# cell charge balance state | 0--no balance, 1--balance
| 00EB | 235 | RO | 35# cell charge balance state | 0--no balance, 1--balance
| 00EC | 236 | RO | 36# cell charge balance state | 0--no balance, 1--balance
| 00ED | 237 | RO | 37# cell charge balance state | 0--no balance, 1--balance
| 00EE | 238 | RO | 38# cell charge balance state | 0--no balance, 1--balance
| 00EF | 239 | RO | 39# cell charge balance state | 0--no balance, 1--balance
| 00F0 | 240 | RO | 40# cell charge balance state | 0--no balance, 1--balance
| 00F1 | 241 | RO | 41# cell charge balance state | 0--no balance, 1--balance
| 00F2 | 242 | RO | 42# cell charge balance state | 0--no balance, 1--balance
| 00F3 | 243 | RO | 43# cell charge balance state | 0--no balance, 1--balance
| 00F4 | 244 | RO | 44# cell charge balance state | 0--no balance, 1--balance
| 00F5 | 245 | RO | 45# cell charge balance state | 0--no balance, 1--balance
| 00F6 | 246 | RO | 46# cell charge balance state | 0--no balance, 1--balance
| 00F7 | 247 | RO | 47# cell charge balance state | 0--no balance, 1--balance
| 00F8 | 248 | RO | 48# cell charge balance state | 0--no balance, 1--balance
| 00F9 | 249 | RO | 49# cell charge balance state | 0--no balance, 1--balance
| 00FA | 250 | RO | 50# cell charge balance state | 0--no balance, 1--balance
| 00FB | 251 | RO | 51# cell charge balance state | 0--no balance, 1--balance
| 00FC | 252 | RO | 52# cell charge balance state | 0--no balance, 1--balance
| 00FD | 253 | RO | 53# cell charge balance state | 0--no balance, 1--balance
| 00FE | 254 | RO | 54# cell charge balance state | 0--no balance, 1--balance
| 00FF | 255 | RO | 55# cell charge balance state | 0--no balance, 1--balance
| 0100 | 256 | RO | 56# cell charge balance state | 0--no balance, 1--balance
| 0101 | 257 | RO | 57# cell charge balance state | 0--no balance, 1--balance
| 0102 | 258 | RO | 58# cell charge balance state | 0--no balance, 1--balance
| 0103 | 259 | RO | 59# cell charge balance state | 0--no balance, 1--balance
| 0104 | 260 | RO | 60# cell charge balance state | 0--no balance, 1--balance
| 0105 | 261 | RO | 61# cell charge balance state | 0--no balance, 1--balance
| 0106 | 262 | RO | 62# cell charge balance state | 0--no balance, 1--balance
| 0107 | 263 | RO | 63# cell charge balance state | 0--no balance, 1--balance
| 0108 | 264 | RO | 64# cell charge balance state | 0--no balance, 1--balance
| 0109 | 265 | RO | 65# cell charge balance state | 0--no balance, 1--balance
| 010A | 266 | RO | 66# cell charge balance state | 0--no balance, 1--balance
| 010B | 267 | RO | 67# cell charge balance state | 0--no balance, 1--balance
| 010C | 268 | RO | 68# cell charge balance state | 0--no balance, 1--balance
| 010D | 269 | RO | 69# cell charge balance state | 0--no balance, 1--balance
| 010E | 270 | RO | 70# cell charge balance state | 0--no balance, 1--balance
| 010F | 271 | RO | 71# cell charge balance state | 0--no balance, 1--balance
| 0110 | 272 | RO | 72# cell charge balance state | 0--no balance, 1--balance
| 0111 | 273 | RO | 73# cell charge balance state | 0--no balance, 1--balance
| 0112 | 274 | RO | 74# cell charge balance state | 0--no balance, 1--balance
| 0113 | 275 | RO | 75# cell charge balance state | 0--no balance, 1--balance
| 0114 | 276 | RO | 76# cell charge balance state | 0--no balance, 1--balance
| 0115 | 277 | RO | 77# cell charge balance state | 0--no balance, 1--balance
| 0116 | 278 | RO | 78# cell charge balance state | 0--no balance, 1--balance
| 0117 | 279 | RO | 79# cell charge balance state | 0--no balance, 1--balance
| 0118 | 280 | RO | 80# cell charge balance state | 0--no balance, 1--balance
| 0119 | 281 | RO | 81# cell charge balance state | 0--no balance, 1--balance
| 011A | 282 | RO | 82# cell charge balance state | 0--no balance, 1--balance
| 011B | 283 | RO | 83# cell charge balance state | 0--no balance, 1--balance
| 011C | 284 | RO | 84# cell charge balance state | 0--no balance, 1--balance
| 011D | 285 | RO | 85# cell charge balance state | 0--no balance, 1--balance
| 011E | 286 | RO | 86# cell charge balance state | 0--no balance, 1--balance
| 011F | 287 | RO | 87# cell charge balance state | 0--no balance, 1--balance
| 0120 | 288 | RO | 88# cell charge balance state | 0--no balance, 1--balance
| 0121 | 289 | RO | 89# cell charge balance state | 0--no balance, 1--balance
| 0122 | 290 | RO | 90# cell charge balance state | 0--no balance, 1--balance
| 0123 | 291 | RO | 91# cell charge balance state | 0--no balance, 1--balance
| 0124 | 292 | RO | 92# cell charge balance state | 0--no balance, 1--balance
| 0125 | 293 | RO | 93# cell charge balance state | 0--no balance, 1--balance
| 0126 | 294 | RO | 94# cell charge balance state | 0--no balance, 1--balance
| 0127 | 295 | RO | 95# cell charge balance state | 0--no balance, 1--balance
| 0128 | 296 | RO | 96# cell charge balance state | 0--no balance, 1--balance
| 0129 | 297 | RO | 97# cell charge balance state | 0--no balance, 1--balance
| 012A | 298 | RO | 98# cell charge balance state | 0--no balance, 1--balance
| 012B | 299 | RO | 99# cell charge balance state | 0--no balance, 1--balance
| 012C | 300 | RO | 100# cell charge balance state | 0--no balance, 1--balance
| 012D | 301 | RO | 101# cell charge balance state | 0--no balance, 1--balance
| 012E | 302 | RO | 102# cell charge balance state | 0--no balance, 1--balance
| 012F | 303 | RO | 103# cell charge balance state | 0--no balance, 1--balance
| 0130 | 304 | RO | 104# cell charge balance state | 0--no balance, 1--balance
| 0131 | 305 | RO | 105# cell charge balance state | 0--no balance, 1--balance
| 0132 | 306 | RO | 106# cell charge balance state | 0--no balance, 1--balance
| 0133 | 307 | RO | 107# cell charge balance state | 0--no balance, 1--balance
| 0134 | 308 | RO | 108# cell charge balance state | 0--no balance, 1--balance
| 0135 | 309 | RO | 109# cell charge balance state | 0--no balance, 1--balance
| 0136 | 310 | RO | 110# cell charge balance state | 0--no balance, 1--balance
| 0137 | 311 | RO | 111# cell charge balance state | 0--no balance, 1--balance
| 0138 | 312 | RO | 112# cell charge balance state | 0--no balance, 1--balance
| 0139 | 313 | RO | 113# cell charge balance state | 0--no balance, 1--balance
| 013A | 314 | RO | 114# cell charge balance state | 0--no balance, 1--balance
| 013B | 315 | RO | 115# cell charge balance state | 0--no balance, 1--balance
| 013C | 316 | RO | 116# cell charge balance state | 0--no balance, 1--balance
| 013D | 317 | RO | 117# cell charge balance state | 0--no balance, 1--balance
| 013E | 318 | RO | 118# cell charge balance state | 0--no balance, 1--balance
| 013F | 319 | RO | 119# cell charge balance state | 0--no balance, 1--balance
| 0140 | 320 | RO | 120# cell charge balance state | 0--no balance, 1--balance
| 0141 | 321 | RO | 121# cell charge balance state | 0--no balance, 1--balance
| 0142 | 322 | RO | 122# cell charge balance state | 0--no balance, 1--balance
| 0143 | 323 | RO | 123# cell charge balance state | 0--no balance, 1--balance
| 0144 | 324 | RO | 124# cell charge balance state | 0--no balance, 1--balance
| 0145 | 325 | RO | 125# cell charge balance state | 0--no balance, 1--balance
| 0146 | 326 | RO | 126# cell charge balance state | 0--no balance, 1--balance
| 0147 | 327 | RO | 127# cell charge balance state | 0--no balance, 1--balance
| 0148 | 328 | RO | 128# cell charge balance state | 0--no balance, 1--balance
| 0149 | 329 | RO | 129# cell charge balance state | 0--no balance, 1--balance
| 014A | 330 | RO | 130# cell charge balance state | 0--no balance, 1--balance
| 014B | 331 | RO | 131# cell charge balance state | 0--no balance, 1--balance
| 014C | 332 | RO | 132# cell charge balance state | 0--no balance, 1--balance
| 014D | 333 | RO | 133# cell charge balance state | 0--no balance, 1--balance
| 014E | 334 | RO | 134# cell charge balance state | 0--no balance, 1--balance
| 014F | 335 | RO | 135# cell charge balance state | 0--no balance, 1--balance
| 0150 | 336 | RO | 136# cell charge balance state | 0--no balance, 1--balance
| 0151 | 337 | RO | 137# cell charge balance state | 0--no balance, 1--balance
| 0152 | 338 | RO | 138# cell charge balance state | 0--no balance, 1--balance
| 0153 | 339 | RO | 139# cell charge balance state | 0--no balance, 1--balance
| 0154 | 340 | RO | 140# cell charge balance state | 0--no balance, 1--balance
| 0155 | 341 | RO | 141# cell charge balance state | 0--no balance, 1--balance
| 0156 | 342 | RO | 142# cell charge balance state | 0--no balance, 1--balance
| 0157 | 343 | RO | 143# cell charge balance state | 0--no balance, 1--balance
| 0158 | 344 | RO | 144# cell charge balance state | 0--no balance, 1--balance
| 0159 | 345 | RO | 145# cell charge balance state | 0--no balance, 1--balance
| 015A | 346 | RO | 146# cell charge balance state | 0--no balance, 1--balance
| 015B | 347 | RO | 147# cell charge balance state | 0--no balance, 1--balance
| 015C | 348 | RO | 148# cell charge balance state | 0--no balance, 1--balance
| 015D | 349 | RO | 149# cell charge balance state | 0--no balance, 1--balance
| 015E | 350 | RO | 150# cell charge balance state | 0--no balance, 1--balance
| 015F | 351 | RO | 151# cell charge balance state | 0--no balance, 1--balance
| 0160 | 352 | RO | 152# cell charge balance state | 0--no balance, 1--balance
| 0161 | 353 | RO | 153# cell charge balance state | 0--no balance, 1--balance
| 0162 | 354 | RO | 154# cell charge balance state | 0--no balance, 1--balance
| 0163 | 355 | RO | 155# cell charge balance state | 0--no balance, 1--balance
| 0164 | 356 | RO | 156# cell charge balance state | 0--no balance, 1--balance
| 0165 | 357 | RO | 157# cell charge balance state | 0--no balance, 1--balance
| 0166 | 358 | RO | 158# cell charge balance state | 0--no balance, 1--balance
| 0167 | 359 | RO | 159# cell charge balance state | 0--no balance, 1--balance
| 0168 | 360 | RO | 160# cell charge balance state | 0--no balance, 1--balance
| 0169 | 361 | RO | 161# cell charge balance state | 0--no balance, 1--balance
| 016A | 362 | RO | 162# cell charge balance state | 0--no balance, 1--balance
| 016B | 363 | RO | 163# cell charge balance state | 0--no balance, 1--balance
| 016C | 364 | RO | 164# cell charge balance state | 0--no balance, 1--balance
| 016D | 365 | RO | 165# cell charge balance state | 0--no balance, 1--balance
| 016E | 366 | RO | 166# cell charge balance state | 0--no balance, 1--balance
| 016F | 367 | RO | 167# cell charge balance state | 0--no balance, 1--balance
| 0170 | 368 | RO | 168# cell charge balance state | 0--no balance, 1--balance
| 0171 | 369 | RO | 169# cell charge balance state | 0--no balance, 1--balance
| 0172 | 370 | RO | 170# cell charge balance state | 0--no balance, 1--balance
| 0173 | 371 | RO | 171# cell charge balance state | 0--no balance, 1--balance
| 0174 | 372 | RO | 172# cell charge balance state | 0--no balance, 1--balance
| 0175 | 373 | RO | 173# cell charge balance state | 0--no balance, 1--balance
| 0176 | 374 | RO | 174# cell charge balance state | 0--no balance, 1--balance
| 0177 | 375 | RO | 175# cell charge balance state | 0--no balance, 1--balance
| 0178 | 376 | RO | 176# cell charge balance state | 0--no balance, 1--balance
| 0179 | 377 | RO | 177# cell charge balance state | 0--no balance, 1--balance
| 017A | 378 | RO | 178# cell charge balance state | 0--no balance, 1--balance
| 017B | 379 | RO | 179# cell charge balance state | 0--no balance, 1--balance
| 017C | 380 | RO | 180# cell charge balance state | 0--no balance, 1--balance
| 017D | 381 | RO | 181# cell charge balance state | 0--no balance, 1--balance
| 017E | 382 | RO | 182# cell charge balance state | 0--no balance, 1--balance
| 017F | 383 | RO | 183# cell charge balance state | 0--no balance, 1--balance
| 0180 | 384 | RO | 184# cell charge balance state | 0--no balance, 1--balance
| 0181 | 385 | RO | 185# cell charge balance state | 0--no balance, 1--balance
| 0182 | 386 | RO | 186# cell charge balance state | 0--no balance, 1--balance
| 0183 | 387 | RO | 187# cell charge balance state | 0--no balance, 1--balance
| 0184 | 388 | RO | 188# cell charge balance state | 0--no balance, 1--balance
| 0185 | 389 | RO | 189# cell charge balance state | 0--no balance, 1--balance
| 0186 | 390 | RO | 190# cell charge balance state | 0--no balance, 1--balance
| 0187 | 391 | RO | 191# cell charge balance state | 0--no balance, 1--balance
| 0188 | 392 | RO | 192# cell charge balance state | 0--no balance, 1--balance
| 0189 | 393 | RO | 193# cell charge balance state | 0--no balance, 1--balance
| 018A | 394 | RO | 194# cell charge balance state | 0--no balance, 1--balance
| 018B | 395 | RO | 195# cell charge balance state | 0--no balance, 1--balance
| 018C | 396 | RO | 196# cell charge balance state | 0--no balance, 1--balance
| 018D | 397 | RO | 197# cell charge balance state | 0--no balance, 1--balance
| 018E | 398 | RO | 198# cell charge balance state | 0--no balance, 1--balance
| 018F | 399 | RO | 199# cell charge balance state | 0--no balance, 1--balance
| 0190 | 400 | RO | 200# cell charge balance state | 0--no balance, 1--balance
| 0191 | 401 | RO | 201# cell charge balance state | 0--no balance, 1--balance
| 0192 | 402 | RO | 202# cell charge balance state | 0--no balance, 1--balance
| 0193 | 403 | RO | 203# cell charge balance state | 0--no balance, 1--balance
| 0194 | 404 | RO | 204# cell charge balance state | 0--no balance, 1--balance
| 0195 | 405 | RO | 205# cell charge balance state | 0--no balance, 1--balance
| 0196 | 406 | RO | 206# cell charge balance state | 0--no balance, 1--balance
| 0197 | 407 | RO | 207# cell charge balance state | 0--no balance, 1--balance
| 0198 | 408 | RO | 208# cell charge balance state | 0--no balance, 1--balance
| 0199 | 409 | RO | 209# cell charge balance state | 0--no balance, 1--balance
| 019A | 410 | RO | 210# cell charge balance state | 0--no balance, 1--balance
| 019B | 411 | RO | 211# cell charge balance state | 0--no balance, 1--balance
| 019C | 412 | RO | 212# cell charge balance state | 0--no balance, 1--balance
| 019D | 413 | RO | 213# cell charge balance state | 0--no balance, 1--balance
| 019E | 414 | RO | 214# cell charge balance state | 0--no balance, 1--balance
| 019F | 415 | RO | 215# cell charge balance state | 0--no balance, 1--balance
| 01A0 | 416 | RO | 216# cell charge balance state | 0--no balance, 1--balance
| 01A1 | 417 | RO | 217# cell charge balance state | 0--no balance, 1--balance
| 01A2 | 418 | RO | 218# cell charge balance state | 0--no balance, 1--balance
| 01A3 | 419 | RO | 219# cell charge balance state | 0--no balance, 1--balance
| 01A4 | 420 | RO | 220# cell charge balance state | 0--no balance, 1--balance
| 01A5 | 421 | RO | 221# cell charge balance state | 0--no balance, 1--balance
| 01A6 | 422 | RO | 222# cell charge balance state | 0--no balance, 1--balance
| 01A7 | 423 | RO | 223# cell charge balance state | 0--no balance, 1--balance
| 01A8 | 424 | RO | 224# cell charge balance state | 0--no balance, 1--balance
| 01A9 | 425 | RO | 225# cell charge balance state | 0--no balance, 1--balance
| 01AA | 426 | RO | 226# cell charge balance state | 0--no balance, 1--balance
| 01AB | 427 | RO | 227# cell charge balance state | 0--no balance, 1--balance
| 01AC | 428 | RO | 228# cell charge balance state | 0--no balance, 1--balance
| 01AD | 429 | RO | 229# cell charge balance state | 0--no balance, 1--balance
| 01AE | 430 | RO | 230# cell charge balance state | 0--no balance, 1--balance
| 01AF | 431 | RO | 231# cell charge balance state | 0--no balance, 1--balance
| 01B0 | 432 | RO | 232# cell charge balance state | 0--no balance, 1--balance
| 01B1 | 433 | RO | 233# cell charge balance state | 0--no balance, 1--balance
| 01B2 | 434 | RO | 234# cell charge balance state | 0--no balance, 1--balance
| 01B3 | 435 | RO | 235# cell charge balance state | 0--no balance, 1--balance
| 01B4 | 436 | RO | 236# cell charge balance state | 0--no balance, 1--balance
| 01B5 | 437 | RO | 237# cell charge balance state | 0--no balance, 1--balance
| 01B6 | 438 | RO | 238# cell charge balance state | 0--no balance, 1--balance
| 01B7 | 439 | RO | 239# cell charge balance state | 0--no balance, 1--balance
| 01B8 | 440 | RO | 240# cell charge balance state | 0--no balance, 1--balance
| 01B9 | 441 | RO | 241# cell charge balance state | 0--no balance, 1--balance
| 01BA | 442 | RO | 242# cell charge balance state | 0--no balance, 1--balance
| 01BB | 443 | RO | 243# cell charge balance state | 0--no balance, 1--balance
| 01BC | 444 | RO | 244# cell charge balance state | 0--no balance, 1--balance
| 01BD | 445 | RO | 245# cell charge balance state | 0--no balance, 1--balance
| 01BE | 446 | RO | 246# cell charge balance state | 0--no balance, 1--balance
| 01BF | 447 | RO | 247# cell charge balance state | 0--no balance, 1--balance
| 01C0 | 448 | RO | 248# cell charge balance state | 0--no balance, 1--balance
| 01C1 | 449 | RO | 249# cell charge balance state | 0--no balance, 1--balance
| 01C2 | 450 | RO | 250# cell charge balance state | 0--no balance, 1--balance
| 01C3 | 451 | RO | 251# cell charge balance state | 0--no balance, 1--balance
| 01C4 | 452 | RO | 252# cell charge balance state | 0--no balance, 1--balance
| 01C5 | 453 | RO | 253# cell charge balance state | 0--no balance, 1--balance
| 01C6 | 454 | RO | 254# cell charge balance state | 0--no balance, 1--balance
| 01C7 | 455 | RO | 255# cell charge balance state | 0--no balance, 1--balance
| 01C8 | 456 | RO | 256# cell charge balance state | 0--no balance, 1--balance
| 01C9 | 457 | RO | 257# cell charge balance state | 0--no balance, 1--balance
| 01CA | 458 | RO | 258# cell charge balance state | 0--no balance, 1--balance
| 01CB | 459 | RO | 259# cell charge balance state | 0--no balance, 1--balance
| 01CC | 460 | RO | 260# cell charge balance state | 0--no balance, 1--balance
| 01CD | 461 | RO | 261# cell charge balance state | 0--no balance, 1--balance
| 01CE | 462 | RO | 262# cell charge balance state | 0--no balance, 1--balance
| 01CF | 463 | RO | 263# cell charge balance state | 0--no balance, 1--balance
| 01D0 | 464 | RO | 264# cell charge balance state | 0--no balance, 1--balance
| 01D1 | 465 | RO | 265# cell charge balance state | 0--no balance, 1--balance
| 01D2 | 466 | RO | 266# cell charge balance state | 0--no balance, 1--balance
| 01D3 | 467 | RO | 267# cell charge balance state | 0--no balance, 1--balance
| 01D4 | 468 | RO | 268# cell charge balance state | 0--no balance, 1--balance
| 01D5 | 469 | RO | 269# cell charge balance state | 0--no balance, 1--balance
| 01D6 | 470 | RO | 270# cell charge balance state | 0--no balance, 1--balance
| 01D7 | 471 | RO | 271# cell charge balance state | 0--no balance, 1--balance
| 01D8 | 472 | RO | 272# cell charge balance state | 0--no balance, 1--balance
| 01D9 | 473 | RO | 273# cell charge balance state | 0--no balance, 1--balance
| 01DA | 474 | RO | 274# cell charge balance state | 0--no balance, 1--balance
| 01DB | 475 | RO | 275# cell charge balance state | 0--no balance, 1--balance
| 01DC | 476 | RO | 276# cell charge balance state | 0--no balance, 1--balance
| 01DD | 477 | RO | 277# cell charge balance state | 0--no balance, 1--balance
| 01DE | 478 | RO | 278# cell charge balance state | 0--no balance, 1--balance
| 01DF | 479 | RO | 279# cell charge balance state | 0--no balance, 1--balance
| 01E0 | 480 | RO | 280# cell charge balance state | 0--no balance, 1--balance
| 01E1 | 481 | RO | 281# cell charge balance state | 0--no balance, 1--balance
| 01E2 | 482 | RO | 282# cell charge balance state | 0--no balance, 1--balance
| 01E3 | 483 | RO | 283# cell charge balance state | 0--no balance, 1--balance
| 01E4 | 484 | RO | 284# cell charge balance state | 0--no balance, 1--balance
| 01E5 | 485 | RO | 285# cell charge balance state | 0--no balance, 1--balance
| 01E6 | 486 | RO | 286# cell charge balance state | 0--no balance, 1--balance
| 01E7 | 487 | RO | 287# cell charge balance state | 0--no balance, 1--balance
| 01E8 | 488 | RO | 288# cell charge balance state | 0--no balance, 1--balance
| 01E9 | 489 | RO | 289# cell charge balance state | 0--no balance, 1--balance
| 01EA | 490 | RO | 290# cell charge balance state | 0--no balance, 1--balance
| 01EB | 491 | RO | 291# cell charge balance state | 0--no balance, 1--balance
| 01EC | 492 | RO | 292# cell charge balance state | 0--no balance, 1--balance
| 01ED | 493 | RO | 293# cell charge balance state | 0--no balance, 1--balance
| 01EE | 494 | RO | 294# cell charge balance state | 0--no balance, 1--balance
| 01EF | 495 | RO | 295# cell charge balance state | 0--no balance, 1--balance
| 01F0 | 496 | RO | 296# cell charge balance state | 0--no balance, 1--balance
| 01F1 | 497 | RO | 297# cell charge balance state | 0--no balance, 1--balance
| 01F2 | 498 | RO | 298# cell charge balance state | 0--no balance, 1--balance
| 01F3 | 499 | RO | 299# cell charge balance state | 0--no balance, 1--balance
| 01F4 | 500 | RO | 300# cell charge balance state | 0--no balance, 1--balance
| 01F5 | 501 | RO | 301# cell charge balance state | 0--no balance, 1--balance
| 01F6 | 502 | RO | 302# cell charge balance state | 0--no balance, 1--balance
| 01F7 | 503 | RO | 303# cell charge balance state | 0--no balance, 1--balance
| 01F8 | 504 | RO | 304# cell charge balance state | 0--no balance, 1--balance
| 01F9 | 505 | RO | 305# cell charge balance state | 0--no balance, 1--balance
| 01FA | 506 | RO | 306# cell charge balance state | 0--no balance, 1--balance
| 01FB | 507 | RO | 307# cell charge balance state | 0--no balance, 1--balance
| 01FC | 508 | RO | 308# cell charge balance state | 0--no balance, 1--balance
| 01FD | 509 | RO | 309# cell charge balance state | 0--no balance, 1--balance
| 01FE | 510 | RO | 310# cell charge balance state | 0--no balance, 1--balance
| 01FF | 511 | RO | 311# cell charge balance state | 0--no balance, 1--balance
| 0200 | 512 | RO | 312# cell charge balance state | 0--no balance, 1--balance
| 0201 | 513 | RO | 313# cell charge balance state | 0--no balance, 1--balance
| 0202 | 514 | RO | 314# cell charge balance state | 0--no balance, 1--balance
| 0203 | 515 | RO | 315# cell charge balance state | 0--no balance, 1--balance
| 0204 | 516 | RO | 316# cell charge balance state | 0--no balance, 1--balance
| 0205 | 517 | RO | 317# cell charge balance state | 0--no balance, 1--balance
| 0206 | 518 | RO | 318# cell charge balance state | 0--no balance, 1--balance
| 0207 | 519 | RO | 319# cell charge balance state | 0--no balance, 1--balance
| 0208 | 520 | RO | 320# cell charge balance state | 0--no balance, 1--balance
| 0209 | 521 | RO | 321# cell charge balance state | 0--no balance, 1--balance
| 020A | 522 | RO | 322# cell charge balance state | 0--no balance, 1--balance
| 020B | 523 | RO | 323# cell charge balance state | 0--no balance, 1--balance
| 020C | 524 | RO | 324# cell charge balance state | 0--no balance, 1--balance
| 020D | 525 | RO | 325# cell charge balance state | 0--no balance, 1--balance
| 020E | 526 | RO | 326# cell charge balance state | 0--no balance, 1--balance
| 020F | 527 | RO | 327# cell charge balance state | 0--no balance, 1--balance
| 0210 | 528 | RO | 328# cell charge balance state | 0--no balance, 1--balance
| 0211 | 529 | RO | 329# cell charge balance state | 0--no balance, 1--balance
| 0212 | 530 | RO | 330# cell charge balance state | 0--no balance, 1--balance
| 0213 | 531 | RO | 331# cell charge balance state | 0--no balance, 1--balance
| 0214 | 532 | RO | 332# cell charge balance state | 0--no balance, 1--balance
| 0215 | 533 | RO | 333# cell charge balance state | 0--no balance, 1--balance
| 0216 | 534 | RO | 334# cell charge balance state | 0--no balance, 1--balance
| 0217 | 535 | RO | 335# cell charge balance state | 0--no balance, 1--balance
| 0218 | 536 | RO | 336# cell charge balance state | 0--no balance, 1--balance
| 0219 | 537 | RO | 337# cell charge balance state | 0--no balance, 1--balance
| 021A | 538 | RO | 338# cell charge balance state | 0--no balance, 1--balance
| 021B | 539 | RO | 339# cell charge balance state | 0--no balance, 1--balance
| 021C | 540 | RO | 340# cell charge balance state | 0--no balance, 1--balance
| 021D | 541 | RO | 341# cell charge balance state | 0--no balance, 1--balance
| 021E | 542 | RO | 342# cell charge balance state | 0--no balance, 1--balance
| 021F | 543 | RO | 343# cell charge balance state | 0--no balance, 1--balance
| 0220 | 544 | RO | 344# cell charge balance state | 0--no balance, 1--balance
| 0221 | 545 | RO | 345# cell charge balance state | 0--no balance, 1--balance
| 0222 | 546 | RO | 346# cell charge balance state | 0--no balance, 1--balance
| 0223 | 547 | RO | 347# cell charge balance state | 0--no balance, 1--balance
| 0224 | 548 | RO | 348# cell charge balance state | 0--no balance, 1--balance
| 0225 | 549 | RO | 349# cell charge balance state | 0--no balance, 1--balance
| 0226 | 550 | RO | 350# cell charge balance state | 0--no balance, 1--balance
| 0227 | 551 | RO | 351# cell charge balance state | 0--no balance, 1--balance
| 0228 | 552 | RO | 352# cell charge balance state | 0--no balance, 1--balance
| 0229 | 553 | RO | 353# cell charge balance state | 0--no balance, 1--balance
| 022A | 554 | RO | 354# cell charge balance state | 0--no balance, 1--balance
| 022B | 555 | RO | 355# cell charge balance state | 0--no balance, 1--balance
| 022C | 556 | RO | 356# cell charge balance state | 0--no balance, 1--balance
| 022D | 557 | RO | 357# cell charge balance state | 0--no balance, 1--balance
| 022E | 558 | RO | 358# cell charge balance state | 0--no balance, 1--balance
| 022F | 559 | RO | 359# cell charge balance state | 0--no balance, 1--balance
| 0230 | 560 | RO | 360# cell charge balance state | 0--no balance, 1--balance
| 0231 | 561 | RO | 361# cell charge balance state | 0--no balance, 1--balance
| 0232 | 562 | RO | 362# cell charge balance state | 0--no balance, 1--balance
| 0233 | 563 | RO | 363# cell charge balance state | 0--no balance, 1--balance
| 0234 | 564 | RO | 364# cell charge balance state | 0--no balance, 1--balance
| 0235 | 565 | RO | 365# cell charge balance state | 0--no balance, 1--balance
| 0236 | 566 | RO | 366# cell charge balance state | 0--no balance, 1--balance
| 0237 | 567 | RO | 367# cell charge balance state | 0--no balance, 1--balance
| 0238 | 568 | RO | 368# cell charge balance state | 0--no balance, 1--balance
| 0239 | 569 | RO | 369# cell charge balance state | 0--no balance, 1--balance
| 023A | 570 | RO | 370# cell charge balance state | 0--no balance, 1--balance
| 023B | 571 | RO | 371# cell charge balance state | 0--no balance, 1--balance
| 023C | 572 | RO | 372# cell charge balance state | 0--no balance, 1--balance
| 023D | 573 | RO | 373# cell charge balance state | 0--no balance, 1--balance
| 023E | 574 | RO | 374# cell charge balance state | 0--no balance, 1--balance
| 023F | 575 | RO | 375# cell charge balance state | 0--no balance, 1--balance
| 0240 | 576 | RO | 376# cell charge balance state | 0--no balance, 1--balance
| 0241 | 577 | RO | 377# cell charge balance state | 0--no balance, 1--balance
| 0242 | 578 | RO | 378# cell charge balance state | 0--no balance, 1--balance
| 0243 | 579 | RO | 379# cell charge balance state | 0--no balance, 1--balance
| 0244 | 580 | RO | 380# cell charge balance state | 0--no balance, 1--balance
| 0245 | 581 | RO | 381# cell charge balance state | 0--no balance, 1--balance
| 0246 | 582 | RO | 382# cell charge balance state | 0--no balance, 1--balance
| 0247 | 583 | RO | 383# cell charge balance state | 0--no balance, 1--balance
| 0248 | 584 | RO | 384# cell charge balance state | 0--no balance, 1--balance
| 0249 | 585 | RO | 385# cell charge balance state | 0--no balance, 1--balance
| 024A | 586 | RO | 386# cell charge balance state | 0--no balance, 1--balance
| 024B | 587 | RO | 387# cell charge balance state | 0--no balance, 1--balance
| 024C | 588 | RO | 388# cell charge balance state | 0--no balance, 1--balance
| 024D | 589 | RO | 389# cell charge balance state | 0--no balance, 1--balance
| 024E | 590 | RO | 390# cell charge balance state | 0--no balance, 1--balance
| 024F | 591 | RO | 391# cell charge balance state | 0--no balance, 1--balance
| 0250 | 592 | RO | 392# cell charge balance state | 0--no balance, 1--balance
| 0251 | 593 | RO | 393# cell charge balance state | 0--no balance, 1--balance
| 0252 | 594 | RO | 394# cell charge balance state | 0--no balance, 1--balance
| 0253 | 595 | RO | 395# cell charge balance state | 0--no balance, 1--balance
| 0254 | 596 | RO | 396# cell charge balance state | 0--no balance, 1--balance
| 0255 | 597 | RO | 397# cell charge balance state | 0--no balance, 1--balance
| 0256 | 598 | RO | 398# cell charge balance state | 0--no balance, 1--balance
| 0257 | 599 | RO | 399# cell charge balance state | 0--no balance, 1--balance
| 0258 | 600 | RO | 400# cell charge balance state | 0--no balance, 1--balance
| 0259 | 601 | RO | 401# cell charge balance state | 0--no balance, 1--balance
| 025A | 602 | RO | 402# cell charge balance state | 0--no balance, 1--balance
| 025B | 603 | RO | 403# cell charge balance state | 0--no balance, 1--balance
| 025C | 604 | RO | 404# cell charge balance state | 0--no balance, 1--balance
| 025D | 605 | RO | 405# cell charge balance state | 0--no balance, 1--balance
| 025E | 606 | RO | 406# cell charge balance state | 0--no balance, 1--balance
| 025F | 607 | RO | 407# cell charge balance state | 0--no balance, 1--balance
| 0260 | 608 | RO | 408# cell charge balance state | 0--no balance, 1--balance
| 0261 | 609 | RO | 409# cell charge balance state | 0--no balance, 1--balance
| 0262 | 610 | RO | 410# cell charge balance state | 0--no balance, 1--balance
| 0263 | 611 | RO | 411# cell charge balance state | 0--no balance, 1--balance
| 0264 | 612 | RO | 412# cell charge balance state | 0--no balance, 1--balance
| 0265 | 613 | RO | 413# cell charge balance state | 0--no balance, 1--balance
| 0266 | 614 | RO | 414# cell charge balance state | 0--no balance, 1--balance
| 0267 | 615 | RO | 415# cell charge balance state | 0--no balance, 1--balance
| 0268 | 616 | RO | 416# cell charge balance state | 0--no balance, 1--balance
| 0269 | 617 | RO | reserve
| 026A | 618 | RO | reserve
| 026B | 619 | RO | reserve
| 026C | 620 | RO | reserve
| 026D | 621 | RO | reserve
| 026E | 622 | RO | reserve
| 026F | 623 | RO | reserve
| 0270 | 624 | RO | reserve
| 0271 | 625 | RO | reserve
| 0272 | 626 | RO | reserve
| 0273 | 627 | RO | reserve
| 0274 | 628 | RO | reserve
| 0275 | 629 | RO | reserve
| 0276 | 630 | RO | reserve
| 0277 | 631 | RO | reserve
| 0278 | 632 | RO | reserve
| 0279 | 633 | RO | reserve
| 027A | 634 | RO | reserve
| 027B | 635 | RO | reserve
| 027C | 636 | RO | reserve
| 027D | 637 | RO | reserve
| 027E | 638 | RO | reserve
| 027F | 639 | RO | reserve
| 0280 | 640 | RO | reserve
| 0281 | 641 | RO | reserve
| 0282 | 642 | RO | reserve
| 0283 | 643 | RO | reserve
| 0284 | 644 | RO | reserve
| 0285 | 645 | RO | reserve
| 0286 | 646 | RO | reserve
| 0287 | 647 | RO | reserve
| 0288 | 648 | RO | reserve
| 0289 | 649 | RO | reserve
| 028A | 650 | RO | reserve
| 028B | 651 | RO | reserve
| 028C | 652 | RO | reserve
| 028D | 653 | RO | reserve
| 028E | 654 | RO | reserve
| 028F | 655 | RO | reserve
| 0290 | 656 | RO | reserve
| 0291 | 657 | RO | reserve
| 0292 | 658 | RO | reserve
| 0293 | 659 | RO | reserve
| 0294 | 660 | RO | reserve
| 0295 | 661 | RO | reserve
| 0296 | 662 | RO | reserve
| 0297 | 663 | RO | reserve
| 0298 | 664 | RO | reserve
| 0299 | 665 | RO | reserve
| 029A | 666 | RO | reserve
| 029B | 667 | RO | reserve
| 029C | 668 | RO | reserve
| 029D | 669 | RO | reserve
| 029E | 670 | RO | reserve
| 029F | 671 | RO | reserve
| 02A0 | 672 | RO | reserve
| 02A1 | 673 | RO | reserve
| 02A2 | 674 | RO | reserve
| 02A3 | 675 | RO | reserve
| 02A4 | 676 | RO | reserve
| 02A5 | 677 | RO | reserve
| 02A6 | 678 | RO | reserve
| 02A7 | 679 | RO | reserve
| 02A8 | 680 | RO | reserve
| 02A9 | 681 | RO | reserve
| 02AA | 682 | RO | reserve
| 02AB | 683 | RO | reserve
| 02AC | 684 | RO | reserve
| 02AD | 685 | RO | reserve
| 02AE | 686 | RO | reserve
| 02AF | 687 | RO | reserve
| 02B0 | 688 | RO | reserve
| 02B1 | 689 | RO | reserve
| 02B2 | 690 | RO | reserve
| 02B3 | 691 | RO | reserve
| 02B4 | 692 | RO | reserve
| 02B5 | 693 | RO | reserve
| 02B6 | 694 | RO | reserve
| 02B7 | 695 | RO | reserve
| 02B8 | 696 | RO | reserve
| 02B9 | 697 | RO | reserve
| 02BA | 698 | RO | reserve
| 02BB | 699 | RO | reserve
| 02BC | 700 | RO | reserve
| 02BD | 701 | RO | reserve
| 02BE | 702 | RO | reserve
| 02BF | 703 | RO | reserve
| 02C0 | 704 | RO | reserve
| 02C1 | 705 | RO | reserve
| 02C2 | 706 | RO | reserve
| 02C3 | 707 | RO | reserve
| 02C4 | 708 | RO | reserve
| 02C5 | 709 | RO | reserve
| 02C6 | 710 | RO | reserve
| 02C7 | 711 | RO | reserve
| 02C8 | 712 | RO | reserve
| 02C9 | 713 | RO | reserve
| 02CA | 714 | RO | reserve
| 02CB | 715 | RO | reserve
| 02CC | 716 | RO | reserve
| 02CD | 717 | RO | reserve
| 02CE | 718 | RO | reserve
| 02CF | 719 | RO | reserve
| 02D0 | 720 | RO | reserve
| 02D1 | 721 | RO | reserve
| 02D2 | 722 | RO | reserve
| 02D3 | 723 | RO | reserve
| 02D4 | 724 | RO | reserve
| 02D5 | 725 | RO | reserve
| 02D6 | 726 | RO | reserve
| 02D7 | 727 | RO | reserve
| 02D8 | 728 | RO | reserve
| 02D9 | 729 | RO | reserve
| 02DA | 730 | RO | reserve
| 02DB | 731 | RO | reserve
| 02DC | 732 | RO | reserve
| 02DD | 733 | RO | reserve
| 02DE | 734 | RO | reserve
| 02DF | 735 | RO | reserve
| 02E0 | 736 | RO | reserve
| 02E1 | 737 | RO | reserve
| 02E2 | 738 | RO | reserve
| 02E3 | 739 | RO | reserve
| 02E4 | 740 | RO | reserve
| 02E5 | 741 | RO | reserve
| 02E6 | 742 | RO | reserve
| 02E7 | 743 | RO | reserve
| 02E8 | 744 | RO | reserve
| 02E9 | 745 | RO | reserve
| 02EA | 746 | RO | reserve
| 02EB | 747 | RO | reserve
| 02EC | 748 | RO | reserve
| 02ED | 749 | RO | reserve
| 02EE | 750 | RO | reserve
| 02EF | 751 | RO | reserve
| 02F0 | 752 | RO | reserve
| 02F1 | 753 | RO | reserve
| 02F2 | 754 | RO | reserve
| 02F3 | 755 | RO | reserve
| 02F4 | 756 | RO | reserve
| 02F5 | 757 | RO | reserve
| 02F6 | 758 | RO | reserve
| 02F7 | 759 | RO | reserve
| 02F8 | 760 | RO | reserve
| 02F9 | 761 | RO | reserve
| 02FA | 762 | RO | reserve
| 02FB | 763 | RO | reserve
| 02FC | 764 | RO | reserve
| 02FD | 765 | RO | reserve
| 02FE | 766 | RO | reserve
| 02FF | 767 | RO | reserve
| 0300 | 768 | RO | reserve
| 0301 | 769 | RO | reserve
| 0302 | 770 | RO | reserve
| 0303 | 771 | RO | reserve
| 0304 | 772 | RO | reserve
| 0305 | 773 | RO | reserve
| 0306 | 774 | RO | reserve
| 0307 | 775 | RO | reserve
| 0308 | 776 | RO | reserve
| 0309 | 777 | RO | reserve
| 030A | 778 | RO | reserve
| 030B | 779 | RO | reserve
| 030C | 780 | RO | reserve
| 030D | 781 | RO | reserve
| 030E | 782 | RO | reserve
| 030F | 783 | RO | reserve
| 0310 | 784 | RO | reserve
| 0311 | 785 | RO | reserve
| 0312 | 786 | RO | reserve
| 0313 | 787 | RO | reserve
| 0314 | 788 | RO | reserve
| 0315 | 789 | RO | reserve
| 0316 | 790 | RO | reserve
| 0317 | 791 | RO | reserve
| 0318 | 792 | RO | reserve
| 0319 | 793 | RO | reserve
| 031A | 794 | RO | reserve
| 031B | 795 | RO | reserve
| 031C | 796 | RO | reserve
| 031D | 797 | RO | reserve
| 031E | 798 | RO | reserve
| 031F | 799 | RO | reserve
| 0320 | 800 | RO | reserve
| 0321 | 801 | RO | 1# cell discharge balance state | 0--no balance，1--balance
| 0322 | 802 | RO | 2# cell discharge balance state | 0--no balance，1--balance
| 0323 | 803 | RO | 3# cell discharge balance state | 0--no balance，1--balance
| 0324 | 804 | RO | 4# cell discharge balance state | 0--no balance，1--balance
| 0325 | 805 | RO | 5# cell discharge balance state | 0--no balance，1--balance
| 0326 | 806 | RO | 6# cell discharge balance state | 0--no balance，1--balance
| 0327 | 807 | RO | 7# cell discharge balance state | 0--no balance，1--balance
| 0328 | 808 | RO | 8# cell discharge balance state | 0--no balance，1--balance
| 0329 | 809 | RO | 9# cell discharge balance state | 0--no balance，1--balance
| 032A | 810 | RO | 10# cell discharge balance state | 0--no balance，1--balance
| 032B | 811 | RO | 11# cell discharge balance state | 0--no balance，1--balance
| 032C | 812 | RO | 12# cell discharge balance state | 0--no balance，1--balance
| 032D | 813 | RO | 13# cell discharge balance state | 0--no balance，1--balance
| 032E | 814 | RO | 14# cell discharge balance state | 0--no balance，1--balance
| 032F | 815 | RO | 15# cell discharge balance state | 0--no balance，1--balance
| 0330 | 816 | RO | 16# cell discharge balance state | 0--no balance，1--balance
| 0331 | 817 | RO | 17# cell discharge balance state | 0--no balance，1--balance
| 0332 | 818 | RO | 18# cell discharge balance state | 0--no balance，1--balance
| 0333 | 819 | RO | 19# cell discharge balance state | 0--no balance，1--balance
| 0334 | 820 | RO | 20# cell discharge balance state | 0--no balance，1--balance
| 0335 | 821 | RO | 21# cell discharge balance state | 0--no balance，1--balance
| 0336 | 822 | RO | 22# cell discharge balance state | 0--no balance，1--balance
| 0337 | 823 | RO | 23# cell discharge balance state | 0--no balance，1--balance
| 0338 | 824 | RO | 24# cell discharge balance state | 0--no balance，1--balance
| 0339 | 825 | RO | 25# cell discharge balance state | 0--no balance，1--balance
| 033A | 826 | RO | 26# cell discharge balance state | 0--no balance，1--balance
| 033B | 827 | RO | 27# cell discharge balance state | 0--no balance，1--balance
| 033C | 828 | RO | 28# cell discharge balance state | 0--no balance，1--balance
| 033D | 829 | RO | 29# cell discharge balance state | 0--no balance，1--balance
| 033E | 830 | RO | 30# cell discharge balance state | 0--no balance，1--balance
| 033F | 831 | RO | 31# cell discharge balance state | 0--no balance，1--balance
| 0340 | 832 | RO | 32# cell discharge balance state | 0--no balance，1--balance
| 0341 | 833 | RO | 33# cell discharge balance state | 0--no balance，1--balance
| 0342 | 834 | RO | 34# cell discharge balance state | 0--no balance，1--balance
| 0343 | 835 | RO | 35# cell discharge balance state | 0--no balance，1--balance
| 0344 | 836 | RO | 36# cell discharge balance state | 0--no balance，1--balance
| 0345 | 837 | RO | 37# cell discharge balance state | 0--no balance，1--balance
| 0346 | 838 | RO | 38# cell discharge balance state | 0--no balance，1--balance
| 0347 | 839 | RO | 39# cell discharge balance state | 0--no balance，1--balance
| 0348 | 840 | RO | 40# cell discharge balance state | 0--no balance，1--balance
| 0349 | 841 | RO | 41# cell discharge balance state | 0--no balance，1--balance
| 034A | 842 | RO | 42# cell discharge balance state | 0--no balance，1--balance
| 034B | 843 | RO | 43# cell discharge balance state | 0--no balance，1--balance
| 034C | 844 | RO | 44# cell discharge balance state | 0--no balance，1--balance
| 034D | 845 | RO | 45# cell discharge balance state | 0--no balance，1--balance
| 034E | 846 | RO | 46# cell discharge balance state | 0--no balance，1--balance
| 034F | 847 | RO | 47# cell discharge balance state | 0--no balance，1--balance
| 0350 | 848 | RO | 48# cell discharge balance state | 0--no balance，1--balance
| 0351 | 849 | RO | 49# cell discharge balance state | 0--no balance，1--balance
| 0352 | 850 | RO | 50# cell discharge balance state | 0--no balance，1--balance
| 0353 | 851 | RO | 51# cell discharge balance state | 0--no balance，1--balance
| 0354 | 852 | RO | 52# cell discharge balance state | 0--no balance，1--balance
| 0355 | 853 | RO | 53# cell discharge balance state | 0--no balance，1--balance
| 0356 | 854 | RO | 54# cell discharge balance state | 0--no balance，1--balance
| 0357 | 855 | RO | 55# cell discharge balance state | 0--no balance，1--balance
| 0358 | 856 | RO | 56# cell discharge balance state | 0--no balance，1--balance
| 0359 | 857 | RO | 57# cell discharge balance state | 0--no balance，1--balance
| 035A | 858 | RO | 58# cell discharge balance state | 0--no balance，1--balance
| 035B | 859 | RO | 59# cell discharge balance state | 0--no balance，1--balance
| 035C | 860 | RO | 60# cell discharge balance state | 0--no balance，1--balance
| 035D | 861 | RO | 61# cell discharge balance state | 0--no balance，1--balance
| 035E | 862 | RO | 62# cell discharge balance state | 0--no balance，1--balance
| 035F | 863 | RO | 63# cell discharge balance state | 0--no balance，1--balance
| 0360 | 864 | RO | 64# cell discharge balance state | 0--no balance，1--balance
| 0361 | 865 | RO | 65# cell discharge balance state | 0--no balance，1--balance
| 0362 | 866 | RO | 66# cell discharge balance state | 0--no balance，1--balance
| 0363 | 867 | RO | 67# cell discharge balance state | 0--no balance，1--balance
| 0364 | 868 | RO | 68# cell discharge balance state | 0--no balance，1--balance
| 0365 | 869 | RO | 69# cell discharge balance state | 0--no balance，1--balance
| 0366 | 870 | RO | 70# cell discharge balance state | 0--no balance，1--balance
| 0367 | 871 | RO | 71# cell discharge balance state | 0--no balance，1--balance
| 0368 | 872 | RO | 72# cell discharge balance state | 0--no balance，1--balance
| 0369 | 873 | RO | 73# cell discharge balance state | 0--no balance，1--balance
| 036A | 874 | RO | 74# cell discharge balance state | 0--no balance，1--balance
| 036B | 875 | RO | 75# cell discharge balance state | 0--no balance，1--balance
| 036C | 876 | RO | 76# cell discharge balance state | 0--no balance，1--balance
| 036D | 877 | RO | 77# cell discharge balance state | 0--no balance，1--balance
| 036E | 878 | RO | 78# cell discharge balance state | 0--no balance，1--balance
| 036F | 879 | RO | 79# cell discharge balance state | 0--no balance，1--balance
| 0370 | 880 | RO | 80# cell discharge balance state | 0--no balance，1--balance
| 0371 | 881 | RO | 81# cell discharge balance state | 0--no balance，1--balance
| 0372 | 882 | RO | 82# cell discharge balance state | 0--no balance，1--balance
| 0373 | 883 | RO | 83# cell discharge balance state | 0--no balance，1--balance
| 0374 | 884 | RO | 84# cell discharge balance state | 0--no balance，1--balance
| 0375 | 885 | RO | 85# cell discharge balance state | 0--no balance，1--balance
| 0376 | 886 | RO | 86# cell discharge balance state | 0--no balance，1--balance
| 0377 | 887 | RO | 87# cell discharge balance state | 0--no balance，1--balance
| 0378 | 888 | RO | 88# cell discharge balance state | 0--no balance，1--balance
| 0379 | 889 | RO | 89# cell discharge balance state | 0--no balance，1--balance
| 037A | 890 | RO | 90# cell discharge balance state | 0--no balance，1--balance
| 037B | 891 | RO | 91# cell discharge balance state | 0--no balance，1--balance
| 037C | 892 | RO | 92# cell discharge balance state | 0--no balance，1--balance
| 037D | 893 | RO | 93# cell discharge balance state | 0--no balance，1--balance
| 037E | 894 | RO | 94# cell discharge balance state | 0--no balance，1--balance
| 037F | 895 | RO | 95# cell discharge balance state | 0--no balance，1--balance
| 0380 | 896 | RO | 96# cell discharge balance state | 0--no balance，1--balance
| 0381 | 897 | RO | 97# cell discharge balance state | 0--no balance，1--balance
| 0382 | 898 | RO | 98# cell discharge balance state | 0--no balance，1--balance
| 0383 | 899 | RO | 99# cell discharge balance state | 0--no balance，1--balance
| 0384 | 900 | RO | 100# cell discharge balance state | 0--no balance，1--balance
| 0385 | 901 | RO | 101# cell discharge balance state | 0--no balance，1--balance
| 0386 | 902 | RO | 102# cell discharge balance state | 0--no balance，1--balance
| 0387 | 903 | RO | 103# cell discharge balance state | 0--no balance，1--balance
| 0388 | 904 | RO | 104# cell discharge balance state | 0--no balance，1--balance
| 0389 | 905 | RO | 105# cell discharge balance state | 0--no balance，1--balance
| 038A | 906 | RO | 106# cell discharge balance state | 0--no balance，1--balance
| 038B | 907 | RO | 107# cell discharge balance state | 0--no balance，1--balance
| 038C | 908 | RO | 108# cell discharge balance state | 0--no balance，1--balance
| 038D | 909 | RO | 109# cell discharge balance state | 0--no balance，1--balance
| 038E | 910 | RO | 110# cell discharge balance state | 0--no balance，1--balance
| 038F | 911 | RO | 111# cell discharge balance state | 0--no balance，1--balance
| 0390 | 912 | RO | 112# cell discharge balance state | 0--no balance，1--balance
| 0391 | 913 | RO | 113# cell discharge balance state | 0--no balance，1--balance
| 0392 | 914 | RO | 114# cell discharge balance state | 0--no balance，1--balance
| 0393 | 915 | RO | 115# cell discharge balance state | 0--no balance，1--balance
| 0394 | 916 | RO | 116# cell discharge balance state | 0--no balance，1--balance
| 0395 | 917 | RO | 117# cell discharge balance state | 0--no balance，1--balance
| 0396 | 918 | RO | 118# cell discharge balance state | 0--no balance，1--balance
| 0397 | 919 | RO | 119# cell discharge balance state | 0--no balance，1--balance
| 0398 | 920 | RO | 120# cell discharge balance state | 0--no balance，1--balance
| 0399 | 921 | RO | 121# cell discharge balance state | 0--no balance，1--balance
| 039A | 922 | RO | 122# cell discharge balance state | 0--no balance，1--balance
| 039B | 923 | RO | 123# cell discharge balance state | 0--no balance，1--balance
| 039C | 924 | RO | 124# cell discharge balance state | 0--no balance，1--balance
| 039D | 925 | RO | 125# cell discharge balance state | 0--no balance，1--balance
| 039E | 926 | RO | 126# cell discharge balance state | 0--no balance，1--balance
| 039F | 927 | RO | 127# cell discharge balance state | 0--no balance，1--balance
| 03A0 | 928 | RO | 128# cell discharge balance state | 0--no balance，1--balance
| 03A1 | 929 | RO | 129# cell discharge balance state | 0--no balance，1--balance
| 03A2 | 930 | RO | 130# cell discharge balance state | 0--no balance，1--balance
| 03A3 | 931 | RO | 131# cell discharge balance state | 0--no balance，1--balance
| 03A4 | 932 | RO | 132# cell discharge balance state | 0--no balance，1--balance
| 03A5 | 933 | RO | 133# cell discharge balance state | 0--no balance，1--balance
| 03A6 | 934 | RO | 134# cell discharge balance state | 0--no balance，1--balance
| 03A7 | 935 | RO | 135# cell discharge balance state | 0--no balance，1--balance
| 03A8 | 936 | RO | 136# cell discharge balance state | 0--no balance，1--balance
| 03A9 | 937 | RO | 137# cell discharge balance state | 0--no balance，1--balance
| 03AA | 938 | RO | 138# cell discharge balance state | 0--no balance，1--balance
| 03AB | 939 | RO | 139# cell discharge balance state | 0--no balance，1--balance
| 03AC | 940 | RO | 140# cell discharge balance state | 0--no balance，1--balance
| 03AD | 941 | RO | 141# cell discharge balance state | 0--no balance，1--balance
| 03AE | 942 | RO | 142# cell discharge balance state | 0--no balance，1--balance
| 03AF | 943 | RO | 143# cell discharge balance state | 0--no balance，1--balance
| 03B0 | 944 | RO | 144# cell discharge balance state | 0--no balance，1--balance
| 03B1 | 945 | RO | 145# cell discharge balance state | 0--no balance，1--balance
| 03B2 | 946 | RO | 146# cell discharge balance state | 0--no balance，1--balance
| 03B3 | 947 | RO | 147# cell discharge balance state | 0--no balance，1--balance
| 03B4 | 948 | RO | 148# cell discharge balance state | 0--no balance，1--balance
| 03B5 | 949 | RO | 149# cell discharge balance state | 0--no balance，1--balance
| 03B6 | 950 | RO | 150# cell discharge balance state | 0--no balance，1--balance
| 03B7 | 951 | RO | 151# cell discharge balance state | 0--no balance，1--balance
| 03B8 | 952 | RO | 152# cell discharge balance state | 0--no balance，1--balance
| 03B9 | 953 | RO | 153# cell discharge balance state | 0--no balance，1--balance
| 03BA | 954 | RO | 154# cell discharge balance state | 0--no balance，1--balance
| 03BB | 955 | RO | 155# cell discharge balance state | 0--no balance，1--balance
| 03BC | 956 | RO | 156# cell discharge balance state | 0--no balance，1--balance
| 03BD | 957 | RO | 157# cell discharge balance state | 0--no balance，1--balance
| 03BE | 958 | RO | 158# cell discharge balance state | 0--no balance，1--balance
| 03BF | 959 | RO | 159# cell discharge balance state | 0--no balance，1--balance
| 03C0 | 960 | RO | 160# cell discharge balance state | 0--no balance，1--balance
| 03C1 | 961 | RO | 161# cell discharge balance state | 0--no balance，1--balance
| 03C2 | 962 | RO | 162# cell discharge balance state | 0--no balance，1--balance
| 03C3 | 963 | RO | 163# cell discharge balance state | 0--no balance，1--balance
| 03C4 | 964 | RO | 164# cell discharge balance state | 0--no balance，1--balance
| 03C5 | 965 | RO | 165# cell discharge balance state | 0--no balance，1--balance
| 03C6 | 966 | RO | 166# cell discharge balance state | 0--no balance，1--balance
| 03C7 | 967 | RO | 167# cell discharge balance state | 0--no balance，1--balance
| 03C8 | 968 | RO | 168# cell discharge balance state | 0--no balance，1--balance
| 03C9 | 969 | RO | 169# cell discharge balance state | 0--no balance，1--balance
| 03CA | 970 | RO | 170# cell discharge balance state | 0--no balance，1--balance
| 03CB | 971 | RO | 171# cell discharge balance state | 0--no balance，1--balance
| 03CC | 972 | RO | 172# cell discharge balance state | 0--no balance，1--balance
| 03CD | 973 | RO | 173# cell discharge balance state | 0--no balance，1--balance
| 03CE | 974 | RO | 174# cell discharge balance state | 0--no balance，1--balance
| 03CF | 975 | RO | 175# cell discharge balance state | 0--no balance，1--balance
| 03D0 | 976 | RO | 176# cell discharge balance state | 0--no balance，1--balance
| 03D1 | 977 | RO | 177# cell discharge balance state | 0--no balance，1--balance
| 03D2 | 978 | RO | 178# cell discharge balance state | 0--no balance，1--balance
| 03D3 | 979 | RO | 179# cell discharge balance state | 0--no balance，1--balance
| 03D4 | 980 | RO | 180# cell discharge balance state | 0--no balance，1--balance
| 03D5 | 981 | RO | 181# cell discharge balance state | 0--no balance，1--balance
| 03D6 | 982 | RO | 182# cell discharge balance state | 0--no balance，1--balance
| 03D7 | 983 | RO | 183# cell discharge balance state | 0--no balance，1--balance
| 03D8 | 984 | RO | 184# cell discharge balance state | 0--no balance，1--balance
| 03D9 | 985 | RO | 185# cell discharge balance state | 0--no balance，1--balance
| 03DA | 986 | RO | 186# cell discharge balance state | 0--no balance，1--balance
| 03DB | 987 | RO | 187# cell discharge balance state | 0--no balance，1--balance
| 03DC | 988 | RO | 188# cell discharge balance state | 0--no balance，1--balance
| 03DD | 989 | RO | 189# cell discharge balance state | 0--no balance，1--balance
| 03DE | 990 | RO | 190# cell discharge balance state | 0--no balance，1--balance
| 03DF | 991 | RO | 191# cell discharge balance state | 0--no balance，1--balance
| 03E0 | 992 | RO | 192# cell discharge balance state | 0--no balance，1--balance
| 03E1 | 993 | RO | 193# cell discharge balance state | 0--no balance，1--balance
| 03E2 | 994 | RO | 194# cell discharge balance state | 0--no balance，1--balance
| 03E3 | 995 | RO | 195# cell discharge balance state | 0--no balance，1--balance
| 03E4 | 996 | RO | 196# cell discharge balance state | 0--no balance，1--balance
| 03E5 | 997 | RO | 197# cell discharge balance state | 0--no balance，1--balance
| 03E6 | 998 | RO | 198# cell discharge balance state | 0--no balance，1--balance
| 03E7 | 999 | RO | 199# cell discharge balance state | 0--no balance，1--balance
| 03E8 | 1000 | RO | 200# cell discharge balance state | 0--no balance，1--balance
| 03E9 | 1001 | RO | 201# cell discharge balance state | 0--no balance，1--balance
| 03EA | 1002 | RO | 202# cell discharge balance state | 0--no balance，1--balance
| 03EB | 1003 | RO | 203# cell discharge balance state | 0--no balance，1--balance
| 03EC | 1004 | RO | 204# cell discharge balance state | 0--no balance，1--balance
| 03ED | 1005 | RO | 205# cell discharge balance state | 0--no balance，1--balance
| 03EE | 1006 | RO | 206# cell discharge balance state | 0--no balance，1--balance
| 03EF | 1007 | RO | 207# cell discharge balance state | 0--no balance，1--balance
| 03F0 | 1008 | RO | 208# cell discharge balance state | 0--no balance，1--balance
| 03F1 | 1009 | RO | 209# cell discharge balance state | 0--no balance，1--balance
| 03F2 | 1010 | RO | 210# cell discharge balance state | 0--no balance，1--balance
| 03F3 | 1011 | RO | 211# cell discharge balance state | 0--no balance，1--balance
| 03F4 | 1012 | RO | 212# cell discharge balance state | 0--no balance，1--balance
| 03F5 | 1013 | RO | 213# cell discharge balance state | 0--no balance，1--balance
| 03F6 | 1014 | RO | 214# cell discharge balance state | 0--no balance，1--balance
| 03F7 | 1015 | RO | 215# cell discharge balance state | 0--no balance，1--balance
| 03F8 | 1016 | RO | 216# cell discharge balance state | 0--no balance，1--balance
| 03F9 | 1017 | RO | 217# cell discharge balance state | 0--no balance，1--balance
| 03FA | 1018 | RO | 218# cell discharge balance state | 0--no balance，1--balance
| 03FB | 1019 | RO | 219# cell discharge balance state | 0--no balance，1--balance
| 03FC | 1020 | RO | 220# cell discharge balance state | 0--no balance，1--balance
| 03FD | 1021 | RO | 221# cell discharge balance state | 0--no balance，1--balance
| 03FE | 1022 | RO | 222# cell discharge balance state | 0--no balance，1--balance
| 03FF | 1023 | RO | 223# cell discharge balance state | 0--no balance，1--balance
| 0400 | 1024 | RO | 224# cell discharge balance state | 0--no balance，1--balance
| 0401 | 1025 | RO | 225# cell discharge balance state | 0--no balance，1--balance
| 0402 | 1026 | RO | 226# cell discharge balance state | 0--no balance，1--balance
| 0403 | 1027 | RO | 227# cell discharge balance state | 0--no balance，1--balance
| 0404 | 1028 | RO | 228# cell discharge balance state | 0--no balance，1--balance
| 0405 | 1029 | RO | 229# cell discharge balance state | 0--no balance，1--balance
| 0406 | 1030 | RO | 230# cell discharge balance state | 0--no balance，1--balance
| 0407 | 1031 | RO | 231# cell discharge balance state | 0--no balance，1--balance
| 0408 | 1032 | RO | 232# cell discharge balance state | 0--no balance，1--balance
| 0409 | 1033 | RO | 233# cell discharge balance state | 0--no balance，1--balance
| 040A | 1034 | RO | 234# cell discharge balance state | 0--no balance，1--balance
| 040B | 1035 | RO | 235# cell discharge balance state | 0--no balance，1--balance
| 040C | 1036 | RO | 236# cell discharge balance state | 0--no balance，1--balance
| 040D | 1037 | RO | 237# cell discharge balance state | 0--no balance，1--balance
| 040E | 1038 | RO | 238# cell discharge balance state | 0--no balance，1--balance
| 040F | 1039 | RO | 239# cell discharge balance state | 0--no balance，1--balance
| 0410 | 1040 | RO | 240# cell discharge balance state | 0--no balance，1--balance
| 0411 | 1041 | RO | 241# cell discharge balance state | 0--no balance，1--balance
| 0412 | 1042 | RO | 242# cell discharge balance state | 0--no balance，1--balance
| 0413 | 1043 | RO | 243# cell discharge balance state | 0--no balance，1--balance
| 0414 | 1044 | RO | 244# cell discharge balance state | 0--no balance，1--balance
| 0415 | 1045 | RO | 245# cell discharge balance state | 0--no balance，1--balance
| 0416 | 1046 | RO | 246# cell discharge balance state | 0--no balance，1--balance
| 0417 | 1047 | RO | 247# cell discharge balance state | 0--no balance，1--balance
| 0418 | 1048 | RO | 248# cell discharge balance state | 0--no balance，1--balance
| 0419 | 1049 | RO | 249# cell discharge balance state | 0--no balance，1--balance
| 041A | 1050 | RO | 250# cell discharge balance state | 0--no balance，1--balance
| 041B | 1051 | RO | 251# cell discharge balance state | 0--no balance，1--balance
| 041C | 1052 | RO | 252# cell discharge balance state | 0--no balance，1--balance
| 041D | 1053 | RO | 253# cell discharge balance state | 0--no balance，1--balance
| 041E | 1054 | RO | 254# cell discharge balance state | 0--no balance，1--balance
| 041F | 1055 | RO | 255# cell discharge balance state | 0--no balance，1--balance
| 0420 | 1056 | RO | 256# cell discharge balance state | 0--no balance，1--balance
| 0421 | 1057 | RO | 257# cell discharge balance state | 0--no balance，1--balance
| 0422 | 1058 | RO | 258# cell discharge balance state | 0--no balance，1--balance
| 0423 | 1059 | RO | 259# cell discharge balance state | 0--no balance，1--balance
| 0424 | 1060 | RO | 260# cell discharge balance state | 0--no balance，1--balance
| 0425 | 1061 | RO | 261# cell discharge balance state | 0--no balance，1--balance
| 0426 | 1062 | RO | 262# cell discharge balance state | 0--no balance，1--balance
| 0427 | 1063 | RO | 263# cell discharge balance state | 0--no balance，1--balance
| 0428 | 1064 | RO | 264# cell discharge balance state | 0--no balance，1--balance
| 0429 | 1065 | RO | 265# cell discharge balance state | 0--no balance，1--balance
| 042A | 1066 | RO | 266# cell discharge balance state | 0--no balance，1--balance
| 042B | 1067 | RO | 267# cell discharge balance state | 0--no balance，1--balance
| 042C | 1068 | RO | 268# cell discharge balance state | 0--no balance，1--balance
| 042D | 1069 | RO | 269# cell discharge balance state | 0--no balance，1--balance
| 042E | 1070 | RO | 270# cell discharge balance state | 0--no balance，1--balance
| 042F | 1071 | RO | 271# cell discharge balance state | 0--no balance，1--balance
| 0430 | 1072 | RO | 272# cell discharge balance state | 0--no balance，1--balance
| 0431 | 1073 | RO | 273# cell discharge balance state | 0--no balance，1--balance
| 0432 | 1074 | RO | 274# cell discharge balance state | 0--no balance，1--balance
| 0433 | 1075 | RO | 275# cell discharge balance state | 0--no balance，1--balance
| 0434 | 1076 | RO | 276# cell discharge balance state | 0--no balance，1--balance
| 0435 | 1077 | RO | 277# cell discharge balance state | 0--no balance，1--balance
| 0436 | 1078 | RO | 278# cell discharge balance state | 0--no balance，1--balance
| 0437 | 1079 | RO | 279# cell discharge balance state | 0--no balance，1--balance
| 0438 | 1080 | RO | 280# cell discharge balance state | 0--no balance，1--balance
| 0439 | 1081 | RO | 281# cell discharge balance state | 0--no balance，1--balance
| 043A | 1082 | RO | 282# cell discharge balance state | 0--no balance，1--balance
| 043B | 1083 | RO | 283# cell discharge balance state | 0--no balance，1--balance
| 043C | 1084 | RO | 284# cell discharge balance state | 0--no balance，1--balance
| 043D | 1085 | RO | 285# cell discharge balance state | 0--no balance，1--balance
| 043E | 1086 | RO | 286# cell discharge balance state | 0--no balance，1--balance
| 043F | 1087 | RO | 287# cell discharge balance state | 0--no balance，1--balance
| 0440 | 1088 | RO | 288# cell discharge balance state | 0--no balance，1--balance
| 0441 | 1089 | RO | 289# cell discharge balance state | 0--no balance，1--balance
| 0442 | 1090 | RO | 290# cell discharge balance state | 0--no balance，1--balance
| 0443 | 1091 | RO | 291# cell discharge balance state | 0--no balance，1--balance
| 0444 | 1092 | RO | 292# cell discharge balance state | 0--no balance，1--balance
| 0445 | 1093 | RO | 293# cell discharge balance state | 0--no balance，1--balance
| 0446 | 1094 | RO | 294# cell discharge balance state | 0--no balance，1--balance
| 0447 | 1095 | RO | 295# cell discharge balance state | 0--no balance，1--balance
| 0448 | 1096 | RO | 296# cell discharge balance state | 0--no balance，1--balance
| 0449 | 1097 | RO | 297# cell discharge balance state | 0--no balance，1--balance
| 044A | 1098 | RO | 298# cell discharge balance state | 0--no balance，1--balance
| 044B | 1099 | RO | 299# cell discharge balance state | 0--no balance，1--balance
| 044C | 1100 | RO | 300# cell discharge balance state | 0--no balance，1--balance
| 044D | 1101 | RO | 301# cell discharge balance state | 0--no balance，1--balance
| 044E | 1102 | RO | 302# cell discharge balance state | 0--no balance，1--balance
| 044F | 1103 | RO | 303# cell discharge balance state | 0--no balance，1--balance
| 0450 | 1104 | RO | 304# cell discharge balance state | 0--no balance，1--balance
| 0451 | 1105 | RO | 305# cell discharge balance state | 0--no balance，1--balance
| 0452 | 1106 | RO | 306# cell discharge balance state | 0--no balance，1--balance
| 0453 | 1107 | RO | 307# cell discharge balance state | 0--no balance，1--balance
| 0454 | 1108 | RO | 308# cell discharge balance state | 0--no balance，1--balance
| 0455 | 1109 | RO | 309# cell discharge balance state | 0--no balance，1--balance
| 0456 | 1110 | RO | 310# cell discharge balance state | 0--no balance，1--balance
| 0457 | 1111 | RO | 311# cell discharge balance state | 0--no balance，1--balance
| 0458 | 1112 | RO | 312# cell discharge balance state | 0--no balance，1--balance
| 0459 | 1113 | RO | 313# cell discharge balance state | 0--no balance，1--balance
| 045A | 1114 | RO | 314# cell discharge balance state | 0--no balance，1--balance
| 045B | 1115 | RO | 315# cell discharge balance state | 0--no balance，1--balance
| 045C | 1116 | RO | 316# cell discharge balance state | 0--no balance，1--balance
| 045D | 1117 | RO | 317# cell discharge balance state | 0--no balance，1--balance
| 045E | 1118 | RO | 318# cell discharge balance state | 0--no balance，1--balance
| 045F | 1119 | RO | 319# cell discharge balance state | 0--no balance，1--balance
| 0460 | 1120 | RO | 320# cell discharge balance state | 0--no balance，1--balance
| 0461 | 1121 | RO | 321# cell discharge balance state | 0--no balance，1--balance
| 0462 | 1122 | RO | 322# cell discharge balance state | 0--no balance，1--balance
| 0463 | 1123 | RO | 323# cell discharge balance state | 0--no balance，1--balance
| 0464 | 1124 | RO | 324# cell discharge balance state | 0--no balance，1--balance
| 0465 | 1125 | RO | 325# cell discharge balance state | 0--no balance，1--balance
| 0466 | 1126 | RO | 326# cell discharge balance state | 0--no balance，1--balance
| 0467 | 1127 | RO | 327# cell discharge balance state | 0--no balance，1--balance
| 0468 | 1128 | RO | 328# cell discharge balance state | 0--no balance，1--balance
| 0469 | 1129 | RO | 329# cell discharge balance state | 0--no balance，1--balance
| 046A | 1130 | RO | 330# cell discharge balance state | 0--no balance，1--balance
| 046B | 1131 | RO | 331# cell discharge balance state | 0--no balance，1--balance
| 046C | 1132 | RO | 332# cell discharge balance state | 0--no balance，1--balance
| 046D | 1133 | RO | 333# cell discharge balance state | 0--no balance，1--balance
| 046E | 1134 | RO | 334# cell discharge balance state | 0--no balance，1--balance
| 046F | 1135 | RO | 335# cell discharge balance state | 0--no balance，1--balance
| 0470 | 1136 | RO | 336# cell discharge balance state | 0--no balance，1--balance
| 0471 | 1137 | RO | 337# cell discharge balance state | 0--no balance，1--balance
| 0472 | 1138 | RO | 338# cell discharge balance state | 0--no balance，1--balance
| 0473 | 1139 | RO | 339# cell discharge balance state | 0--no balance，1--balance
| 0474 | 1140 | RO | 340# cell discharge balance state | 0--no balance，1--balance
| 0475 | 1141 | RO | 341# cell discharge balance state | 0--no balance，1--balance
| 0476 | 1142 | RO | 342# cell discharge balance state | 0--no balance，1--balance
| 0477 | 1143 | RO | 343# cell discharge balance state | 0--no balance，1--balance
| 0478 | 1144 | RO | 344# cell discharge balance state | 0--no balance，1--balance
| 0479 | 1145 | RO | 345# cell discharge balance state | 0--no balance，1--balance
| 047A | 1146 | RO | 346# cell discharge balance state | 0--no balance，1--balance
| 047B | 1147 | RO | 347# cell discharge balance state | 0--no balance，1--balance
| 047C | 1148 | RO | 348# cell discharge balance state | 0--no balance，1--balance
| 047D | 1149 | RO | 349# cell discharge balance state | 0--no balance，1--balance
| 047E | 1150 | RO | 350# cell discharge balance state | 0--no balance，1--balance
| 047F | 1151 | RO | 351# cell discharge balance state | 0--no balance，1--balance
| 0480 | 1152 | RO | 352# cell discharge balance state | 0--no balance，1--balance
| 0481 | 1153 | RO | 353# cell discharge balance state | 0--no balance，1--balance
| 0482 | 1154 | RO | 354# cell discharge balance state | 0--no balance，1--balance
| 0483 | 1155 | RO | 355# cell discharge balance state | 0--no balance，1--balance
| 0484 | 1156 | RO | 356# cell discharge balance state | 0--no balance，1--balance
| 0485 | 1157 | RO | 357# cell discharge balance state | 0--no balance，1--balance
| 0486 | 1158 | RO | 358# cell discharge balance state | 0--no balance，1--balance
| 0487 | 1159 | RO | 359# cell discharge balance state | 0--no balance，1--balance
| 0488 | 1160 | RO | 360# cell discharge balance state | 0--no balance，1--balance
| 0489 | 1161 | RO | 361# cell discharge balance state | 0--no balance，1--balance
| 048A | 1162 | RO | 362# cell discharge balance state | 0--no balance，1--balance
| 048B | 1163 | RO | 363# cell discharge balance state | 0--no balance，1--balance
| 048C | 1164 | RO | 364# cell discharge balance state | 0--no balance，1--balance
| 048D | 1165 | RO | 365# cell discharge balance state | 0--no balance，1--balance
| 048E | 1166 | RO | 366# cell discharge balance state | 0--no balance，1--balance
| 048F | 1167 | RO | 367# cell discharge balance state | 0--no balance，1--balance
| 0490 | 1168 | RO | 368# cell discharge balance state | 0--no balance，1--balance
| 0491 | 1169 | RO | 369# cell discharge balance state | 0--no balance，1--balance
| 0492 | 1170 | RO | 370# cell discharge balance state | 0--no balance，1--balance
| 0493 | 1171 | RO | 371# cell discharge balance state | 0--no balance，1--balance
| 0494 | 1172 | RO | 372# cell discharge balance state | 0--no balance，1--balance
| 0495 | 1173 | RO | 373# cell discharge balance state | 0--no balance，1--balance
| 0496 | 1174 | RO | 374# cell discharge balance state | 0--no balance，1--balance
| 0497 | 1175 | RO | 375# cell discharge balance state | 0--no balance，1--balance
| 0498 | 1176 | RO | 376# cell discharge balance state | 0--no balance，1--balance
| 0499 | 1177 | RO | 377# cell discharge balance state | 0--no balance，1--balance
| 049A | 1178 | RO | 378# cell discharge balance state | 0--no balance，1--balance
| 049B | 1179 | RO | 379# cell discharge balance state | 0--no balance，1--balance
| 049C | 1180 | RO | 380# cell discharge balance state | 0--no balance，1--balance
| 049D | 1181 | RO | 381# cell discharge balance state | 0--no balance，1--balance
| 049E | 1182 | RO | 382# cell discharge balance state | 0--no balance，1--balance
| 049F | 1183 | RO | 383# cell discharge balance state | 0--no balance，1--balance
| 04A0 | 1184 | RO | 384# cell discharge balance state | 0--no balance，1--balance
| 04A1 | 1185 | RO | 385# cell discharge balance state | 0--no balance，1--balance
| 04A2 | 1186 | RO | 386# cell discharge balance state | 0--no balance，1--balance
| 04A3 | 1187 | RO | 387# cell discharge balance state | 0--no balance，1--balance
| 04A4 | 1188 | RO | 388# cell discharge balance state | 0--no balance，1--balance
| 04A5 | 1189 | RO | 389# cell discharge balance state | 0--no balance，1--balance
| 04A6 | 1190 | RO | 390# cell discharge balance state | 0--no balance，1--balance
| 04A7 | 1191 | RO | 391# cell discharge balance state | 0--no balance，1--balance
| 04A8 | 1192 | RO | 392# cell discharge balance state | 0--no balance，1--balance
| 04A9 | 1193 | RO | 393# cell discharge balance state | 0--no balance，1--balance
| 04AA | 1194 | RO | 394# cell discharge balance state | 0--no balance，1--balance
| 04AB | 1195 | RO | 395# cell discharge balance state | 0--no balance，1--balance
| 04AC | 1196 | RO | 396# cell discharge balance state | 0--no balance，1--balance
| 04AD | 1197 | RO | 397# cell discharge balance state | 0--no balance，1--balance
| 04AE | 1198 | RO | 398# cell discharge balance state | 0--no balance，1--balance
| 04AF | 1199 | RO | 399# cell discharge balance state | 0--no balance，1--balance
| 04B0 | 1200 | RO | 400# cell discharge balance state | 0--no balance，1--balance
| 04B1 | 1201 | RO | 401# cell discharge balance state | 0--no balance，1--balance
| 04B2 | 1202 | RO | 402# cell discharge balance state | 0--no balance，1--balance
| 04B3 | 1203 | RO | 403# cell discharge balance state | 0--no balance，1--balance
| 04B4 | 1204 | RO | 404# cell discharge balance state | 0--no balance，1--balance
| 04B5 | 1205 | RO | 405# cell discharge balance state | 0--no balance，1--balance
| 04B6 | 1206 | RO | 406# cell discharge balance state | 0--no balance，1--balance
| 04B7 | 1207 | RO | 407# cell discharge balance state | 0--no balance，1--balance
| 04B8 | 1208 | RO | 408# cell discharge balance state | 0--no balance，1--balance
| 04B9 | 1209 | RO | 409# cell discharge balance state | 0--no balance，1--balance
| 04BA | 1210 | RO | 410# cell discharge balance state | 0--no balance，1--balance
| 04BB | 1211 | RO | 411# cell discharge balance state | 0--no balance，1--balance
| 04BC | 1212 | RO | 412# cell discharge balance state | 0--no balance，1--balance
| 04BD | 1213 | RO | 413# cell discharge balance state | 0--no balance，1--balance
| 04BE | 1214 | RO | 414# cell discharge balance state | 0--no balance，1--balance
| 04BF | 1215 | RO | 415# cell discharge balance state | 0--no balance，1--balance
| 04C0 | 1216 | RO | 416# cell discharge balance state | 0--no balance，1--balance
| 04C1 | 1217 | RO | reserve
| 04C2 | 1218 | RO | reserve
| 04C3 | 1219 | RO | reserve
| 04C4 | 1220 | RO | reserve
| 04C5 | 1221 | RO | reserve
| 04C6 | 1222 | RO | reserve
| 04C7 | 1223 | RO | reserve
| 04C8 | 1224 | RO | reserve
| 04C9 | 1225 | RO | reserve
| 04CA | 1226 | RO | reserve
| 04CB | 1227 | RO | reserve
| 04CC | 1228 | RO | reserve
| 04CD | 1229 | RO | reserve
| 04CE | 1230 | RO | reserve
| 04CF | 1231 | RO | reserve
| 04D0 | 1232 | RO | reserve
| 04D1 | 1233 | RO | reserve
| 04D2 | 1234 | RO | reserve
| 04D3 | 1235 | RO | reserve
| 04D4 | 1236 | RO | reserve
| 04D5 | 1237 | RO | reserve
| 04D6 | 1238 | RO | reserve
| 04D7 | 1239 | RO | reserve
| 04D8 | 1240 | RO | reserve
| 04D9 | 1241 | RO | reserve
| 04DA | 1242 | RO | reserve
| 04DB | 1243 | RO | reserve
| 04DC | 1244 | RO | reserve
| 04DD | 1245 | RO | reserve
| 04DE | 1246 | RO | reserve
| 04DF | 1247 | RO | reserve
| 04E0 | 1248 | RO | reserve
| 04E1 | 1249 | RO | reserve
| 04E2 | 1250 | RO | reserve
| 04E3 | 1251 | RO | reserve
| 04E4 | 1252 | RO | reserve
| 04E5 | 1253 | RO | reserve
| 04E6 | 1254 | RO | reserve
| 04E7 | 1255 | RO | reserve
| 04E8 | 1256 | RO | reserve
| 04E9 | 1257 | RO | reserve
| 04EA | 1258 | RO | reserve
| 04EB | 1259 | RO | reserve
| 04EC | 1260 | RO | reserve
| 04ED | 1261 | RO | reserve
| 04EE | 1262 | RO | reserve
| 04EF | 1263 | RO | reserve
| 04F0 | 1264 | RO | reserve
| 04F1 | 1265 | RO | reserve
| 04F2 | 1266 | RO | reserve
| 04F3 | 1267 | RO | reserve
| 04F4 | 1268 | RO | reserve
| 04F5 | 1269 | RO | reserve
| 04F6 | 1270 | RO | reserve
| 04F7 | 1271 | RO | reserve
| 04F8 | 1272 | RO | reserve
| 04F9 | 1273 | RO | reserve
| 04FA | 1274 | RO | reserve
| 04FB | 1275 | RO | reserve
| 04FC | 1276 | RO | reserve
| 04FD | 1277 | RO | reserve
| 04FE | 1278 | RO | reserve
| 04FF | 1279 | RO | reserve
| 0500 | 1280 | RO | reserve
| 0501 | 1281 | RO | reserve
| 0502 | 1282 | RO | reserve
| 0503 | 1283 | RO | reserve
| 0504 | 1284 | RO | reserve
| 0505 | 1285 | RO | reserve
| 0506 | 1286 | RO | reserve
| 0507 | 1287 | RO | reserve
| 0508 | 1288 | RO | reserve
| 0509 | 1289 | RO | reserve
| 050A | 1290 | RO | reserve
| 050B | 1291 | RO | reserve
| 050C | 1292 | RO | reserve
| 050D | 1293 | RO | reserve
| 050E | 1294 | RO | reserve
| 050F | 1295 | RO | reserve
| 0510 | 1296 | RO | reserve
| 0511 | 1297 | RO | reserve
| 0512 | 1298 | RO | reserve
| 0513 | 1299 | RO | reserve
| 0514 | 1300 | RO | reserve
| 0515 | 1301 | RO | reserve
| 0516 | 1302 | RO | reserve
| 0517 | 1303 | RO | reserve
| 0518 | 1304 | RO | reserve
| 0519 | 1305 | RO | reserve
| 051A | 1306 | RO | reserve
| 051B | 1307 | RO | reserve
| 051C | 1308 | RO | reserve
| 051D | 1309 | RO | reserve
| 051E | 1310 | RO | reserve
| 051F | 1311 | RO | reserve
| 0520 | 1312 | RO | reserve
| 0521 | 1313 | RO | reserve
| 0522 | 1314 | RO | reserve
| 0523 | 1315 | RO | reserve
| 0524 | 1316 | RO | reserve
| 0525 | 1317 | RO | reserve
| 0526 | 1318 | RO | reserve
| 0527 | 1319 | RO | reserve
| 0528 | 1320 | RO | reserve
| 0529 | 1321 | RO | reserve
| 052A | 1322 | RO | reserve
| 052B | 1323 | RO | reserve
| 052C | 1324 | RO | reserve
| 052D | 1325 | RO | reserve
| 052E | 1326 | RO | reserve
| 052F | 1327 | RO | reserve
| 0530 | 1328 | RO | reserve
| 0531 | 1329 | RO | reserve
| 0532 | 1330 | RO | reserve
| 0533 | 1331 | RO | reserve
| 0534 | 1332 | RO | reserve
| 0535 | 1333 | RO | reserve
| 0536 | 1334 | RO | reserve
| 0537 | 1335 | RO | reserve
| 0538 | 1336 | RO | reserve
| 0539 | 1337 | RO | reserve
| 053A | 1338 | RO | reserve
| 053B | 1339 | RO | reserve
| 053C | 1340 | RO | reserve
| 053D | 1341 | RO | reserve
| 053E | 1342 | RO | reserve
| 053F | 1343 | RO | reserve
| 0540 | 1344 | RO | reserve
| 0541 | 1345 | RO | reserve
| 0542 | 1346 | RO | reserve
| 0543 | 1347 | RO | reserve
| 0544 | 1348 | RO | reserve
| 0545 | 1349 | RO | reserve
| 0546 | 1350 | RO | reserve
| 0547 | 1351 | RO | reserve
| 0548 | 1352 | RO | reserve
| 0549 | 1353 | RO | reserve
| 054A | 1354 | RO | reserve
| 054B | 1355 | RO | reserve
| 054C | 1356 | RO | reserve
| 054D | 1357 | RO | reserve
| 054E | 1358 | RO | reserve
| 054F | 1359 | RO | reserve
| 0550 | 1360 | RO | reserve
| 0551 | 1361 | RO | reserve
| 0552 | 1362 | RO | reserve
| 0553 | 1363 | RO | reserve
| 0554 | 1364 | RO | reserve
| 0555 | 1365 | RO | reserve
| 0556 | 1366 | RO | reserve
| 0557 | 1367 | RO | reserve
| 0558 | 1368 | RO | reserve
| 0559 | 1369 | RO | reserve
| 055A | 1370 | RO | reserve
| 055B | 1371 | RO | reserve
| 055C | 1372 | RO | reserve
| 055D | 1373 | RO | reserve
| 055E | 1374 | RO | reserve
| 055F | 1375 | RO | reserve
| 0560 | 1376 | RO | reserve
| 0561 | 1377 | RO | reserve
| 0562 | 1378 | RO | reserve
| 0563 | 1379 | RO | reserve
| 0564 | 1380 | RO | reserve
| 0565 | 1381 | RO | reserve
| 0566 | 1382 | RO | reserve
| 0567 | 1383 | RO | reserve
| 0568 | 1384 | RO | reserve
| 0569 | 1385 | RO | reserve
| 056A | 1386 | RO | reserve
| 056B | 1387 | RO | reserve
| 056C | 1388 | RO | reserve
| 056D | 1389 | RO | reserve
| 056E | 1390 | RO | reserve
| 056F | 1391 | RO | reserve
| 0570 | 1392 | RO | reserve
| 0571 | 1393 | RO | reserve
| 0572 | 1394 | RO | reserve
| 0573 | 1395 | RO | reserve
| 0574 | 1396 | RO | reserve
| 0575 | 1397 | RO | reserve
| 0576 | 1398 | RO | reserve
| 0577 | 1399 | RO | reserve
| 0578 | 1400 | RO | reserve

## Cell Volt
Register Type | Register Address |  | Attributes | Meaning | Data Types | Coefficient | Offset | Units | Remarks | Decimal pointPrecision required | Units
| Hexadecimal | Decimal
Cell voltage data (Each rack Modbus address independent, starting from 2, discrete input registers,function code 0x04, same Modbus address as rack data, same function code, different register addresses) | 00C9 | 201 | RO | 1# cell voltage | FLOAT |  |  | V | Cell voltage | 0.001 | V
| 00CB | 203 | RO | 2# cell voltage | FLOAT |  |  | V |  | 0.001 | V
| 00CD | 205 | RO | 3# cell voltage | FLOAT |  |  | V |  | 0.001 | V
| 00CF | 207 | RO | 4# cell voltage | FLOAT |  |  | V |  | 0.001 | V
| 00D1 | 209 | RO | 5# cell voltage | FLOAT |  |  | V |  | 0.001 | V
| 00D3 | 211 | RO | 6# cell voltage | FLOAT |  |  | V |  | 0.001 | V
| 00D5 | 213 | RO | 7# cell voltage | FLOAT |  |  | V |  | 0.001 | V
| 00D7 | 215 | RO | 8# cell voltage | FLOAT |  |  | V |  | 0.001 | V
| 00D9 | 217 | RO | 9# cell voltage | FLOAT |  |  | V |  | 0.001 | V
| 00DB | 219 | RO | 10# cell voltage | FLOAT |  |  | V |  | 0.001 | V
| 00DD | 221 | RO | 11# cell voltage | FLOAT |  |  | V |  | 0.001 | V
| 00DF | 223 | RO | 12# cell voltage | FLOAT |  |  | V |  | 0.001 | V
| 0 | 225 | RO | 13# cell voltage | FLOAT |  |  | V |  | 0.001 | V
| 0 | 227 | RO | 14# cell voltage | FLOAT |  |  | V |  | 0.001 | V
| 0 | 229 | RO | 15# cell voltage | FLOAT |  |  | V |  | 0.001 | V
| 0 | 231 | RO | 16# cell voltage | FLOAT |  |  | V |  | 0.001 | V
| 0 | 233 | RO | 17# cell voltage | FLOAT |  |  | V |  | 0.001 | V
| 00EB | 235 | RO | 18# cell voltage | FLOAT |  |  | V |  | 0.001 | V
| 00ED | 237 | RO | 19# cell voltage | FLOAT |  |  | V |  | 0.001 | V
| 00EF | 239 | RO | 20# cell voltage | FLOAT |  |  | V |  | 0.001 | V
| 00F1 | 241 | RO | 21# cell voltage | FLOAT |  |  | V |  | 0.001 | V
| 00F3 | 243 | RO | 22# cell voltage | FLOAT |  |  | V |  | 0.001 | V
| 00F5 | 245 | RO | 23# cell voltage | FLOAT |  |  | V |  | 0.001 | V
| 00F7 | 247 | RO | 24# cell voltage | FLOAT |  |  | V |  | 0.001 | V
| 00F9 | 249 | RO | 25# cell voltage | FLOAT |  |  | V |  | 0.001 | V
| 00FB | 251 | RO | 26# cell voltage | FLOAT |  |  | V |  | 0.001 | V
| 00FD | 253 | RO | 27# cell voltage | FLOAT |  |  | V |  | 0.001 | V
| 00FF | 255 | RO | 28# cell voltage | FLOAT |  |  | V |  | 0.001 | V
| 101 | 257 | RO | 29# cell voltage | FLOAT |  |  | V |  | 0.001 | V
| 103 | 259 | RO | 30# cell voltage | FLOAT |  |  | V |  | 0.001 | V
| 105 | 261 | RO | 31# cell voltage | FLOAT |  |  | V |  | 0.001 | V
| 107 | 263 | RO | 32# cell voltage | FLOAT |  |  | V |  | 0.001 | V
| 109 | 265 | RO | 33# cell voltage | FLOAT |  |  | V |  | 0.001 | V
| 010B | 267 | RO | 34# cell voltage | FLOAT |  |  | V |  | 0.001 | V
| 010D | 269 | RO | 35# cell voltage | FLOAT |  |  | V |  | 0.001 | V
| 010F | 271 | RO | 36# cell voltage | FLOAT |  |  | V |  | 0.001 | V
| 111 | 273 | RO | 37# cell voltage | FLOAT |  |  | V |  | 0.001 | V
| 113 | 275 | RO | 38# cell voltage | FLOAT |  |  | V |  | 0.001 | V
| 115 | 277 | RO | 39# cell voltage | FLOAT |  |  | V |  | 0.001 | V
| 117 | 279 | RO | 40# cell voltage | FLOAT |  |  | V |  | 0.001 | V
| 119 | 281 | RO | 41# cell voltage | FLOAT |  |  | V |  | 0.001 | V
| 011B | 283 | RO | 42# cell voltage | FLOAT |  |  | V |  | 0.001 | V
| 011D | 285 | RO | 43# cell voltage | FLOAT |  |  | V |  | 0.001 | V
| 011F | 287 | RO | 44# cell voltage | FLOAT |  |  | V |  | 0.001 | V
| 121 | 289 | RO | 45# cell voltage | FLOAT |  |  | V |  | 0.001 | V
| 123 | 291 | RO | 46# cell voltage | FLOAT |  |  | V |  | 0.001 | V
| 125 | 293 | RO | 47# cell voltage | FLOAT |  |  | V |  | 0.001 | V
| 127 | 295 | RO | 48# cell voltage | FLOAT |  |  | V |  | 0.001 | V
| 129 | 297 | RO | 49# cell voltage | FLOAT |  |  | V |  | 0.001 | V
| 012B | 299 | RO | 50# cell voltage | FLOAT |  |  | V |  | 0.001 | V
| 012D | 301 | RO | 51# cell voltage | FLOAT |  |  | V |  | 0.001 | V
| 012F | 303 | RO | 52# cell voltage | FLOAT |  |  | V |  | 0.001 | V
| 131 | 305 | RO | 53# cell voltage | FLOAT |  |  | V |  | 0.001 | V
| 133 | 307 | RO | 54# cell voltage | FLOAT |  |  | V |  | 0.001 | V
| 135 | 309 | RO | 55# cell voltage | FLOAT |  |  | V |  | 0.001 | V
| 137 | 311 | RO | 56# cell voltage | FLOAT |  |  | V |  | 0.001 | V
| 139 | 313 | RO | 57# cell voltage | FLOAT |  |  | V |  | 0.001 | V
| 013B | 315 | RO | 58# cell voltage | FLOAT |  |  | V |  | 0.001 | V
| 013D | 317 | RO | 59# cell voltage | FLOAT |  |  | V |  | 0.001 | V
| 013F | 319 | RO | 60# cell voltage | FLOAT |  |  | V |  | 0.001 | V
| 141 | 321 | RO | 61# cell voltage | FLOAT |  |  | V |  | 0.001 | V
| 143 | 323 | RO | 62# cell voltage | FLOAT |  |  | V |  | 0.001 | V
| 145 | 325 | RO | 63# cell voltage | FLOAT |  |  | V |  | 0.001 | V
| 147 | 327 | RO | 64# cell voltage | FLOAT |  |  | V |  | 0.001 | V
| 149 | 329 | RO | 65# cell voltage | FLOAT |  |  | V |  | 0.001 | V
| 014B | 331 | RO | 66# cell voltage | FLOAT |  |  | V |  | 0.001 | V
| 014D | 333 | RO | 67# cell voltage | FLOAT |  |  | V |  | 0.001 | V
| 014F | 335 | RO | 68# cell voltage | FLOAT |  |  | V |  | 0.001 | V
| 151 | 337 | RO | 69# cell voltage | FLOAT |  |  | V |  | 0.001 | V
| 153 | 339 | RO | 70# cell voltage | FLOAT |  |  | V |  | 0.001 | V
| 155 | 341 | RO | 71# cell voltage | FLOAT |  |  | V |  | 0.001 | V
| 157 | 343 | RO | 72# cell voltage | FLOAT |  |  | V |  | 0.001 | V
| 159 | 345 | RO | 73# cell voltage | FLOAT |  |  | V |  | 0.001 | V
| 015B | 347 | RO | 74# cell voltage | FLOAT |  |  | V |  | 0.001 | V
| 015D | 349 | RO | 75# cell voltage | FLOAT |  |  | V |  | 0.001 | V
| 015F | 351 | RO | 76# cell voltage | FLOAT |  |  | V |  | 0.001 | V
| 161 | 353 | RO | 77# cell voltage | FLOAT |  |  | V |  | 0.001 | V
| 163 | 355 | RO | 78# cell voltage | FLOAT |  |  | V |  | 0.001 | V
| 165 | 357 | RO | 79# cell voltage | FLOAT |  |  | V |  | 0.001 | V
| 167 | 359 | RO | 80# cell voltage | FLOAT |  |  | V |  | 0.001 | V
| 169 | 361 | RO | 81# cell voltage | FLOAT |  |  | V |  | 0.001 | V
| 016B | 363 | RO | 82# cell voltage | FLOAT |  |  | V |  | 0.001 | V
| 016D | 365 | RO | 83# cell voltage | FLOAT |  |  | V |  | 0.001 | V
| 016F | 367 | RO | 84# cell voltage | FLOAT |  |  | V |  | 0.001 | V
| 171 | 369 | RO | 85# cell voltage | FLOAT |  |  | V |  | 0.001 | V
| 173 | 371 | RO | 86# cell voltage | FLOAT |  |  | V |  | 0.001 | V
| 175 | 373 | RO | 87# cell voltage | FLOAT |  |  | V |  | 0.001 | V
| 177 | 375 | RO | 88# cell voltage | FLOAT |  |  | V |  | 0.001 | V
| 179 | 377 | RO | 89# cell voltage | FLOAT |  |  | V |  | 0.001 | V
| 017B | 379 | RO | 90# cell voltage | FLOAT |  |  | V |  | 0.001 | V
| 017D | 381 | RO | 91# cell voltage | FLOAT |  |  | V |  | 0.001 | V
| 017F | 383 | RO | 92# cell voltage | FLOAT |  |  | V |  | 0.001 | V
| 181 | 385 | RO | 93# cell voltage | FLOAT |  |  | V |  | 0.001 | V
| 183 | 387 | RO | 94# cell voltage | FLOAT |  |  | V |  | 0.001 | V
| 185 | 389 | RO | 95# cell voltage | FLOAT |  |  | V |  | 0.001 | V
| 187 | 391 | RO | 96# cell voltage | FLOAT |  |  | V |  | 0.001 | V
| 189 | 393 | RO | 97# cell voltage | FLOAT |  |  | V |  | 0.001 | V
| 018B | 395 | RO | 98# cell voltage | FLOAT |  |  | V |  | 0.001 | V
| 018D | 397 | RO | 99# cell voltage | FLOAT |  |  | V |  | 0.001 | V
| 018F | 399 | RO | 100# cell voltage | FLOAT |  |  | V |  | 0.001 | V
| 191 | 401 | RO | 101# cell voltage | FLOAT |  |  | V |  | 0.001 | V
| 193 | 403 | RO | 102# cell voltage | FLOAT |  |  | V |  | 0.001 | V
| 195 | 405 | RO | 103# cell voltage | FLOAT |  |  | V |  | 0.001 | V
| 197 | 407 | RO | 104# cell voltage | FLOAT |  |  | V |  | 0.001 | V
| 199 | 409 | RO | 105# cell voltage | FLOAT |  |  | V |  | 0.001 | V
| 019B | 411 | RO | 106# cell voltage | FLOAT |  |  | V |  | 0.001 | V
| 019D | 413 | RO | 107# cell voltage | FLOAT |  |  | V |  | 0.001 | V
| 019F | 415 | RO | 108# cell voltage | FLOAT |  |  | V |  | 0.001 | V
| 01A1 | 417 | RO | 109# cell voltage | FLOAT |  |  | V |  | 0.001 | V
| 01A3 | 419 | RO | 110# cell voltage | FLOAT |  |  | V |  | 0.001 | V
| 01A5 | 421 | RO | 111# cell voltage | FLOAT |  |  | V |  | 0.001 | V
| 01A7 | 423 | RO | 112# cell voltage | FLOAT |  |  | V |  | 0.001 | V
| 01A9 | 425 | RO | 113# cell voltage | FLOAT |  |  | V |  | 0.001 | V
| 01AB | 427 | RO | 114# cell voltage | FLOAT |  |  | V |  | 0.001 | V
| 01AD | 429 | RO | 115# cell voltage | FLOAT |  |  | V |  | 0.001 | V
| 01AF | 431 | RO | 116# cell voltage | FLOAT |  |  | V |  | 0.001 | V
| 01B1 | 433 | RO | 117# cell voltage | FLOAT |  |  | V |  | 0.001 | V
| 01B3 | 435 | RO | 118# cell voltage | FLOAT |  |  | V |  | 0.001 | V
| 01B5 | 437 | RO | 119# cell voltage | FLOAT |  |  | V |  | 0.001 | V
| 01B7 | 439 | RO | 120# cell voltage | FLOAT |  |  | V |  | 0.001 | V
| 01B9 | 441 | RO | 121# cell voltage | FLOAT |  |  | V |  | 0.001 | V
| 01BB | 443 | RO | 122# cell voltage | FLOAT |  |  | V |  | 0.001 | V
| 01BD | 445 | RO | 123# cell voltage | FLOAT |  |  | V |  | 0.001 | V
| 01BF | 447 | RO | 124# cell voltage | FLOAT |  |  | V |  | 0.001 | V
| 01C1 | 449 | RO | 125# cell voltage | FLOAT |  |  | V |  | 0.001 | V
| 01C3 | 451 | RO | 126# cell voltage | FLOAT |  |  | V |  | 0.001 | V
| 01C5 | 453 | RO | 127# cell voltage | FLOAT |  |  | V |  | 0.001 | V
| 01C7 | 455 | RO | 128# cell voltage | FLOAT |  |  | V |  | 0.001 | V
| 01C9 | 457 | RO | 129# cell voltage | FLOAT |  |  | V |  | 0.001 | V
| 01CB | 459 | RO | 130# cell voltage | FLOAT |  |  | V |  | 0.001 | V
| 01CD | 461 | RO | 131# cell voltage | FLOAT |  |  | V |  | 0.001 | V
| 01CF | 463 | RO | 132# cell voltage | FLOAT |  |  | V |  | 0.001 | V
| 01D1 | 465 | RO | 133# cell voltage | FLOAT |  |  | V |  | 0.001 | V
| 01D3 | 467 | RO | 134# cell voltage | FLOAT |  |  | V |  | 0.001 | V
| 01D5 | 469 | RO | 135# cell voltage | FLOAT |  |  | V |  | 0.001 | V
| 01D7 | 471 | RO | 136# cell voltage | FLOAT |  |  | V |  | 0.001 | V
| 01D9 | 473 | RO | 137# cell voltage | FLOAT |  |  | V |  | 0.001 | V
| 01DB | 475 | RO | 138# cell voltage | FLOAT |  |  | V |  | 0.001 | V
| 01DD | 477 | RO | 139# cell voltage | FLOAT |  |  | V |  | 0.001 | V
| 01DF | 479 | RO | 140# cell voltage | FLOAT |  |  | V |  | 0.001 | V
| 10 | 481 | RO | 141# cell voltage | FLOAT |  |  | V |  | 0.001 | V
| 1000 | 483 | RO | 142# cell voltage | FLOAT |  |  | V |  | 0.001 | V
| 100000 | 485 | RO | 143# cell voltage | FLOAT |  |  | V |  | 0.001 | V
| 10000000 | 487 | RO | 144# cell voltage | FLOAT |  |  | V |  | 0.001 | V
| 1000000000 | 489 | RO | 145# cell voltage | FLOAT |  |  | V |  | 0.001 | V
| 01EB | 491 | RO | 146# cell voltage | FLOAT |  |  | V |  | 0.001 | V
| 01ED | 493 | RO | 147# cell voltage | FLOAT |  |  | V |  | 0.001 | V
| 01EF | 495 | RO | 148# cell voltage | FLOAT |  |  | V |  | 0.001 | V
| 01F1 | 497 | RO | 149# cell voltage | FLOAT |  |  | V |  | 0.001 | V
| 01F3 | 499 | RO | 150# cell voltage | FLOAT |  |  | V |  | 0.001 | V
| 01F5 | 501 | RO | 151# cell voltage | FLOAT |  |  | V |  | 0.001 | V
| 01F7 | 503 | RO | 152# cell voltage | FLOAT |  |  | V |  | 0.001 | V
| 01F9 | 505 | RO | 153# cell voltage | FLOAT |  |  | V |  | 0.001 | V
| 01FB | 507 | RO | 154# cell voltage | FLOAT |  |  | V |  | 0.001 | V
| 01FD | 509 | RO | 155# cell voltage | FLOAT |  |  | V |  | 0.001 | V
| 01FF | 511 | RO | 156# cell voltage | FLOAT |  |  | V |  | 0.001 | V
| 201 | 513 | RO | 157# cell voltage | FLOAT |  |  | V |  | 0.001 | V
| 203 | 515 | RO | 158# cell voltage | FLOAT |  |  | V |  | 0.001 | V
| 205 | 517 | RO | 159# cell voltage | FLOAT |  |  | V |  | 0.001 | V
| 207 | 519 | RO | 160# cell voltage | FLOAT |  |  | V |  | 0.001 | V
| 209 | 521 | RO | 161# cell voltage | FLOAT |  |  | V |  | 0.001 | V
| 020B | 523 | RO | 162# cell voltage | FLOAT |  |  | V |  | 0.001 | V
| 020D | 525 | RO | 163# cell voltage | FLOAT |  |  | V |  | 0.001 | V
| 020F | 527 | RO | 164# cell voltage | FLOAT |  |  | V |  | 0.001 | V
| 211 | 529 | RO | 165# cell voltage | FLOAT |  |  | V |  | 0.001 | V
| 213 | 531 | RO | 166# cell voltage | FLOAT |  |  | V |  | 0.001 | V
| 215 | 533 | RO | 167# cell voltage | FLOAT |  |  | V |  | 0.001 | V
| 217 | 535 | RO | 168# cell voltage | FLOAT |  |  | V |  | 0.001 | V
| 219 | 537 | RO | 169# cell voltage | FLOAT |  |  | V |  | 0.001 | V
| 021B | 539 | RO | 170# cell voltage | FLOAT |  |  | V |  | 0.001 | V
| 021D | 541 | RO | 171# cell voltage | FLOAT |  |  | V |  | 0.001 | V
| 021F | 543 | RO | 172# cell voltage | FLOAT |  |  | V |  | 0.001 | V
| 221 | 545 | RO | 173# cell voltage | FLOAT |  |  | V |  | 0.001 | V
| 223 | 547 | RO | 174# cell voltage | FLOAT |  |  | V |  | 0.001 | V
| 225 | 549 | RO | 175# cell voltage | FLOAT |  |  | V |  | 0.001 | V
| 227 | 551 | RO | 176# cell voltage | FLOAT |  |  | V |  | 0.001 | V
| 229 | 553 | RO | 177# cell voltage | FLOAT |  |  | V |  | 0.001 | V
| 022B | 555 | RO | 178# cell voltage | FLOAT |  |  | V |  | 0.001 | V
| 022D | 557 | RO | 179# cell voltage | FLOAT |  |  | V |  | 0.001 | V
| 022F | 559 | RO | 180# cell voltage | FLOAT |  |  | V |  | 0.001 | V
| 231 | 561 | RO | 181# cell voltage | FLOAT |  |  | V |  | 0.001 | V
| 233 | 563 | RO | 182# cell voltage | FLOAT |  |  | V |  | 0.001 | V
| 235 | 565 | RO | 183# cell voltage | FLOAT |  |  | V |  | 0.001 | V
| 237 | 567 | RO | 184# cell voltage | FLOAT |  |  | V |  | 0.001 | V
| 239 | 569 | RO | 185# cell voltage | FLOAT |  |  | V |  | 0.001 | V
| 023B | 571 | RO | 186# cell voltage | FLOAT |  |  | V |  | 0.001 | V
| 023D | 573 | RO | 187# cell voltage | FLOAT |  |  | V |  | 0.001 | V
| 023F | 575 | RO | 188# cell voltage | FLOAT |  |  | V |  | 0.001 | V
| 241 | 577 | RO | 189# cell voltage | FLOAT |  |  | V |  | 0.001 | V
| 243 | 579 | RO | 190# cell voltage | FLOAT |  |  | V |  | 0.001 | V
| 245 | 581 | RO | 191# cell voltage | FLOAT |  |  | V |  | 0.001 | V
| 247 | 583 | RO | 192# cell voltage | FLOAT |  |  | V |  | 0.001 | V
| 249 | 585 | RO | 193# cell voltage | FLOAT |  |  | V |  | 0.001 | V
| 024B | 587 | RO | 194# cell voltage | FLOAT |  |  | V |  | 0.001 | V
| 024D | 589 | RO | 195# cell voltage | FLOAT |  |  | V |  | 0.001 | V
| 024F | 591 | RO | 196# cell voltage | FLOAT |  |  | V |  | 0.001 | V
| 251 | 593 | RO | 197# cell voltage | FLOAT |  |  | V |  | 0.001 | V
| 253 | 595 | RO | 198# cell voltage | FLOAT |  |  | V |  | 0.001 | V
| 255 | 597 | RO | 199# cell voltage | FLOAT |  |  | V |  | 0.001 | V
| 257 | 599 | RO | 200# cell voltage | FLOAT |  |  | V |  | 0.001 | V
| 259 | 601 | RO | 201# cell voltage | FLOAT |  |  | V |  | 0.001 | V
| 025B | 603 | RO | 202# cell voltage | FLOAT |  |  | V |  | 0.001 | V
| 025D | 605 | RO | 203# cell voltage | FLOAT |  |  | V |  | 0.001 | V
| 025F | 607 | RO | 204# cell voltage | FLOAT |  |  | V |  | 0.001 | V
| 261 | 609 | RO | 205# cell voltage | FLOAT |  |  | V |  | 0.001 | V
| 263 | 611 | RO | 206# cell voltage | FLOAT |  |  | V |  | 0.001 | V
| 265 | 613 | RO | 207# cell voltage | FLOAT |  |  | V |  | 0.001 | V
| 267 | 615 | RO | 208# cell voltage | FLOAT |  |  | V |  | 0.001 | V
| 269 | 617 | RO | 209# cell voltage | FLOAT |  |  | V |  | 0.001 | V
| 026B | 619 | RO | 210# cell voltage | FLOAT |  |  | V |  | 0.001 | V
| 026D | 621 | RO | 211# cell voltage | FLOAT |  |  | V |  | 0.001 | V
| 026F | 623 | RO | 212# cell voltage | FLOAT |  |  | V |  | 0.001 | V
| 271 | 625 | RO | 213# cell voltage | FLOAT |  |  | V |  | 0.001 | V
| 273 | 627 | RO | 214# cell voltage | FLOAT |  |  | V |  | 0.001 | V
| 275 | 629 | RO | 215# cell voltage | FLOAT |  |  | V |  | 0.001 | V
| 277 | 631 | RO | 216# cell voltage | FLOAT |  |  | V |  | 0.001 | V
| 279 | 633 | RO | 217# cell voltage | FLOAT |  |  | V |  | 0.001 | V
| 027B | 635 | RO | 218# cell voltage | FLOAT |  |  | V |  | 0.001 | V
| 027D | 637 | RO | 219# cell voltage | FLOAT |  |  | V |  | 0.001 | V
| 027F | 639 | RO | 220# cell voltage | FLOAT |  |  | V |  | 0.001 | V
| 281 | 641 | RO | 221# cell voltage | FLOAT |  |  | V |  | 0.001 | V
| 283 | 643 | RO | 222# cell voltage | FLOAT |  |  | V |  | 0.001 | V
| 285 | 645 | RO | 223# cell voltage | FLOAT |  |  | V |  | 0.001 | V
| 287 | 647 | RO | 224# cell voltage | FLOAT |  |  | V |  | 0.001 | V
| 289 | 649 | RO | 225# cell voltage | FLOAT |  |  | V |  | 0.001 | V
| 028B | 651 | RO | 226# cell voltage | FLOAT |  |  | V |  | 0.001 | V
| 028D | 653 | RO | 227# cell voltage | FLOAT |  |  | V |  | 0.001 | V
| 028F | 655 | RO | 228# cell voltage | FLOAT |  |  | V |  | 0.001 | V
| 291 | 657 | RO | 229# cell voltage | FLOAT |  |  | V |  | 0.001 | V
| 293 | 659 | RO | 230# cell voltage | FLOAT |  |  | V |  | 0.001 | V
| 295 | 661 | RO | 231# cell voltage | FLOAT |  |  | V |  | 0.001 | V
| 297 | 663 | RO | 232# cell voltage | FLOAT |  |  | V |  | 0.001 | V
| 299 | 665 | RO | 233# cell voltage | FLOAT |  |  | V |  | 0.001 | V
| 029B | 667 | RO | 234# cell voltage | FLOAT |  |  | V |  | 0.001 | V
| 029D | 669 | RO | 235# cell voltage | FLOAT |  |  | V |  | 0.001 | V
| 029F | 671 | RO | 236# cell voltage | FLOAT |  |  | V |  | 0.001 | V
| 02A1 | 673 | RO | 237# cell voltage | FLOAT |  |  | V |  | 0.001 | V
| 02A3 | 675 | RO | 238# cell voltage | FLOAT |  |  | V |  | 0.001 | V
| 02A5 | 677 | RO | 239# cell voltage | FLOAT |  |  | V |  | 0.001 | V
| 02A7 | 679 | RO | 240# cell voltage | FLOAT |  |  | V |  | 0.001 | V
| 02A9 | 681 | RO | 241# cell voltage | FLOAT |  |  | V |  | 0.001 | V
| 02AB | 683 | RO | 242# cell voltage | FLOAT |  |  | V |  | 0.001 | V
| 02AD | 685 | RO | 243# cell voltage | FLOAT |  |  | V |  | 0.001 | V
| 02AF | 687 | RO | 244# cell voltage | FLOAT |  |  | V |  | 0.001 | V
| 02B1 | 689 | RO | 245# cell voltage | FLOAT |  |  | V |  | 0.001 | V
| 02B3 | 691 | RO | 246# cell voltage | FLOAT |  |  | V |  | 0.001 | V
| 02B5 | 693 | RO | 247# cell voltage | FLOAT |  |  | V |  | 0.001 | V
| 02B7 | 695 | RO | 248# cell voltage | FLOAT |  |  | V |  | 0.001 | V
| 02B9 | 697 | RO | 249# cell voltage | FLOAT |  |  | V |  | 0.001 | V
| 02BB | 699 | RO | 250# cell voltage | FLOAT |  |  | V |  | 0.001 | V
| 02BD | 701 | RO | 251# cell voltage | FLOAT |  |  | V |  | 0.001 | V
| 02BF | 703 | RO | 252# cell voltage | FLOAT |  |  | V |  | 0.001 | V
| 02C1 | 705 | RO | 253# cell voltage | FLOAT |  |  | V |  | 0.001 | V
| 02C3 | 707 | RO | 254# cell voltage | FLOAT |  |  | V |  | 0.001 | V
| 02C5 | 709 | RO | 255# cell voltage | FLOAT |  |  | V |  | 0.001 | V
| 02C7 | 711 | RO | 256# cell voltage | FLOAT |  |  | V |  | 0.001 | V
| 02C9 | 713 | RO | 257# cell voltage | FLOAT |  |  | V |  | 0.001 | V
| 02CB | 715 | RO | 258# cell voltage | FLOAT |  |  | V |  | 0.001 | V
| 02CD | 717 | RO | 259# cell voltage | FLOAT |  |  | V |  | 0.001 | V
| 02CF | 719 | RO | 260# cell voltage | FLOAT |  |  | V |  | 0.001 | V
| 02D1 | 721 | RO | 261# cell voltage | FLOAT |  |  | V |  | 0.001 | V
| 02D3 | 723 | RO | 262# cell voltage | FLOAT |  |  | V |  | 0.001 | V
| 02D5 | 725 | RO | 263# cell voltage | FLOAT |  |  | V |  | 0.001 | V
| 02D7 | 727 | RO | 264# cell voltage | FLOAT |  |  | V |  | 0.001 | V
| 02D9 | 729 | RO | 265# cell voltage | FLOAT |  |  | V |  | 0.001 | V
| 02DB | 731 | RO | 266# cell voltage | FLOAT |  |  | V |  | 0.001 | V
| 02DD | 733 | RO | 267# cell voltage | FLOAT |  |  | V |  | 0.001 | V
| 02DF | 735 | RO | 268# cell voltage | FLOAT |  |  | V |  | 0.001 | V
| 20 | 737 | RO | 269# cell voltage | FLOAT |  |  | V |  | 0.001 | V
| 2000 | 739 | RO | 270# cell voltage | FLOAT |  |  | V |  | 0.001 | V
| 200000 | 741 | RO | 271# cell voltage | FLOAT |  |  | V |  | 0.001 | V
| 20000000 | 743 | RO | 272# cell voltage | FLOAT |  |  | V |  | 0.001 | V
| 2000000000 | 745 | RO | 273# cell voltage | FLOAT |  |  | V |  | 0.001 | V
| 02EB | 747 | RO | 274# cell voltage | FLOAT |  |  | V |  | 0.001 | V
| 02ED | 749 | RO | 275# cell voltage | FLOAT |  |  | V |  | 0.001 | V
| 02EF | 751 | RO | 276# cell voltage | FLOAT |  |  | V |  | 0.001 | V
| 02F1 | 753 | RO | 277# cell voltage | FLOAT |  |  | V |  | 0.001 | V
| 02F3 | 755 | RO | 278# cell voltage | FLOAT |  |  | V |  | 0.001 | V
| 02F5 | 757 | RO | 279# cell voltage | FLOAT |  |  | V |  | 0.001 | V
| 02F7 | 759 | RO | 280# cell voltage | FLOAT |  |  | V |  | 0.001 | V
| 02F9 | 761 | RO | 281# cell voltage | FLOAT |  |  | V |  | 0.001 | V
| 02FB | 763 | RO | 282# cell voltage | FLOAT |  |  | V |  | 0.001 | V
| 02FD | 765 | RO | 283# cell voltage | FLOAT |  |  | V |  | 0.001 | V
| 02FF | 767 | RO | 284# cell voltage | FLOAT |  |  | V |  | 0.001 | V
| 301 | 769 | RO | 285# cell voltage | FLOAT |  |  | V |  | 0.001 | V
| 303 | 771 | RO | 286# cell voltage | FLOAT |  |  | V |  | 0.001 | V
| 305 | 773 | RO | 287# cell voltage | FLOAT |  |  | V |  | 0.001 | V
| 307 | 775 | RO | 288# cell voltage | FLOAT |  |  | V |  | 0.001 | V
| 309 | 777 | RO | 289# cell voltage | FLOAT |  |  | V |  | 0.001 | V
| 030B | 779 | RO | 290# cell voltage | FLOAT |  |  | V |  | 0.001 | V
| 030D | 781 | RO | 291# cell voltage | FLOAT |  |  | V |  | 0.001 | V
| 030F | 783 | RO | 292# cell voltage | FLOAT |  |  | V |  | 0.001 | V
| 311 | 785 | RO | 293# cell voltage | FLOAT |  |  | V |  | 0.001 | V
| 313 | 787 | RO | 294# cell voltage | FLOAT |  |  | V |  | 0.001 | V
| 315 | 789 | RO | 295# cell voltage | FLOAT |  |  | V |  | 0.001 | V
| 317 | 791 | RO | 296# cell voltage | FLOAT |  |  | V |  | 0.001 | V
| 319 | 793 | RO | 297# cell voltage | FLOAT |  |  | V |  | 0.001 | V
| 031B | 795 | RO | 298# cell voltage | FLOAT |  |  | V |  | 0.001 | V
| 031D | 797 | RO | 299# cell voltage | FLOAT |  |  | V |  | 0.001 | V
| 031F | 799 | RO | 300# cell voltage | FLOAT |  |  | V |  | 0.001 | V
| 321 | 801 | RO | 301# cell voltage | FLOAT |  |  | V |  | 0.001 | V
| 323 | 803 | RO | 302# cell voltage | FLOAT |  |  | V |  | 0.001 | V
| 325 | 805 | RO | 303# cell voltage | FLOAT |  |  | V |  | 0.001 | V
| 327 | 807 | RO | 304# cell voltage | FLOAT |  |  | V |  | 0.001 | V
| 329 | 809 | RO | 305# cell voltage | FLOAT |  |  | V |  | 0.001 | V
| 032B | 811 | RO | 306# cell voltage | FLOAT |  |  | V |  | 0.001 | V
| 032D | 813 | RO | 307# cell voltage | FLOAT |  |  | V |  | 0.001 | V
| 032F | 815 | RO | 308# cell voltage | FLOAT |  |  | V |  | 0.001 | V
| 331 | 817 | RO | 309# cell voltage | FLOAT |  |  | V |  | 0.001 | V
| 333 | 819 | RO | 310# cell voltage | FLOAT |  |  | V |  | 0.001 | V
| 335 | 821 | RO | 311# cell voltage | FLOAT |  |  | V |  | 0.001 | V
| 337 | 823 | RO | 312# cell voltage | FLOAT |  |  | V |  | 0.001 | V
| 339 | 825 | RO | 313# cell voltage | FLOAT |  |  | V |  | 0.001 | V
| 033B | 827 | RO | 314# cell voltage | FLOAT |  |  | V |  | 0.001 | V
| 033D | 829 | RO | 315# cell voltage | FLOAT |  |  | V |  | 0.001 | V
| 033F | 831 | RO | 316# cell voltage | FLOAT |  |  | V |  | 0.001 | V
| 341 | 833 | RO | 317# cell voltage | FLOAT |  |  | V |  | 0.001 | V
| 343 | 835 | RO | 318# cell voltage | FLOAT |  |  | V |  | 0.001 | V
| 345 | 837 | RO | 319# cell voltage | FLOAT |  |  | V |  | 0.001 | V
| 347 | 839 | RO | 320# cell voltage | FLOAT |  |  | V |  | 0.001 | V
| 349 | 841 | RO | 321# cell voltage | FLOAT |  |  | V |  | 0.001 | V
| 034B | 843 | RO | 322# cell voltage | FLOAT |  |  | V |  | 0.001 | V
| 034D | 845 | RO | 323# cell voltage | FLOAT |  |  | V |  | 0.001 | V
| 034F | 847 | RO | 324# cell voltage | FLOAT |  |  | V |  | 0.001 | V
| 351 | 849 | RO | 325# cell voltage | FLOAT |  |  | V |  | 0.001 | V
| 353 | 851 | RO | 326# cell voltage | FLOAT |  |  | V |  | 0.001 | V
| 355 | 853 | RO | 327# cell voltage | FLOAT |  |  | V |  | 0.001 | V
| 357 | 855 | RO | 328# cell voltage | FLOAT |  |  | V |  | 0.001 | V
| 359 | 857 | RO | 329# cell voltage | FLOAT |  |  | V |  | 0.001 | V
| 035B | 859 | RO | 330# cell voltage | FLOAT |  |  | V |  | 0.001 | V
| 035D | 861 | RO | 331# cell voltage | FLOAT |  |  | V |  | 0.001 | V
| 035F | 863 | RO | 332# cell voltage | FLOAT |  |  | V |  | 0.001 | V
| 361 | 865 | RO | 333# cell voltage | FLOAT |  |  | V |  | 0.001 | V
| 363 | 867 | RO | 334# cell voltage | FLOAT |  |  | V |  | 0.001 | V
| 365 | 869 | RO | 335# cell voltage | FLOAT |  |  | V |  | 0.001 | V
| 367 | 871 | RO | 336# cell voltage | FLOAT |  |  | V |  | 0.001 | V
| 369 | 873 | RO | 337# cell voltage | FLOAT |  |  | V |  | 0.001 | V
| 036B | 875 | RO | 338# cell voltage | FLOAT |  |  | V |  | 0.001 | V
| 036D | 877 | RO | 339# cell voltage | FLOAT |  |  | V |  | 0.001 | V
| 036F | 879 | RO | 340# cell voltage | FLOAT |  |  | V |  | 0.001 | V
| 371 | 881 | RO | 341# cell voltage | FLOAT |  |  | V |  | 0.001 | V
| 373 | 883 | RO | 342# cell voltage | FLOAT |  |  | V |  | 0.001 | V
| 375 | 885 | RO | 343# cell voltage | FLOAT |  |  | V |  | 0.001 | V
| 377 | 887 | RO | 344# cell voltage | FLOAT |  |  | V |  | 0.001 | V
| 379 | 889 | RO | 345# cell voltage | FLOAT |  |  | V |  | 0.001 | V
| 037B | 891 | RO | 346# cell voltage | FLOAT |  |  | V |  | 0.001 | V
| 037D | 893 | RO | 347# cell voltage | FLOAT |  |  | V |  | 0.001 | V
| 037F | 895 | RO | 348# cell voltage | FLOAT |  |  | V |  | 0.001 | V
| 381 | 897 | RO | 349# cell voltage | FLOAT |  |  | V |  | 0.001 | V
| 383 | 899 | RO | 350# cell voltage | FLOAT |  |  | V |  | 0.001 | V
| 385 | 901 | RO | 351# cell voltage | FLOAT |  |  | V |  | 0.001 | V
| 387 | 903 | RO | 352# cell voltage | FLOAT |  |  | V |  | 0.001 | V
| 389 | 905 | RO | 353# cell voltage | FLOAT |  |  | V |  | 0.001 | V
| 038B | 907 | RO | 354# cell voltage | FLOAT |  |  | V |  | 0.001 | V
| 038D | 909 | RO | 355# cell voltage | FLOAT |  |  | V |  | 0.001 | V
| 038F | 911 | RO | 356# cell voltage | FLOAT |  |  | V |  | 0.001 | V
| 391 | 913 | RO | 357# cell voltage | FLOAT |  |  | V |  | 0.001 | V
| 393 | 915 | RO | 358# cell voltage | FLOAT |  |  | V |  | 0.001 | V
| 395 | 917 | RO | 359# cell voltage | FLOAT |  |  | V |  | 0.001 | V
| 397 | 919 | RO | 360# cell voltage | FLOAT |  |  | V |  | 0.001 | V
| 399 | 921 | RO | 361# cell voltage | FLOAT |  |  | V |  | 0.001 | V
| 039B | 923 | RO | 362# cell voltage | FLOAT |  |  | V |  | 0.001 | V
| 039D | 925 | RO | 363# cell voltage | FLOAT |  |  | V |  | 0.001 | V
| 039F | 927 | RO | 364# cell voltage | FLOAT |  |  | V |  | 0.001 | V
| 03A1 | 929 | RO | 365# cell voltage | FLOAT |  |  | V |  | 0.001 | V
| 03A3 | 931 | RO | 366# cell voltage | FLOAT |  |  | V |  | 0.001 | V
| 03A5 | 933 | RO | 367# cell voltage | FLOAT |  |  | V |  | 0.001 | V
| 03A7 | 935 | RO | 368# cell voltage | FLOAT |  |  | V |  | 0.001 | V
| 03A9 | 937 | RO | 369# cell voltage | FLOAT |  |  | V |  | 0.001 | V
| 03AB | 939 | RO | 370# cell voltage | FLOAT |  |  | V |  | 0.001 | V
| 03AD | 941 | RO | 371# cell voltage | FLOAT |  |  | V |  | 0.001 | V
| 03AF | 943 | RO | 372# cell voltage | FLOAT |  |  | V |  | 0.001 | V
| 03B1 | 945 | RO | 373# cell voltage | FLOAT |  |  | V |  | 0.001 | V
| 03B3 | 947 | RO | 374# cell voltage | FLOAT |  |  | V |  | 0.001 | V
| 03B5 | 949 | RO | 375# cell voltage | FLOAT |  |  | V |  | 0.001 | V
| 03B7 | 951 | RO | 376# cell voltage | FLOAT |  |  | V |  | 0.001 | V
| 03B9 | 953 | RO | 377# cell voltage | FLOAT |  |  | V |  | 0.001 | V
| 03BB | 955 | RO | 378# cell voltage | FLOAT |  |  | V |  | 0.001 | V
| 03BD | 957 | RO | 379# cell voltage | FLOAT |  |  | V |  | 0.001 | V
| 03BF | 959 | RO | 380# cell voltage | FLOAT |  |  | V |  | 0.001 | V
| 03C1 | 961 | RO | 381# cell voltage | FLOAT |  |  | V |  | 0.001 | V
| 03C3 | 963 | RO | 382# cell voltage | FLOAT |  |  | V |  | 0.001 | V
| 03C5 | 965 | RO | 383# cell voltage | FLOAT |  |  | V |  | 0.001 | V
| 03C7 | 967 | RO | 384# cell voltage | FLOAT |  |  | V |  | 0.001 | V
| 03C9 | 969 | RO | 385# cell voltage | FLOAT |  |  | V |  | 0.001 | V
| 03CB | 971 | RO | 386# cell voltage | FLOAT |  |  | V |  | 0.001 | V
| 03CD | 973 | RO | 387# cell voltage | FLOAT |  |  | V |  | 0.001 | V
| 03CF | 975 | RO | 388# cell voltage | FLOAT |  |  | V |  | 0.001 | V
| 03D1 | 977 | RO | 389# cell voltage | FLOAT |  |  | V |  | 0.001 | V
| 03D3 | 979 | RO | 390# cell voltage | FLOAT |  |  | V |  | 0.001 | V
| 03D5 | 981 | RO | 391# cell voltage | FLOAT |  |  | V |  | 0.001 | V
| 03D7 | 983 | RO | 392# cell voltage | FLOAT |  |  | V |  | 0.001 | V
| 03D9 | 985 | RO | 393# cell voltage | FLOAT |  |  | V |  | 0.001 | V
| 03DB | 987 | RO | 394# cell voltage | FLOAT |  |  | V |  | 0.001 | V
| 03DD | 989 | RO | 395# cell voltage | FLOAT |  |  | V |  | 0.001 | V
| 03DF | 991 | RO | 396# cell voltage | FLOAT |  |  | V |  | 0.001 | V
| 30 | 993 | RO | 397# cell voltage | FLOAT |  |  | V |  | 0.001 | V
| 3000 | 995 | RO | 398# cell voltage | FLOAT |  |  | V |  | 0.001 | V
| 300000 | 997 | RO | 399# cell voltage | FLOAT |  |  | V |  | 0.001 | V
| 30000000 | 999 | RO | 400# cell voltage | FLOAT |  |  | V |  | 0.001 | V
| 3000000000 | 1001 | RO | 401# cell voltage | FLOAT |  |  | V |  | 0.001 | V
| 03EB | 1003 | RO | 402# cell voltage | FLOAT |  |  | V |  | 0.001 | V
| 03ED | 1005 | RO | 403# cell voltage | FLOAT |  |  | V |  | 0.001 | V
| 03EF | 1007 | RO | 404# cell voltage | FLOAT |  |  | V |  | 0.001 | V
| 03F1 | 1009 | RO | 405# cell voltage | FLOAT |  |  | V |  | 0.001 | V
| 03F3 | 1011 | RO | 406# cell voltage | FLOAT |  |  | V |  | 0.001 | V
| 03F5 | 1013 | RO | 407# cell voltage | FLOAT |  |  | V |  | 0.001 | V
| 03F7 | 1015 | RO | 408# cell voltage | FLOAT |  |  | V |  | 0.001 | V
| 03F9 | 1017 | RO | 409# cell voltage | FLOAT |  |  | V |  | 0.001 | V
| 03FB | 1019 | RO | 410# cell voltage | FLOAT |  |  | V |  | 0.001 | V
| 03FD | 1021 | RO | 411# cell voltage | FLOAT |  |  | V |  | 0.001 | V
| 03FF | 1023 | RO | 412# cell voltage | FLOAT |  |  | V |  | 0.001 | V
| 401 | 1025 | RO | 413# cell voltage | FLOAT |  |  | V |  | 0.001 | V
| 403 | 1027 | RO | 414# cell voltage | FLOAT |  |  | V |  | 0.001 | V
| 405 | 1029 | RO | 415# cell voltage | FLOAT |  |  | V |  | 0.001
| 407 | 1031 | RO | 416# cell voltage | FLOAT |  |  | V |  | 0.001 | V
| 409 | 1033 | RO | reserve | FLOAT
| 040B | 1035 | RO | reserve | FLOAT
| 040D | 1037 | RO | reserve | FLOAT
| 040F | 1039 | RO | reserve | FLOAT
| 411 | 1041 | RO | reserve | FLOAT
| 413 | 1043 | RO | reserve | FLOAT
| 415 | 1045 | RO | reserve | FLOAT
| 417 | 1047 | RO | reserve | FLOAT
| 419 | 1049 | RO | reserve | FLOAT
| 041B | 1051 | RO | reserve | FLOAT
| 041D | 1053 | RO | reserve | FLOAT
| 041F | 1055 | RO | reserve | FLOAT
| 421 | 1057 | RO | reserve | FLOAT
| 423 | 1059 | RO | reserve | FLOAT
| 425 | 1061 | RO | reserve | FLOAT
| 427 | 1063 | RO | reserve | FLOAT
| 429 | 1065 | RO | reserve | FLOAT
| 042B | 1067 | RO | reserve | FLOAT
| 042D | 1069 | RO | reserve | FLOAT
| 042F | 1071 | RO | reserve | FLOAT
| 431 | 1073 | RO | reserve | FLOAT
| 433 | 1075 | RO | reserve | FLOAT
| 435 | 1077 | RO | reserve | FLOAT
| 437 | 1079 | RO | reserve | FLOAT
| 439 | 1081 | RO | reserve | FLOAT
| 043B | 1083 | RO | reserve | FLOAT
| 043D | 1085 | RO | reserve | FLOAT
| 043F | 1087 | RO | reserve | FLOAT
| 441 | 1089 | RO | reserve | FLOAT
| 443 | 1091 | RO | reserve | FLOAT
| 445 | 1093 | RO | reserve | FLOAT
| 447 | 1095 | RO | reserve | FLOAT
| 449 | 1097 | RO | reserve | FLOAT
| 044B | 1099 | RO | reserve | FLOAT
| 044D | 1101 | RO | reserve | FLOAT
| 044F | 1103 | RO | reserve | FLOAT
| 451 | 1105 | RO | reserve | FLOAT
| 453 | 1107 | RO | reserve | FLOAT
| 455 | 1109 | RO | reserve | FLOAT
| 457 | 1111 | RO | reserve | FLOAT
| 459 | 1113 | RO | reserve | FLOAT
| 045B | 1115 | RO | reserve | FLOAT
| 045D | 1117 | RO | reserve | FLOAT
| 045F | 1119 | RO | reserve | FLOAT
| 461 | 1121 | RO | reserve | FLOAT
| 463 | 1123 | RO | reserve | FLOAT
| 465 | 1125 | RO | reserve | FLOAT
| 467 | 1127 | RO | reserve | FLOAT
| 469 | 1129 | RO | reserve | FLOAT
| 046B | 1131 | RO | reserve | FLOAT
| 046D | 1133 | RO | reserve | FLOAT
| 046F | 1135 | RO | reserve | FLOAT
| 471 | 1137 | RO | reserve | FLOAT
| 473 | 1139 | RO | reserve | FLOAT
| 475 | 1141 | RO | reserve | FLOAT
| 477 | 1143 | RO | reserve | FLOAT
| 479 | 1145 | RO | reserve | FLOAT
| 047B | 1147 | RO | reserve | FLOAT
| 047D | 1149 | RO | reserve | FLOAT
| 047F | 1151 | RO | reserve | FLOAT
| 481 | 1153 | RO | reserve | FLOAT
| 483 | 1155 | RO | reserve | FLOAT
| 485 | 1157 | RO | reserve | FLOAT
| 487 | 1159 | RO | reserve | FLOAT
| 489 | 1161 | RO | reserve | FLOAT
| 048B | 1163 | RO | reserve | FLOAT
| 048D | 1165 | RO | reserve | FLOAT
| 048F | 1167 | RO | reserve | FLOAT
| 491 | 1169 | RO | reserve | FLOAT
| 493 | 1171 | RO | reserve | FLOAT
| 495 | 1173 | RO | reserve | FLOAT
| 497 | 1175 | RO | reserve | FLOAT
| 499 | 1177 | RO | reserve | FLOAT
| 049B | 1179 | RO | reserve | FLOAT
| 049D | 1181 | RO | reserve | FLOAT
| 049F | 1183 | RO | reserve | FLOAT
| 04A1 | 1185 | RO | reserve | FLOAT
| 04A3 | 1187 | RO | reserve | FLOAT
| 04A5 | 1189 | RO | reserve | FLOAT
| 04A7 | 1191 | RO | reserve | FLOAT
| 04A9 | 1193 | RO | reserve | FLOAT
| 04AB | 1195 | RO | reserve | FLOAT
| 04AD | 1197 | RO | reserve | FLOAT
| 04AF | 1199 | RO | reserve | FLOAT
| 04B1 | 1201 | RO | reserve | FLOAT
| 04B3 | 1203 | RO | reserve | FLOAT
| 04B5 | 1205 | RO | reserve | FLOAT
| 04B7 | 1207 | RO | reserve | FLOAT
| 04B9 | 1209 | RO | reserve | FLOAT
| 04BB | 1211 | RO | reserve | FLOAT
| 04BD | 1213 | RO | reserve | FLOAT
| 04BF | 1215 | RO | reserve | FLOAT
| 04C1 | 1217 | RO | reserve | FLOAT
| 04C3 | 1219 | RO | reserve | FLOAT
| 04C5 | 1221 | RO | reserve | FLOAT
| 04C7 | 1223 | RO | reserve | FLOAT
| 04C9 | 1225 | RO | reserve | FLOAT
| 04CB | 1227 | RO | reserve | FLOAT
| 04CD | 1229 | RO | reserve | FLOAT
| 04CF | 1231 | RO | reserve | FLOAT
| 04D1 | 1233 | RO | reserve | FLOAT
| 04D3 | 1235 | RO | reserve | FLOAT
| 04D5 | 1237 | RO | reserve | FLOAT
| 04D7 | 1239 | RO | reserve | FLOAT
| 04D9 | 1241 | RO | reserve | FLOAT
| 04DB | 1243 | RO | reserve | FLOAT
| 04DD | 1245 | RO | reserve | FLOAT
| 04DF | 1247 | RO | reserve | FLOAT
| 40 | 1249 | RO | reserve | FLOAT
| 4000 | 1251 | RO | reserve | FLOAT
| 400000 | 1253 | RO | reserve | FLOAT
| 40000000 | 1255 | RO | reserve | FLOAT
| 4000000000 | 1257 | RO | reserve | FLOAT
| 04EB | 1259 | RO | reserve | FLOAT
| 04ED | 1261 | RO | reserve | FLOAT
| 04EF | 1263 | RO | reserve | FLOAT
| 04F1 | 1265 | RO | reserve | FLOAT
| 04F3 | 1267 | RO | reserve | FLOAT
| 04F5 | 1269 | RO | reserve | FLOAT
| 04F7 | 1271 | RO | reserve | FLOAT
| 04F9 | 1273 | RO | reserve | FLOAT
| 04FB | 1275 | RO | reserve | FLOAT
| 04FD | 1277 | RO | reserve | FLOAT
| 04FF | 1279 | RO | reserve | FLOAT
| 501 | 1281 | RO | reserve | FLOAT
| 503 | 1283 | RO | reserve | FLOAT
| 505 | 1285 | RO | reserve | FLOAT
| 507 | 1287 | RO | reserve | FLOAT
| 509 | 1289 | RO | reserve | FLOAT
| 050B | 1291 | RO | reserve | FLOAT
| 050D | 1293 | RO | reserve | FLOAT
| 050F | 1295 | RO | reserve | FLOAT
| 511 | 1297 | RO | reserve | FLOAT
| 513 | 1299 | RO | reserve | FLOAT
| 515 | 1301 | RO | reserve | FLOAT
| 517 | 1303 | RO | reserve | FLOAT
| 519 | 1305 | RO | reserve | FLOAT
| 051B | 1307 | RO | reserve | FLOAT
| 051D | 1309 | RO | reserve | FLOAT
| 051F | 1311 | RO | reserve | FLOAT
| 521 | 1313 | RO | reserve | FLOAT
| 523 | 1315 | RO | reserve | FLOAT
| 525 | 1317 | RO | reserve | FLOAT
| 527 | 1319 | RO | reserve | FLOAT
| 529 | 1321 | RO | reserve | FLOAT
| 052B | 1323 | RO | reserve | FLOAT
| 052D | 1325 | RO | reserve | FLOAT
| 052F | 1327 | RO | reserve | FLOAT
| 531 | 1329 | RO | reserve | FLOAT
| 533 | 1331 | RO | reserve | FLOAT
| 535 | 1333 | RO | reserve | FLOAT
| 537 | 1335 | RO | reserve | FLOAT
| 539 | 1337 | RO | reserve | FLOAT
| 053B | 1339 | RO | reserve | FLOAT
| 053D | 1341 | RO | reserve | FLOAT
| 053F | 1343 | RO | reserve | FLOAT
| 541 | 1345 | RO | reserve | FLOAT
| 543 | 1347 | RO | reserve | FLOAT
| 545 | 1349 | RO | reserve | FLOAT
| 547 | 1351 | RO | reserve | FLOAT
| 549 | 1353 | RO | reserve | FLOAT
| 054B | 1355 | RO | reserve | FLOAT
| 054D | 1357 | RO | reserve | FLOAT
| 054F | 1359 | RO | reserve | FLOAT
| 551 | 1361 | RO | reserve | FLOAT
| 553 | 1363 | RO | reserve | FLOAT
| 555 | 1365 | RO | reserve | FLOAT
| 557 | 1367 | RO | reserve | FLOAT
| 559 | 1369 | RO | reserve | FLOAT
| 055B | 1371 | RO | reserve | FLOAT
| 055D | 1373 | RO | reserve | FLOAT
| 055F | 1375 | RO | reserve | FLOAT
| 561 | 1377 | RO | reserve | FLOAT
| 563 | 1379 | RO | reserve | FLOAT
| 565 | 1381 | RO | reserve | FLOAT
| 567 | 1383 | RO | reserve | FLOAT
| 569 | 1385 | RO | reserve | FLOAT
| 056B | 1387 | RO | reserve | FLOAT
| 056D | 1389 | RO | reserve | FLOAT
| 056F | 1391 | RO | reserve | FLOAT
| 571 | 1393 | RO | reserve | FLOAT
| 573 | 1395 | RO | reserve | FLOAT
| 575 | 1397 | RO | reserve | FLOAT
| 577 | 1399 | RO | reserve | FLOAT

## Cell SOC
Register Type | Register Address |  | Attributes | Meaning | Data Types | Coefficient | Offset | Units | Remarks | Decimal pointPrecision required | Units
| Hexadecimal | Decimal
Cell SOC data (Each rack Modbus address independent, starting from 2, discrete input registers,function code 0x04, same Modbus address as rack data, same function code, different register addresses) | 0A29 | 2601 | RO | 1# cell SOC | FLOAT | 1 | 0 | % | cell SOC | 1 | %
| 0A2B | 2603 | RO | 2# cell SOC | FLOAT | 1 | 0 | % |  | 1 | %
| 0A2D | 2605 | RO | 3# cell SOC | FLOAT | 1 | 0 | % |  | 1 | %
| 0A2F | 2607 | RO | 4# cell SOC | FLOAT | 1 | 0 | % |  | 1 | %
| 0A31 | 2609 | RO | 5# cell SOC | FLOAT | 1 | 0 | % |  | 1 | %
| 0A33 | 2611 | RO | 6# cell SOC | FLOAT | 1 | 0 | % |  | 1 | %
| 0A35 | 2613 | RO | 7# cell SOC | FLOAT | 1 | 0 | % |  | 1 | %
| 0A37 | 2615 | RO | 8# cell SOC | FLOAT | 1 | 0 | % |  | 1 | %
| 0A39 | 2617 | RO | 9# cell SOC | FLOAT | 1 | 0 | % |  | 1 | %
| 0A3B | 2619 | RO | 10# cell SOC | FLOAT | 1 | 0 | % |  | 1 | %
| 0A3D | 2621 | RO | 11# cell SOC | FLOAT | 1 | 0 | % |  | 1 | %
| 0A3F | 2623 | RO | 12# cell SOC | FLOAT | 1 | 0 | % |  | 1 | %
| 0A41 | 2625 | RO | 13# cell SOC | FLOAT | 1 | 0 | % |  | 1 | %
| 0A43 | 2627 | RO | 14# cell SOC | FLOAT | 1 | 0 | % |  | 1 | %
| 0A45 | 2629 | RO | 15# cell SOC | FLOAT | 1 | 0 | % |  | 1 | %
| 0A47 | 2631 | RO | 16# cell SOC | FLOAT | 1 | 0 | % |  | 1 | %
| 0A49 | 2633 | RO | 17# cell SOC | FLOAT | 1 | 0 | % |  | 1 | %
| 0A4B | 2635 | RO | 18# cell SOC | FLOAT | 1 | 0 | % |  | 1 | %
| 0A4D | 2637 | RO | 19# cell SOC | FLOAT | 1 | 0 | % |  | 1 | %
| 0A4F | 2639 | RO | 20# cell SOC | FLOAT | 1 | 0 | % |  | 1 | %
| 0A51 | 2641 | RO | 21# cell SOC | FLOAT | 1 | 0 | % |  | 1 | %
| 0A53 | 2643 | RO | 22# cell SOC | FLOAT | 1 | 0 | % |  | 1 | %
| 0A55 | 2645 | RO | 23# cell SOC | FLOAT | 1 | 0 | % |  | 1 | %
| 0A57 | 2647 | RO | 24# cell SOC | FLOAT | 1 | 0 | % |  | 1 | %
| 0A59 | 2649 | RO | 25# cell SOC | FLOAT | 1 | 0 | % |  | 1 | %
| 0A5B | 2651 | RO | 26# cell SOC | FLOAT | 1 | 0 | % |  | 1 | %
| 0A5D | 2653 | RO | 27# cell SOC | FLOAT | 1 | 0 | % |  | 1 | %
| 0A5F | 2655 | RO | 28# cell SOC | FLOAT | 1 | 0 | % |  | 1 | %
| 0A61 | 2657 | RO | 29# cell SOC | FLOAT | 1 | 0 | % |  | 1 | %
| 0A63 | 2659 | RO | 30# cell SOC | FLOAT | 1 | 0 | % |  | 1 | %
| 0A65 | 2661 | RO | 31# cell SOC | FLOAT | 1 | 0 | % |  | 1 | %
| 0A67 | 2663 | RO | 32# cell SOC | FLOAT | 1 | 0 | % |  | 1 | %
| 0A69 | 2665 | RO | 33# cell SOC | FLOAT | 1 | 0 | % |  | 1 | %
| 0A6B | 2667 | RO | 34# cell SOC | FLOAT | 1 | 0 | % |  | 1 | %
| 0A6D | 2669 | RO | 35# cell SOC | FLOAT | 1 | 0 | % |  | 1 | %
| 0A6F | 2671 | RO | 36# cell SOC | FLOAT | 1 | 0 | % |  | 1 | %
| 0A71 | 2673 | RO | 37# cell SOC | FLOAT | 1 | 0 | % |  | 1 | %
| 0A73 | 2675 | RO | 38# cell SOC | FLOAT | 1 | 0 | % |  | 1 | %
| 0A75 | 2677 | RO | 39# cell SOC | FLOAT | 1 | 0 | % |  | 1 | %
| 0A77 | 2679 | RO | 40# cell SOC | FLOAT | 1 | 0 | % |  | 1 | %
| 0A79 | 2681 | RO | 41# cell SOC | FLOAT | 1 | 0 | % |  | 1 | %
| 0A7B | 2683 | RO | 42# cell SOC | FLOAT | 1 | 0 | % |  | 1 | %
| 0A7D | 2685 | RO | 43# cell SOC | FLOAT | 1 | 0 | % |  | 1 | %
| 0A7F | 2687 | RO | 44# cell SOC | FLOAT | 1 | 0 | % |  | 1 | %
| 0A81 | 2689 | RO | 45# cell SOC | FLOAT | 1 | 0 | % |  | 1 | %
| 0A83 | 2691 | RO | 46# cell SOC | FLOAT | 1 | 0 | % |  | 1 | %
| 0A85 | 2693 | RO | 47# cell SOC | FLOAT | 1 | 0 | % |  | 1 | %
| 0A87 | 2695 | RO | 48# cell SOC | FLOAT | 1 | 0 | % |  | 1 | %
| 0A89 | 2697 | RO | 49# cell SOC | FLOAT | 1 | 0 | % |  | 1 | %
| 0A8B | 2699 | RO | 50# cell SOC | FLOAT | 1 | 0 | % |  | 1 | %
| 0A8D | 2701 | RO | 51# cell SOC | FLOAT | 1 | 0 | % |  | 1 | %
| 0A8F | 2703 | RO | 52# cell SOC | FLOAT | 1 | 0 | % |  | 1 | %
| 0A91 | 2705 | RO | 53# cell SOC | FLOAT | 1 | 0 | % |  | 1 | %
| 0A93 | 2707 | RO | 54# cell SOC | FLOAT | 1 | 0 | % |  | 1 | %
| 0A95 | 2709 | RO | 55# cell SOC | FLOAT | 1 | 0 | % |  | 1 | %
| 0A97 | 2711 | RO | 56# cell SOC | FLOAT | 1 | 0 | % |  | 1 | %
| 0A99 | 2713 | RO | 57# cell SOC | FLOAT | 1 | 0 | % |  | 1 | %
| 0A9B | 2715 | RO | 58# cell SOC | FLOAT | 1 | 0 | % |  | 1 | %
| 0A9D | 2717 | RO | 59# cell SOC | FLOAT | 1 | 0 | % |  | 1 | %
| 0A9F | 2719 | RO | 60# cell SOC | FLOAT | 1 | 0 | % |  | 1 | %
| 0AA1 | 2721 | RO | 61# cell SOC | FLOAT | 1 | 0 | % |  | 1 | %
| 0AA3 | 2723 | RO | 62# cell SOC | FLOAT | 1 | 0 | % |  | 1 | %
| 0AA5 | 2725 | RO | 63# cell SOC | FLOAT | 1 | 0 | % |  | 1 | %
| 0AA7 | 2727 | RO | 64# cell SOC | FLOAT | 1 | 0 | % |  | 1 | %
| 0AA9 | 2729 | RO | 65# cell SOC | FLOAT | 1 | 0 | % |  | 1 | %
| 0AAB | 2731 | RO | 66# cell SOC | FLOAT | 1 | 0 | % |  | 1 | %
| 0AAD | 2733 | RO | 67# cell SOC | FLOAT | 1 | 0 | % |  | 1 | %
| 0AAF | 2735 | RO | 68# cell SOC | FLOAT | 1 | 0 | % |  | 1 | %
| 0AB1 | 2737 | RO | 69# cell SOC | FLOAT | 1 | 0 | % |  | 1 | %
| 0AB3 | 2739 | RO | 70# cell SOC | FLOAT | 1 | 0 | % |  | 1 | %
| 0AB5 | 2741 | RO | 71# cell SOC | FLOAT | 1 | 0 | % |  | 1 | %
| 0AB7 | 2743 | RO | 72# cell SOC | FLOAT | 1 | 0 | % |  | 1 | %
| 0AB9 | 2745 | RO | 73# cell SOC | FLOAT | 1 | 0 | % |  | 1 | %
| 0ABB | 2747 | RO | 74# cell SOC | FLOAT | 1 | 0 | % |  | 1 | %
| 0ABD | 2749 | RO | 75# cell SOC | FLOAT | 1 | 0 | % |  | 1 | %
| 0ABF | 2751 | RO | 76# cell SOC | FLOAT | 1 | 0 | % |  | 1 | %
| 0AC1 | 2753 | RO | 77# cell SOC | FLOAT | 1 | 0 | % |  | 1 | %
| 0AC3 | 2755 | RO | 78# cell SOC | FLOAT | 1 | 0 | % |  | 1 | %
| 0AC5 | 2757 | RO | 79# cell SOC | FLOAT | 1 | 0 | % |  | 1 | %
| 0AC7 | 2759 | RO | 80# cell SOC | FLOAT | 1 | 0 | % |  | 1 | %
| 0AC9 | 2761 | RO | 81# cell SOC | FLOAT | 1 | 0 | % |  | 1 | %
| 0ACB | 2763 | RO | 82# cell SOC | FLOAT | 1 | 0 | % |  | 1 | %
| 0ACD | 2765 | RO | 83# cell SOC | FLOAT | 1 | 0 | % |  | 1 | %
| 0ACF | 2767 | RO | 84# cell SOC | FLOAT | 1 | 0 | % |  | 1 | %
| 0AD1 | 2769 | RO | 85# cell SOC | FLOAT | 1 | 0 | % |  | 1 | %
| 0AD3 | 2771 | RO | 86# cell SOC | FLOAT | 1 | 0 | % |  | 1 | %
| 0AD5 | 2773 | RO | 87# cell SOC | FLOAT | 1 | 0 | % |  | 1 | %
| 0AD7 | 2775 | RO | 88# cell SOC | FLOAT | 1 | 0 | % |  | 1 | %
| 0AD9 | 2777 | RO | 89# cell SOC | FLOAT | 1 | 0 | % |  | 1 | %
| 0ADB | 2779 | RO | 90# cell SOC | FLOAT | 1 | 0 | % |  | 1 | %
| 0ADD | 2781 | RO | 91# cell SOC | FLOAT | 1 | 0 | % |  | 1 | %
| 0ADF | 2783 | RO | 92# cell SOC | FLOAT | 1 | 0 | % |  | 1 | %
| 0AE1 | 2785 | RO | 93# cell SOC | FLOAT | 1 | 0 | % |  | 1 | %
| 0AE3 | 2787 | RO | 94# cell SOC | FLOAT | 1 | 0 | % |  | 1 | %
| 0AE5 | 2789 | RO | 95# cell SOC | FLOAT | 1 | 0 | % |  | 1 | %
| 0AE7 | 2791 | RO | 96# cell SOC | FLOAT | 1 | 0 | % |  | 1 | %
| 0AE9 | 2793 | RO | 97# cell SOC | FLOAT | 1 | 0 | % |  | 1 | %
| 0AEB | 2795 | RO | 98# cell SOC | FLOAT | 1 | 0 | % |  | 1 | %
| 0AED | 2797 | RO | 99# cell SOC | FLOAT | 1 | 0 | % |  | 1 | %
| 0AEF | 2799 | RO | 100# cell SOC | FLOAT | 1 | 0 | % |  | 1 | %
| 0AF1 | 2801 | RO | 101# cell SOC | FLOAT | 1 | 0 | % |  | 1 | %
| 0AF3 | 2803 | RO | 102# cell SOC | FLOAT | 1 | 0 | % |  | 1 | %
| 0AF5 | 2805 | RO | 103# cell SOC | FLOAT | 1 | 0 | % |  | 1 | %
| 0AF7 | 2807 | RO | 104# cell SOC | FLOAT | 1 | 0 | % |  | 1 | %
| 0AF9 | 2809 | RO | 105# cell SOC | FLOAT | 1 | 0 | % |  | 1 | %
| 0AFB | 2811 | RO | 106# cell SOC | FLOAT | 1 | 0 | % |  | 1 | %
| 0AFD | 2813 | RO | 107# cell SOC | FLOAT | 1 | 0 | % |  | 1 | %
| 0AFF | 2815 | RO | 108# cell SOC | FLOAT | 1 | 0 | % |  | 1 | %
| 0B01 | 2817 | RO | 109# cell SOC | FLOAT | 1 | 0 | % |  | 1 | %
| 0B03 | 2819 | RO | 110# cell SOC | FLOAT | 1 | 0 | % |  | 1 | %
| 0B05 | 2821 | RO | 111# cell SOC | FLOAT | 1 | 0 | % |  | 1 | %
| 0B07 | 2823 | RO | 112# cell SOC | FLOAT | 1 | 0 | % |  | 1 | %
| 0B09 | 2825 | RO | 113# cell SOC | FLOAT | 1 | 0 | % |  | 1 | %
| 0B0B | 2827 | RO | 114# cell SOC | FLOAT | 1 | 0 | % |  | 1 | %
| 0B0D | 2829 | RO | 115# cell SOC | FLOAT | 1 | 0 | % |  | 1 | %
| 0B0F | 2831 | RO | 116# cell SOC | FLOAT | 1 | 0 | % |  | 1 | %
| 0B11 | 2833 | RO | 117# cell SOC | FLOAT | 1 | 0 | % |  | 1 | %
| 0B13 | 2835 | RO | 118# cell SOC | FLOAT | 1 | 0 | % |  | 1 | %
| 0B15 | 2837 | RO | 119# cell SOC | FLOAT | 1 | 0 | % |  | 1 | %
| 0B17 | 2839 | RO | 120# cell SOC | FLOAT | 1 | 0 | % |  | 1 | %
| 0B19 | 2841 | RO | 121# cell SOC | FLOAT | 1 | 0 | % |  | 1 | %
| 0B1B | 2843 | RO | 122# cell SOC | FLOAT | 1 | 0 | % |  | 1 | %
| 0B1D | 2845 | RO | 123# cell SOC | FLOAT | 1 | 0 | % |  | 1 | %
| 0B1F | 2847 | RO | 124# cell SOC | FLOAT | 1 | 0 | % |  | 1 | %
| 0B21 | 2849 | RO | 125# cell SOC | FLOAT | 1 | 0 | % |  | 1 | %
| 0B23 | 2851 | RO | 126# cell SOC | FLOAT | 1 | 0 | % |  | 1 | %
| 0B25 | 2853 | RO | 127# cell SOC | FLOAT | 1 | 0 | % |  | 1 | %
| 0B27 | 2855 | RO | 128# cell SOC | FLOAT | 1 | 0 | % |  | 1 | %
| 0B29 | 2857 | RO | 129# cell SOC | FLOAT | 1 | 0 | % |  | 1 | %
| 0B2B | 2859 | RO | 130# cell SOC | FLOAT | 1 | 0 | % |  | 1 | %
| 0B2D | 2861 | RO | 131# cell SOC | FLOAT | 1 | 0 | % |  | 1 | %
| 0B2F | 2863 | RO | 132# cell SOC | FLOAT | 1 | 0 | % |  | 1 | %
| 0B31 | 2865 | RO | 133# cell SOC | FLOAT | 1 | 0 | % |  | 1 | %
| 0B33 | 2867 | RO | 134# cell SOC | FLOAT | 1 | 0 | % |  | 1 | %
| 0B35 | 2869 | RO | 135# cell SOC | FLOAT | 1 | 0 | % |  | 1 | %
| 0B37 | 2871 | RO | 136# cell SOC | FLOAT | 1 | 0 | % |  | 1 | %
| 0B39 | 2873 | RO | 137# cell SOC | FLOAT | 1 | 0 | % |  | 1 | %
| 0B3B | 2875 | RO | 138# cell SOC | FLOAT | 1 | 0 | % |  | 1 | %
| 0B3D | 2877 | RO | 139# cell SOC | FLOAT | 1 | 0 | % |  | 1 | %
| 0B3F | 2879 | RO | 140# cell SOC | FLOAT | 1 | 0 | % |  | 1 | %
| 0B41 | 2881 | RO | 141# cell SOC | FLOAT | 1 | 0 | % |  | 1 | %
| 0B43 | 2883 | RO | 142# cell SOC | FLOAT | 1 | 0 | % |  | 1 | %
| 0B45 | 2885 | RO | 143# cell SOC | FLOAT | 1 | 0 | % |  | 1 | %
| 0B47 | 2887 | RO | 144# cell SOC | FLOAT | 1 | 0 | % |  | 1 | %
| 0B49 | 2889 | RO | 145# cell SOC | FLOAT | 1 | 0 | % |  | 1 | %
| 0B4B | 2891 | RO | 146# cell SOC | FLOAT | 1 | 0 | % |  | 1 | %
| 0B4D | 2893 | RO | 147# cell SOC | FLOAT | 1 | 0 | % |  | 1 | %
| 0B4F | 2895 | RO | 148# cell SOC | FLOAT | 1 | 0 | % |  | 1 | %
| 0B51 | 2897 | RO | 149# cell SOC | FLOAT | 1 | 0 | % |  | 1 | %
| 0B53 | 2899 | RO | 150# cell SOC | FLOAT | 1 | 0 | % |  | 1 | %
| 0B55 | 2901 | RO | 151# cell SOC | FLOAT | 1 | 0 | % |  | 1 | %
| 0B57 | 2903 | RO | 152# cell SOC | FLOAT | 1 | 0 | % |  | 1 | %
| 0B59 | 2905 | RO | 153# cell SOC | FLOAT | 1 | 0 | % |  | 1 | %
| 0B5B | 2907 | RO | 154# cell SOC | FLOAT | 1 | 0 | % |  | 1 | %
| 0B5D | 2909 | RO | 155# cell SOC | FLOAT | 1 | 0 | % |  | 1 | %
| 0B5F | 2911 | RO | 156# cell SOC | FLOAT | 1 | 0 | % |  | 1 | %
| 0B61 | 2913 | RO | 157# cell SOC | FLOAT | 1 | 0 | % |  | 1 | %
| 0B63 | 2915 | RO | 158# cell SOC | FLOAT | 1 | 0 | % |  | 1 | %
| 0B65 | 2917 | RO | 159# cell SOC | FLOAT | 1 | 0 | % |  | 1 | %
| 0B67 | 2919 | RO | 160# cell SOC | FLOAT | 1 | 0 | % |  | 1 | %
| 0B69 | 2921 | RO | 161# cell SOC | FLOAT | 1 | 0 | % |  | 1 | %
| 0B6B | 2923 | RO | 162# cell SOC | FLOAT | 1 | 0 | % |  | 1 | %
| 0B6D | 2925 | RO | 163# cell SOC | FLOAT | 1 | 0 | % |  | 1 | %
| 0B6F | 2927 | RO | 164# cell SOC | FLOAT | 1 | 0 | % |  | 1 | %
| 0B71 | 2929 | RO | 165# cell SOC | FLOAT | 1 | 0 | % |  | 1 | %
| 0B73 | 2931 | RO | 166# cell SOC | FLOAT | 1 | 0 | % |  | 1 | %
| 0B75 | 2933 | RO | 167# cell SOC | FLOAT | 1 | 0 | % |  | 1 | %
| 0B77 | 2935 | RO | 168# cell SOC | FLOAT | 1 | 0 | % |  | 1 | %
| 0B79 | 2937 | RO | 169# cell SOC | FLOAT | 1 | 0 | % |  | 1 | %
| 0B7B | 2939 | RO | 170# cell SOC | FLOAT | 1 | 0 | % |  | 1 | %
| 0B7D | 2941 | RO | 171# cell SOC | FLOAT | 1 | 0 | % |  | 1 | %
| 0B7F | 2943 | RO | 172# cell SOC | FLOAT | 1 | 0 | % |  | 1 | %
| 0B81 | 2945 | RO | 173# cell SOC | FLOAT | 1 | 0 | % |  | 1 | %
| 0B83 | 2947 | RO | 174# cell SOC | FLOAT | 1 | 0 | % |  | 1 | %
| 0B85 | 2949 | RO | 175# cell SOC | FLOAT | 1 | 0 | % |  | 1 | %
| 0B87 | 2951 | RO | 176# cell SOC | FLOAT | 1 | 0 | % |  | 1 | %
| 0B89 | 2953 | RO | 177# cell SOC | FLOAT | 1 | 0 | % |  | 1 | %
| 0B8B | 2955 | RO | 178# cell SOC | FLOAT | 1 | 0 | % |  | 1 | %
| 0B8D | 2957 | RO | 179# cell SOC | FLOAT | 1 | 0 | % |  | 1 | %
| 0B8F | 2959 | RO | 180# cell SOC | FLOAT | 1 | 0 | % |  | 1 | %
| 0B91 | 2961 | RO | 181# cell SOC | FLOAT | 1 | 0 | % |  | 1 | %
| 0B93 | 2963 | RO | 182# cell SOC | FLOAT | 1 | 0 | % |  | 1 | %
| 0B95 | 2965 | RO | 183# cell SOC | FLOAT | 1 | 0 | % |  | 1 | %
| 0B97 | 2967 | RO | 184# cell SOC | FLOAT | 1 | 0 | % |  | 1 | %
| 0B99 | 2969 | RO | 185# cell SOC | FLOAT | 1 | 0 | % |  | 1 | %
| 0B9B | 2971 | RO | 186# cell SOC | FLOAT | 1 | 0 | % |  | 1 | %
| 0B9D | 2973 | RO | 187# cell SOC | FLOAT | 1 | 0 | % |  | 1 | %
| 0B9F | 2975 | RO | 188# cell SOC | FLOAT | 1 | 0 | % |  | 1 | %
| 0BA1 | 2977 | RO | 189# cell SOC | FLOAT | 1 | 0 | % |  | 1 | %
| 0BA3 | 2979 | RO | 190# cell SOC | FLOAT | 1 | 0 | % |  | 1 | %
| 0BA5 | 2981 | RO | 191# cell SOC | FLOAT | 1 | 0 | % |  | 1 | %
| 0BA7 | 2983 | RO | 192# cell SOC | FLOAT | 1 | 0 | % |  | 1 | %
| 0BA9 | 2985 | RO | 193# cell SOC | FLOAT | 1 | 0 | % |  | 1 | %
| 0BAB | 2987 | RO | 194# cell SOC | FLOAT | 1 | 0 | % |  | 1 | %
| 0BAD | 2989 | RO | 195# cell SOC | FLOAT | 1 | 0 | % |  | 1 | %
| 0BAF | 2991 | RO | 196# cell SOC | FLOAT | 1 | 0 | % |  | 1 | %
| 0BB1 | 2993 | RO | 197# cell SOC | FLOAT | 1 | 0 | % |  | 1 | %
| 0BB3 | 2995 | RO | 198# cell SOC | FLOAT | 1 | 0 | % |  | 1 | %
| 0BB5 | 2997 | RO | 199# cell SOC | FLOAT | 1 | 0 | % |  | 1 | %
| 0BB7 | 2999 | RO | 200# cell SOC | FLOAT | 1 | 0 | % |  | 1 | %
| 0BB9 | 3001 | RO | 201# cell SOC | FLOAT | 1 | 0 | % |  | 1 | %
| 0BBB | 3003 | RO | 202# cell SOC | FLOAT | 1 | 0 | % |  | 1 | %
| 0BBD | 3005 | RO | 203# cell SOC | FLOAT | 1 | 0 | % |  | 1 | %
| 0BBF | 3007 | RO | 204# cell SOC | FLOAT | 1 | 0 | % |  | 1 | %
| 0BC1 | 3009 | RO | 205# cell SOC | FLOAT | 1 | 0 | % |  | 1 | %
| 0BC3 | 3011 | RO | 206# cell SOC | FLOAT | 1 | 0 | % |  | 1 | %
| 0BC5 | 3013 | RO | 207# cell SOC | FLOAT | 1 | 0 | % |  | 1 | %
| 0BC7 | 3015 | RO | 208# cell SOC | FLOAT | 1 | 0 | % |  | 1 | %
| 0BC9 | 3017 | RO | 209# cell SOC | FLOAT | 1 | 0 | % |  | 1 | %
| 0BCB | 3019 | RO | 210# cell SOC | FLOAT | 1 | 0 | % |  | 1 | %
| 0BCD | 3021 | RO | 211# cell SOC | FLOAT | 1 | 0 | % |  | 1 | %
| 0BCF | 3023 | RO | 212# cell SOC | FLOAT | 1 | 0 | % |  | 1 | %
| 0BD1 | 3025 | RO | 213# cell SOC | FLOAT | 1 | 0 | % |  | 1 | %
| 0BD3 | 3027 | RO | 214# cell SOC | FLOAT | 1 | 0 | % |  | 1 | %
| 0BD5 | 3029 | RO | 215# cell SOC | FLOAT | 1 | 0 | % |  | 1 | %
| 0BD7 | 3031 | RO | 216# cell SOC | FLOAT | 1 | 0 | % |  | 1 | %
| 0BD9 | 3033 | RO | 217# cell SOC | FLOAT | 1 | 0 | % |  | 1 | %
| 0BDB | 3035 | RO | 218# cell SOC | FLOAT | 1 | 0 | % |  | 1 | %
| 0BDD | 3037 | RO | 219# cell SOC | FLOAT | 1 | 0 | % |  | 1 | %
| 0BDF | 3039 | RO | 220# cell SOC | FLOAT | 1 | 0 | % |  | 1 | %
| 0BE1 | 3041 | RO | 221# cell SOC | FLOAT | 1 | 0 | % |  | 1 | %
| 0BE3 | 3043 | RO | 222# cell SOC | FLOAT | 1 | 0 | % |  | 1 | %
| 0BE5 | 3045 | RO | 223# cell SOC | FLOAT | 1 | 0 | % |  | 1 | %
| 0BE7 | 3047 | RO | 224# cell SOC | FLOAT | 1 | 0 | % |  | 1 | %
| 0BE9 | 3049 | RO | 225# cell SOC | FLOAT | 1 | 0 | % |  | 1 | %
| 0BEB | 3051 | RO | 226# cell SOC | FLOAT | 1 | 0 | % |  | 1 | %
| 0BED | 3053 | RO | 227# cell SOC | FLOAT | 1 | 0 | % |  | 1 | %
| 0BEF | 3055 | RO | 228# cell SOC | FLOAT | 1 | 0 | % |  | 1 | %
| 0BF1 | 3057 | RO | 229# cell SOC | FLOAT | 1 | 0 | % |  | 1 | %
| 0BF3 | 3059 | RO | 230# cell SOC | FLOAT | 1 | 0 | % |  | 1 | %
| 0BF5 | 3061 | RO | 231# cell SOC | FLOAT | 1 | 0 | % |  | 1 | %
| 0BF7 | 3063 | RO | 232# cell SOC | FLOAT | 1 | 0 | % |  | 1 | %
| 0BF9 | 3065 | RO | 233# cell SOC | FLOAT | 1 | 0 | % |  | 1 | %
| 0BFB | 3067 | RO | 234# cell SOC | FLOAT | 1 | 0 | % |  | 1 | %
| 0BFD | 3069 | RO | 235# cell SOC | FLOAT | 1 | 0 | % |  | 1 | %
| 0BFF | 3071 | RO | 236# cell SOC | FLOAT | 1 | 0 | % |  | 1 | %
| 0C01 | 3073 | RO | 237# cell SOC | FLOAT | 1 | 0 | % |  | 1 | %
| 0C03 | 3075 | RO | 238# cell SOC | FLOAT | 1 | 0 | % |  | 1 | %
| 0C05 | 3077 | RO | 239# cell SOC | FLOAT | 1 | 0 | % |  | 1 | %
| 0C07 | 3079 | RO | 240# cell SOC | FLOAT | 1 | 0 | % |  | 1 | %
| 0C09 | 3081 | RO | 241# cell SOC | FLOAT | 1 | 0 | % |  | 1 | %
| 0C0B | 3083 | RO | 242# cell SOC | FLOAT | 1 | 0 | % |  | 1 | %
| 0C0D | 3085 | RO | 243# cell SOC | FLOAT | 1 | 0 | % |  | 1 | %
| 0C0F | 3087 | RO | 244# cell SOC | FLOAT | 1 | 0 | % |  | 1 | %
| 0C11 | 3089 | RO | 245# cell SOC | FLOAT | 1 | 0 | % |  | 1 | %
| 0C13 | 3091 | RO | 246# cell SOC | FLOAT | 1 | 0 | % |  | 1 | %
| 0C15 | 3093 | RO | 247# cell SOC | FLOAT | 1 | 0 | % |  | 1 | %
| 0C17 | 3095 | RO | 248# cell SOC | FLOAT | 1 | 0 | % |  | 1 | %
| 0C19 | 3097 | RO | 249# cell SOC | FLOAT | 1 | 0 | % |  | 1 | %
| 0C1B | 3099 | RO | 250# cell SOC | FLOAT | 1 | 0 | % |  | 1 | %
| 0C1D | 3101 | RO | 251# cell SOC | FLOAT | 1 | 0 | % |  | 1 | %
| 0C1F | 3103 | RO | 252# cell SOC | FLOAT | 1 | 0 | % |  | 1 | %
| 0C21 | 3105 | RO | 253# cell SOC | FLOAT | 1 | 0 | % |  | 1 | %
| 0C23 | 3107 | RO | 254# cell SOC | FLOAT | 1 | 0 | % |  | 1 | %
| 0C25 | 3109 | RO | 255# cell SOC | FLOAT | 1 | 0 | % |  | 1 | %
| 0C27 | 3111 | RO | 256# cell SOC | FLOAT | 1 | 0 | % |  | 1 | %
| 0C29 | 3113 | RO | 257# cell SOC | FLOAT | 1 | 0 | % |  | 1 | %
| 0C2B | 3115 | RO | 258# cell SOC | FLOAT | 1 | 0 | % |  | 1 | %
| 0C2D | 3117 | RO | 259# cell SOC | FLOAT | 1 | 0 | % |  | 1 | %
| 0C2F | 3119 | RO | 260# cell SOC | FLOAT | 1 | 0 | % |  | 1 | %
| 0C31 | 3121 | RO | 261# cell SOC | FLOAT | 1 | 0 | % |  | 1 | %
| 0C33 | 3123 | RO | 262# cell SOC | FLOAT | 1 | 0 | % |  | 1 | %
| 0C35 | 3125 | RO | 263# cell SOC | FLOAT | 1 | 0 | % |  | 1 | %
| 0C37 | 3127 | RO | 264# cell SOC | FLOAT | 1 | 0 | % |  | 1 | %
| 0C39 | 3129 | RO | 265# cell SOC | FLOAT | 1 | 0 | % |  | 1 | %
| 0C3B | 3131 | RO | 266# cell SOC | FLOAT | 1 | 0 | % |  | 1 | %
| 0C3D | 3133 | RO | 267# cell SOC | FLOAT | 1 | 0 | % |  | 1 | %
| 0C3F | 3135 | RO | 268# cell SOC | FLOAT | 1 | 0 | % |  | 1 | %
| 0C41 | 3137 | RO | 269# cell SOC | FLOAT | 1 | 0 | % |  | 1 | %
| 0C43 | 3139 | RO | 270# cell SOC | FLOAT | 1 | 0 | % |  | 1 | %
| 0C45 | 3141 | RO | 271# cell SOC | FLOAT | 1 | 0 | % |  | 1 | %
| 0C47 | 3143 | RO | 272# cell SOC | FLOAT | 1 | 0 | % |  | 1 | %
| 0C49 | 3145 | RO | 273# cell SOC | FLOAT | 1 | 0 | % |  | 1 | %
| 0C4B | 3147 | RO | 274# cell SOC | FLOAT | 1 | 0 | % |  | 1 | %
| 0C4D | 3149 | RO | 275# cell SOC | FLOAT | 1 | 0 | % |  | 1 | %
| 0C4F | 3151 | RO | 276# cell SOC | FLOAT | 1 | 0 | % |  | 1 | %
| 0C51 | 3153 | RO | 277# cell SOC | FLOAT | 1 | 0 | % |  | 1 | %
| 0C53 | 3155 | RO | 278# cell SOC | FLOAT | 1 | 0 | % |  | 1 | %
| 0C55 | 3157 | RO | 279# cell SOC | FLOAT | 1 | 0 | % |  | 1 | %
| 0C57 | 3159 | RO | 280# cell SOC | FLOAT | 1 | 0 | % |  | 1 | %
| 0C59 | 3161 | RO | 281# cell SOC | FLOAT | 1 | 0 | % |  | 1 | %
| 0C5B | 3163 | RO | 282# cell SOC | FLOAT | 1 | 0 | % |  | 1 | %
| 0C5D | 3165 | RO | 283# cell SOC | FLOAT | 1 | 0 | % |  | 1 | %
| 0C5F | 3167 | RO | 284# cell SOC | FLOAT | 1 | 0 | % |  | 1 | %
| 0C61 | 3169 | RO | 285# cell SOC | FLOAT | 1 | 0 | % |  | 1 | %
| 0C63 | 3171 | RO | 286# cell SOC | FLOAT | 1 | 0 | % |  | 1 | %
| 0C65 | 3173 | RO | 287# cell SOC | FLOAT | 1 | 0 | % |  | 1 | %
| 0C67 | 3175 | RO | 288# cell SOC | FLOAT | 1 | 0 | % |  | 1 | %
| 0C69 | 3177 | RO | 289# cell SOC | FLOAT | 1 | 0 | % |  | 1 | %
| 0C6B | 3179 | RO | 290# cell SOC | FLOAT | 1 | 0 | % |  | 1 | %
| 0C6D | 3181 | RO | 291# cell SOC | FLOAT | 1 | 0 | % |  | 1 | %
| 0C6F | 3183 | RO | 292# cell SOC | FLOAT | 1 | 0 | % |  | 1 | %
| 0C71 | 3185 | RO | 293# cell SOC | FLOAT | 1 | 0 | % |  | 1 | %
| 0C73 | 3187 | RO | 294# cell SOC | FLOAT | 1 | 0 | % |  | 1 | %
| 0C75 | 3189 | RO | 295# cell SOC | FLOAT | 1 | 0 | % |  | 1 | %
| 0C77 | 3191 | RO | 296# cell SOC | FLOAT | 1 | 0 | % |  | 1 | %
| 0C79 | 3193 | RO | 297# cell SOC | FLOAT | 1 | 0 | % |  | 1 | %
| 0C7B | 3195 | RO | 298# cell SOC | FLOAT | 1 | 0 | % |  | 1 | %
| 0C7D | 3197 | RO | 299# cell SOC | FLOAT | 1 | 0 | % |  | 1 | %
| 0C7F | 3199 | RO | 300# cell SOC | FLOAT | 1 | 0 | % |  | 1 | %
| 0C81 | 3201 | RO | 301# cell SOC | FLOAT | 1 | 0 | % |  | 1 | %
| 0C83 | 3203 | RO | 302# cell SOC | FLOAT | 1 | 0 | % |  | 1 | %
| 0C85 | 3205 | RO | 303# cell SOC | FLOAT | 1 | 0 | % |  | 1 | %
| 0C87 | 3207 | RO | 304# cell SOC | FLOAT | 1 | 0 | % |  | 1 | %
| 0C89 | 3209 | RO | 305# cell SOC | FLOAT | 1 | 0 | % |  | 1 | %
| 0C8B | 3211 | RO | 306# cell SOC | FLOAT | 1 | 0 | % |  | 1 | %
| 0C8D | 3213 | RO | 307# cell SOC | FLOAT | 1 | 0 | % |  | 1 | %
| 0C8F | 3215 | RO | 308# cell SOC | FLOAT | 1 | 0 | % |  | 1 | %
| 0C91 | 3217 | RO | 309# cell SOC | FLOAT | 1 | 0 | % |  | 1 | %
| 0C93 | 3219 | RO | 310# cell SOC | FLOAT | 1 | 0 | % |  | 1 | %
| 0C95 | 3221 | RO | 311# cell SOC | FLOAT | 1 | 0 | % |  | 1 | %
| 0C97 | 3223 | RO | 312# cell SOC | FLOAT | 1 | 0 | % |  | 1 | %
| 0C99 | 3225 | RO | 313# cell SOC | FLOAT | 1 | 0 | % |  | 1 | %
| 0C9B | 3227 | RO | 314# cell SOC | FLOAT | 1 | 0 | % |  | 1 | %
| 0C9D | 3229 | RO | 315# cell SOC | FLOAT | 1 | 0 | % |  | 1 | %
| 0C9F | 3231 | RO | 316# cell SOC | FLOAT | 1 | 0 | % |  | 1 | %
| 0CA1 | 3233 | RO | 317# cell SOC | FLOAT | 1 | 0 | % |  | 1 | %
| 0CA3 | 3235 | RO | 318# cell SOC | FLOAT | 1 | 0 | % |  | 1 | %
| 0CA5 | 3237 | RO | 319# cell SOC | FLOAT | 1 | 0 | % |  | 1 | %
| 0CA7 | 3239 | RO | 320# cell SOC | FLOAT | 1 | 0 | % |  | 1 | %
| 0CA9 | 3241 | RO | 321# cell SOC | FLOAT | 1 | 0 | % |  | 1 | %
| 0CAB | 3243 | RO | 322# cell SOC | FLOAT | 1 | 0 | % |  | 1 | %
| 0CAD | 3245 | RO | 323# cell SOC | FLOAT | 1 | 0 | % |  | 1 | %
| 0CAF | 3247 | RO | 324# cell SOC | FLOAT | 1 | 0 | % |  | 1 | %
| 0CB1 | 3249 | RO | 325# cell SOC | FLOAT | 1 | 0 | % |  | 1 | %
| 0CB3 | 3251 | RO | 326# cell SOC | FLOAT | 1 | 0 | % |  | 1 | %
| 0CB5 | 3253 | RO | 327# cell SOC | FLOAT | 1 | 0 | % |  | 1 | %
| 0CB7 | 3255 | RO | 328# cell SOC | FLOAT | 1 | 0 | % |  | 1 | %
| 0CB9 | 3257 | RO | 329# cell SOC | FLOAT | 1 | 0 | % |  | 1 | %
| 0CBB | 3259 | RO | 330# cell SOC | FLOAT | 1 | 0 | % |  | 1 | %
| 0CBD | 3261 | RO | 331# cell SOC | FLOAT | 1 | 0 | % |  | 1 | %
| 0CBF | 3263 | RO | 332# cell SOC | FLOAT | 1 | 0 | % |  | 1 | %
| 0CC1 | 3265 | RO | 333# cell SOC | FLOAT | 1 | 0 | % |  | 1 | %
| 0CC3 | 3267 | RO | 334# cell SOC | FLOAT | 1 | 0 | % |  | 1 | %
| 0CC5 | 3269 | RO | 335# cell SOC | FLOAT | 1 | 0 | % |  | 1 | %
| 0CC7 | 3271 | RO | 336# cell SOC | FLOAT | 1 | 0 | % |  | 1 | %
| 0CC9 | 3273 | RO | 337# cell SOC | FLOAT | 1 | 0 | % |  | 1 | %
| 0CCB | 3275 | RO | 338# cell SOC | FLOAT | 1 | 0 | % |  | 1 | %
| 0CCD | 3277 | RO | 339# cell SOC | FLOAT | 1 | 0 | % |  | 1 | %
| 0CCF | 3279 | RO | 340# cell SOC | FLOAT | 1 | 0 | % |  | 1 | %
| 0CD1 | 3281 | RO | 341# cell SOC | FLOAT | 1 | 0 | % |  | 1 | %
| 0CD3 | 3283 | RO | 342# cell SOC | FLOAT | 1 | 0 | % |  | 1 | %
| 0CD5 | 3285 | RO | 343# cell SOC | FLOAT | 1 | 0 | % |  | 1 | %
| 0CD7 | 3287 | RO | 344# cell SOC | FLOAT | 1 | 0 | % |  | 1 | %
| 0CD9 | 3289 | RO | 345# cell SOC | FLOAT | 1 | 0 | % |  | 1 | %
| 0CDB | 3291 | RO | 346# cell SOC | FLOAT | 1 | 0 | % |  | 1 | %
| 0CDD | 3293 | RO | 347# cell SOC | FLOAT | 1 | 0 | % |  | 1 | %
| 0CDF | 3295 | RO | 348# cell SOC | FLOAT | 1 | 0 | % |  | 1 | %
| 0CE1 | 3297 | RO | 349# cell SOC | FLOAT | 1 | 0 | % |  | 1 | %
| 0CE3 | 3299 | RO | 350# cell SOC | FLOAT | 1 | 0 | % |  | 1 | %
| 0CE5 | 3301 | RO | 351# cell SOC | FLOAT | 1 | 0 | % |  | 1 | %
| 0CE7 | 3303 | RO | 352# cell SOC | FLOAT | 1 | 0 | % |  | 1 | %
| 0CE9 | 3305 | RO | 353# cell SOC | FLOAT | 1 | 0 | % |  | 1 | %
| 0CEB | 3307 | RO | 354# cell SOC | FLOAT | 1 | 0 | % |  | 1 | %
| 0CED | 3309 | RO | 355# cell SOC | FLOAT | 1 | 0 | % |  | 1 | %
| 0CEF | 3311 | RO | 356# cell SOC | FLOAT | 1 | 0 | % |  | 1 | %
| 0CF1 | 3313 | RO | 357# cell SOC | FLOAT | 1 | 0 | % |  | 1 | %
| 0CF3 | 3315 | RO | 358# cell SOC | FLOAT | 1 | 0 | % |  | 1 | %
| 0CF5 | 3317 | RO | 359# cell SOC | FLOAT | 1 | 0 | % |  | 1 | %
| 0CF7 | 3319 | RO | 360# cell SOC | FLOAT | 1 | 0 | % |  | 1 | %
| 0CF9 | 3321 | RO | 361# cell SOC | FLOAT | 1 | 0 | % |  | 1 | %
| 0CFB | 3323 | RO | 362# cell SOC | FLOAT | 1 | 0 | % |  | 1 | %
| 0CFD | 3325 | RO | 363# cell SOC | FLOAT | 1 | 0 | % |  | 1 | %
| 0CFF | 3327 | RO | 364# cell SOC | FLOAT | 1 | 0 | % |  | 1 | %
| 0D01 | 3329 | RO | 365# cell SOC | FLOAT | 1 | 0 | % |  | 1 | %
| 0D03 | 3331 | RO | 366# cell SOC | FLOAT | 1 | 0 | % |  | 1 | %
| 0D05 | 3333 | RO | 367# cell SOC | FLOAT | 1 | 0 | % |  | 1 | %
| 0D07 | 3335 | RO | 368# cell SOC | FLOAT | 1 | 0 | % |  | 1 | %
| 0D09 | 3337 | RO | 369# cell SOC | FLOAT | 1 | 0 | % |  | 1 | %
| 0D0B | 3339 | RO | 370# cell SOC | FLOAT | 1 | 0 | % |  | 1 | %
| 0D0D | 3341 | RO | 371# cell SOC | FLOAT | 1 | 0 | % |  | 1 | %
| 0D0F | 3343 | RO | 372# cell SOC | FLOAT | 1 | 0 | % |  | 1 | %
| 0D11 | 3345 | RO | 373# cell SOC | FLOAT | 1 | 0 | % |  | 1 | %
| 0D13 | 3347 | RO | 374# cell SOC | FLOAT | 1 | 0 | % |  | 1 | %
| 0D15 | 3349 | RO | 375# cell SOC | FLOAT | 1 | 0 | % |  | 1 | %
| 0D17 | 3351 | RO | 376# cell SOC | FLOAT | 1 | 0 | % |  | 1 | %
| 0D19 | 3353 | RO | 377# cell SOC | FLOAT | 1 | 0 | % |  | 1 | %
| 0D1B | 3355 | RO | 378# cell SOC | FLOAT | 1 | 0 | % |  | 1 | %
| 0D1D | 3357 | RO | 379# cell SOC | FLOAT | 1 | 0 | % |  | 1 | %
| 0D1F | 3359 | RO | 380# cell SOC | FLOAT | 1 | 0 | % |  | 1 | %
| 0D21 | 3361 | RO | 381# cell SOC | FLOAT | 1 | 0 | % |  | 1 | %
| 0D23 | 3363 | RO | 382# cell SOC | FLOAT | 1 | 0 | % |  | 1 | %
| 0D25 | 3365 | RO | 383# cell SOC | FLOAT | 1 | 0 | % |  | 1 | %
| 0D27 | 3367 | RO | 384# cell SOC | FLOAT | 1 | 0 | % |  | 1 | %
| 0D29 | 3369 | RO | 385# cell SOC | FLOAT | 1 | 0 | % |  | 1 | %
| 0D2B | 3371 | RO | 386# cell SOC | FLOAT | 1 | 0 | % |  | 1 | %
| 0D2D | 3373 | RO | 387# cell SOC | FLOAT | 1 | 0 | % |  | 1 | %
| 0D2F | 3375 | RO | 388# cell SOC | FLOAT | 1 | 0 | % |  | 1 | %
| 0D31 | 3377 | RO | 389# cell SOC | FLOAT | 1 | 0 | % |  | 1 | %
| 0D33 | 3379 | RO | 390# cell SOC | FLOAT | 1 | 0 | % |  | 1 | %
| 0D35 | 3381 | RO | 391# cell SOC | FLOAT | 1 | 0 | % |  | 1 | %
| 0D37 | 3383 | RO | 392# cell SOC | FLOAT | 1 | 0 | % |  | 1 | %
| 0D39 | 3385 | RO | 393# cell SOC | FLOAT | 1 | 0 | % |  | 1 | %
| 0D3B | 3387 | RO | 394# cell SOC | FLOAT | 1 | 0 | % |  | 1 | %
| 0D3D | 3389 | RO | 395# cell SOC | FLOAT | 1 | 0 | % |  | 1 | %
| 0D3F | 3391 | RO | 396# cell SOC | FLOAT | 1 | 0 | % |  | 1 | %
| 0D41 | 3393 | RO | 397# cell SOC | FLOAT | 1 | 0 | % |  | 1 | %
| 0D43 | 3395 | RO | 398# cell SOC | FLOAT | 1 | 0 | % |  | 1 | %
| 0D45 | 3397 | RO | 399# cell SOC | FLOAT | 1 | 0 | % |  | 1 | %
| 0D47 | 3399 | RO | 400# cell SOC | FLOAT | 1 | 0 | % |  | 1 | %
| 0D49 | 3401 | RO | 401# cell SOC | FLOAT | 1 | 0 | % |  | 1 | %
| 0D4B | 3403 | RO | 402# cell SOC | FLOAT | 1 | 0 | % |  | 1 | %
| 0D4D | 3405 | RO | 403# cell SOC | FLOAT | 1 | 0 | % |  | 1 | %
| 0D4F | 3407 | RO | 404# cell SOC | FLOAT | 1 | 0 | % |  | 1 | %
| 0D51 | 3409 | RO | 405# cell SOC | FLOAT | 1 | 0 | % |  | 1 | %
| 0D53 | 3411 | RO | 406# cell SOC | FLOAT | 1 | 0 | % |  | 1 | %
| 0D55 | 3413 | RO | 407# cell SOC | FLOAT | 1 | 0 | % |  | 1 | %
| 0D57 | 3415 | RO | 408# cell SOC | FLOAT | 1 | 0 | % |  | 1 | %
| 0D59 | 3417 | RO | 409# cell SOC | FLOAT | 1 | 0 | % |  | 1 | %
| 0D5B | 3419 | RO | 410# cell SOC | FLOAT | 1 | 0 | % |  | 1 | %
| 0D5D | 3421 | RO | 411# cell SOC | FLOAT | 1 | 0 | % |  | 1 | %
| 0D5F | 3423 | RO | 412# cell SOC | FLOAT | 1 | 0 | % |  | 1 | %
| 0D61 | 3425 | RO | 413# cell SOC | FLOAT | 1 | 0 | % |  | 1 | %
| 0D63 | 3427 | RO | 414# cell SOC | FLOAT | 1 | 0 | % |  | 1 | %
| 0D65 | 3429 | RO | 415# cell SOC | FLOAT | 1 | 0 | % |  | 1 | %
| 0D67 | 3431 | RO | 416# cell SOC | FLOAT | 1 | 0 | % |  | 1 | %
| 0D69 | 3433 | RO | reserve | FLOAT
| 0D6B | 3435 | RO | reserve | FLOAT
| 0D6D | 3437 | RO | reserve | FLOAT
| 0D6F | 3439 | RO | reserve | FLOAT
| 0D71 | 3441 | RO | reserve | FLOAT
| 0D73 | 3443 | RO | reserve | FLOAT
| 0D75 | 3445 | RO | reserve | FLOAT
| 0D77 | 3447 | RO | reserve | FLOAT
| 0D79 | 3449 | RO | reserve | FLOAT
| 0D7B | 3451 | RO | reserve | FLOAT
| 0D7D | 3453 | RO | reserve | FLOAT
| 0D7F | 3455 | RO | reserve | FLOAT
| 0D81 | 3457 | RO | reserve | FLOAT
| 0D83 | 3459 | RO | reserve | FLOAT
| 0D85 | 3461 | RO | reserve | FLOAT
| 0D87 | 3463 | RO | reserve | FLOAT
| 0D89 | 3465 | RO | reserve | FLOAT
| 0D8B | 3467 | RO | reserve | FLOAT
| 0D8D | 3469 | RO | reserve | FLOAT
| 0D8F | 3471 | RO | reserve | FLOAT
| 0D91 | 3473 | RO | reserve | FLOAT
| 0D93 | 3475 | RO | reserve | FLOAT
| 0D95 | 3477 | RO | reserve | FLOAT
| 0D97 | 3479 | RO | reserve | FLOAT
| 0D99 | 3481 | RO | reserve | FLOAT
| 0D9B | 3483 | RO | reserve | FLOAT
| 0D9D | 3485 | RO | reserve | FLOAT
| 0D9F | 3487 | RO | reserve | FLOAT
| 0DA1 | 3489 | RO | reserve | FLOAT
| 0DA3 | 3491 | RO | reserve | FLOAT
| 0DA5 | 3493 | RO | reserve | FLOAT
| 0DA7 | 3495 | RO | reserve | FLOAT
| 0DA9 | 3497 | RO | reserve | FLOAT
| 0DAB | 3499 | RO | reserve | FLOAT
| 0DAD | 3501 | RO | reserve | FLOAT
| 0DAF | 3503 | RO | reserve | FLOAT
| 0DB1 | 3505 | RO | reserve | FLOAT
| 0DB3 | 3507 | RO | reserve | FLOAT
| 0DB5 | 3509 | RO | reserve | FLOAT
| 0DB7 | 3511 | RO | reserve | FLOAT
| 0DB9 | 3513 | RO | reserve | FLOAT
| 0DBB | 3515 | RO | reserve | FLOAT
| 0DBD | 3517 | RO | reserve | FLOAT
| 0DBF | 3519 | RO | reserve | FLOAT
| 0DC1 | 3521 | RO | reserve | FLOAT
| 0DC3 | 3523 | RO | reserve | FLOAT
| 0DC5 | 3525 | RO | reserve | FLOAT
| 0DC7 | 3527 | RO | reserve | FLOAT
| 0DC9 | 3529 | RO | reserve | FLOAT
| 0DCB | 3531 | RO | reserve | FLOAT
| 0DCD | 3533 | RO | reserve | FLOAT
| 0DCF | 3535 | RO | reserve | FLOAT
| 0DD1 | 3537 | RO | reserve | FLOAT
| 0DD3 | 3539 | RO | reserve | FLOAT
| 0DD5 | 3541 | RO | reserve | FLOAT
| 0DD7 | 3543 | RO | reserve | FLOAT
| 0DD9 | 3545 | RO | reserve | FLOAT
| 0DDB | 3547 | RO | reserve | FLOAT
| 0DDD | 3549 | RO | reserve | FLOAT
| 0DDF | 3551 | RO | reserve | FLOAT
| 0DE1 | 3553 | RO | reserve | FLOAT
| 0DE3 | 3555 | RO | reserve | FLOAT
| 0DE5 | 3557 | RO | reserve | FLOAT
| 0DE7 | 3559 | RO | reserve | FLOAT
| 0DE9 | 3561 | RO | reserve | FLOAT
| 0DEB | 3563 | RO | reserve | FLOAT
| 0DED | 3565 | RO | reserve | FLOAT
| 0DEF | 3567 | RO | reserve | FLOAT
| 0DF1 | 3569 | RO | reserve | FLOAT
| 0DF3 | 3571 | RO | reserve | FLOAT
| 0DF5 | 3573 | RO | reserve | FLOAT
| 0DF7 | 3575 | RO | reserve | FLOAT
| 0DF9 | 3577 | RO | reserve | FLOAT
| 0DFB | 3579 | RO | reserve | FLOAT
| 0DFD | 3581 | RO | reserve | FLOAT
| 0DFF | 3583 | RO | reserve | FLOAT
| 0 | 3585 | RO | reserve | FLOAT
| 0 | 3587 | RO | reserve | FLOAT
| 0 | 3589 | RO | reserve | FLOAT
| 0 | 3591 | RO | reserve | FLOAT
| 0 | 3593 | RO | reserve | FLOAT
| 0E0B | 3595 | RO | reserve | FLOAT
| 0E0D | 3597 | RO | reserve | FLOAT
| 0E0F | 3599 | RO | reserve | FLOAT
| 0 | 3601 | RO | reserve | FLOAT
| 0 | 3603 | RO | reserve | FLOAT
| 0 | 3605 | RO | reserve | FLOAT
| 0 | 3607 | RO | reserve | FLOAT
| 0 | 3609 | RO | reserve | FLOAT
| 0E1B | 3611 | RO | reserve | FLOAT
| 0E1D | 3613 | RO | reserve | FLOAT
| 0E1F | 3615 | RO | reserve | FLOAT
| 0 | 3617 | RO | reserve | FLOAT
| 0 | 3619 | RO | reserve | FLOAT
| 0 | 3621 | RO | reserve | FLOAT
| 0 | 3623 | RO | reserve | FLOAT
| 0 | 3625 | RO | reserve | FLOAT
| 0E2B | 3627 | RO | reserve | FLOAT
| 0E2D | 3629 | RO | reserve | FLOAT
| 0E2F | 3631 | RO | reserve | FLOAT
| 0 | 3633 | RO | reserve | FLOAT
| 0 | 3635 | RO | reserve | FLOAT
| 0 | 3637 | RO | reserve | FLOAT
| 0 | 3639 | RO | reserve | FLOAT
| 0 | 3641 | RO | reserve | FLOAT
| 0E3B | 3643 | RO | reserve | FLOAT
| 0E3D | 3645 | RO | reserve | FLOAT
| 0E3F | 3647 | RO | reserve | FLOAT
| 0 | 3649 | RO | reserve | FLOAT
| 0 | 3651 | RO | reserve | FLOAT
| 0 | 3653 | RO | reserve | FLOAT
| 0 | 3655 | RO | reserve | FLOAT
| 0 | 3657 | RO | reserve | FLOAT
| 0E4B | 3659 | RO | reserve | FLOAT
| 0E4D | 3661 | RO | reserve | FLOAT
| 0E4F | 3663 | RO | reserve | FLOAT
| 0 | 3665 | RO | reserve | FLOAT
| 0 | 3667 | RO | reserve | FLOAT
| 0 | 3669 | RO | reserve | FLOAT
| 0 | 3671 | RO | reserve | FLOAT
| 0 | 3673 | RO | reserve | FLOAT
| 0E5B | 3675 | RO | reserve | FLOAT
| 0E5D | 3677 | RO | reserve | FLOAT
| 0E5F | 3679 | RO | reserve | FLOAT
| 0 | 3681 | RO | reserve | FLOAT
| 0 | 3683 | RO | reserve | FLOAT
| 0 | 3685 | RO | reserve | FLOAT
| 0 | 3687 | RO | reserve | FLOAT
| 0 | 3689 | RO | reserve | FLOAT
| 0E6B | 3691 | RO | reserve | FLOAT
| 0E6D | 3693 | RO | reserve | FLOAT
| 0E6F | 3695 | RO | reserve | FLOAT
| 0 | 3697 | RO | reserve | FLOAT
| 0 | 3699 | RO | reserve | FLOAT
| 0 | 3701 | RO | reserve | FLOAT
| 0 | 3703 | RO | reserve | FLOAT
| 0 | 3705 | RO | reserve | FLOAT
| 0E7B | 3707 | RO | reserve | FLOAT
| 0E7D | 3709 | RO | reserve | FLOAT
| 0E7F | 3711 | RO | reserve | FLOAT
| 0 | 3713 | RO | reserve | FLOAT
| 0 | 3715 | RO | reserve | FLOAT
| 0 | 3717 | RO | reserve | FLOAT
| 0 | 3719 | RO | reserve | FLOAT
| 0 | 3721 | RO | reserve | FLOAT
| 0E8B | 3723 | RO | reserve | FLOAT
| 0E8D | 3725 | RO | reserve | FLOAT
| 0E8F | 3727 | RO | reserve | FLOAT
| 0 | 3729 | RO | reserve | FLOAT
| 0 | 3731 | RO | reserve | FLOAT
| 0 | 3733 | RO | reserve | FLOAT
| 0 | 3735 | RO | reserve | FLOAT
| 0 | 3737 | RO | reserve | FLOAT
| 0E9B | 3739 | RO | reserve | FLOAT
| 0E9D | 3741 | RO | reserve | FLOAT
| 0E9F | 3743 | RO | reserve | FLOAT
| 0EA1 | 3745 | RO | reserve | FLOAT
| 0EA3 | 3747 | RO | reserve | FLOAT
| 0EA5 | 3749 | RO | reserve | FLOAT
| 0EA7 | 3751 | RO | reserve | FLOAT
| 0EA9 | 3753 | RO | reserve | FLOAT
| 0EAB | 3755 | RO | reserve | FLOAT
| 0EAD | 3757 | RO | reserve | FLOAT
| 0EAF | 3759 | RO | reserve | FLOAT
| 0EB1 | 3761 | RO | reserve | FLOAT
| 0EB3 | 3763 | RO | reserve | FLOAT
| 0EB5 | 3765 | RO | reserve | FLOAT
| 0EB7 | 3767 | RO | reserve | FLOAT
| 0EB9 | 3769 | RO | reserve | FLOAT
| 0EBB | 3771 | RO | reserve | FLOAT
| 0EBD | 3773 | RO | reserve | FLOAT
| 0EBF | 3775 | RO | reserve | FLOAT
| 0EC1 | 3777 | RO | reserve | FLOAT
| 0EC3 | 3779 | RO | reserve | FLOAT
| 0EC5 | 3781 | RO | reserve | FLOAT
| 0EC7 | 3783 | RO | reserve | FLOAT
| 0EC9 | 3785 | RO | reserve | FLOAT
| 0ECB | 3787 | RO | reserve | FLOAT
| 0ECD | 3789 | RO | reserve | FLOAT
| 0ECF | 3791 | RO | reserve | FLOAT
| 0ED1 | 3793 | RO | reserve | FLOAT
| 0ED3 | 3795 | RO | reserve | FLOAT
| 0ED5 | 3797 | RO | reserve | FLOAT
| 0ED7 | 3799 | RO | reserve | FLOAT

## Pack Temp
Register Type | Register Address |  | Attributes | Meaning | Data Types | Coefficient | Offset | Units | Remarks | Decimal pointPrecision required | Units
| Hexadecimal | Decimal
Pack pole temperature data (Each rack Modbus address independent, starting from 2, discrete input registers,function code 0x04, same Modbus address as rack data, same function code, different register addresses) | 1839 | 6201 | RO | 1# pack negative pole temperature | FLOAT | 1 | 0 | ℃ | pack pole temperature | 0.1 | ℃
| 183B | 6203 | RO | 1# pack positive pole temperature | FLOAT | 1 | 0 | ℃ |  | 0.1 | ℃
| 183D | 6205 | RO | 2# pack negative pole temperature | FLOAT | 1 | 0 | ℃ |  | 0.1 | ℃
| 183F | 6207 | RO | 2# pack positive pole temperature | FLOAT | 1 | 0 | ℃ |  | 0.1 | ℃
| 1841 | 6209 | RO | 3# pack negative pole temperature | FLOAT | 1 | 0 | ℃ |  | 0.1 | ℃
| 1843 | 6211 | RO | 3# pack positive pole temperature | FLOAT | 1 | 0 | ℃ |  | 0.1 | ℃
| 1845 | 6213 | RO | 4# pack negative pole temperature | FLOAT | 1 | 0 | ℃ |  | 0.1 | ℃
| 1847 | 6215 | RO | 4# pack positive pole temperature | FLOAT | 1 | 0 | ℃ |  | 0.1 | ℃
| 1849 | 6217 | RO | 5# pack negative pole temperature | FLOAT | 1 | 0 | ℃ |  | 0.1 | ℃
| 184B | 6219 | RO | 5# pack positive pole temperature | FLOAT | 1 | 0 | ℃ |  | 0.1 | ℃
| 184D | 6221 | RO | 6# pack negative pole temperature | FLOAT | 1 | 0 | ℃ |  | 0.1 | ℃
| 184F | 6223 | RO | 6# pack positive pole temperature | FLOAT | 1 | 0 | ℃ |  | 0.1 | ℃
| 1851 | 6225 | RO | 7# pack negative pole temperature | FLOAT | 1 | 0 | ℃ |  | 0.1 | ℃
| 1853 | 6227 | RO | 7# pack positive pole temperature | FLOAT | 1 | 0 | ℃ |  | 0.1 | ℃
| 1855 | 6229 | RO | 8# pack negative pole temperature | FLOAT | 1 | 0 | ℃ |  | 0.1 | ℃
| 1857 | 6231 | RO | 8# pack positive pole temperature | FLOAT | 1 | 0 | ℃ |  | 0.1 | ℃
| 1859 | 6233 | RO | reserve | FLOAT
| 185B | 6235 | RO | reserve | FLOAT
| 185D | 6237 | RO | reserve | FLOAT
| 185F | 6239 | RO | reserve | FLOAT
| 1861 | 6241 | RO | reserve | FLOAT
| 1863 | 6243 | RO | reserve | FLOAT
| 1865 | 6245 | RO | reserve | FLOAT
| 1867 | 6247 | RO | reserve | FLOAT
| 1869 | 6249 | RO | reserve | FLOAT
| 186B | 6251 | RO | reserve | FLOAT
| 186D | 6253 | RO | reserve | FLOAT
| 186F | 6255 | RO | reserve | FLOAT
| 1871 | 6257 | RO | reserve | FLOAT
| 1873 | 6259 | RO | reserve | FLOAT
| 1875 | 6261 | RO | reserve | FLOAT
| 1877 | 6263 | RO | reserve | FLOAT
| 1879 | 6265 | RO | reserve | FLOAT
| 187B | 6267 | RO | reserve | FLOAT
| 187D | 6269 | RO | reserve | FLOAT
| 187F | 6271 | RO | reserve | FLOAT
| 1881 | 6273 | RO | reserve | FLOAT
| 1883 | 6275 | RO | reserve | FLOAT
| 1885 | 6277 | RO | reserve | FLOAT
| 1887 | 6279 | RO | reserve | FLOAT
| 1889 | 6281 | RO | reserve | FLOAT
| 188B | 6283 | RO | reserve | FLOAT
| 188D | 6285 | RO | reserve | FLOAT
| 188F | 6287 | RO | reserve | FLOAT
| 1891 | 6289 | RO | reserve | FLOAT
| 1893 | 6291 | RO | reserve | FLOAT
| 1895 | 6293 | RO | reserve | FLOAT
| 1897 | 6295 | RO | reserve | FLOAT
| 1899 | 6297 | RO | reserve | FLOAT
| 189B | 6299 | RO | reserve | FLOAT
| 189D | 6301 | RO | reserve | FLOAT
| 189F | 6303 | RO | reserve | FLOAT
| 18A1 | 6305 | RO | reserve | FLOAT
| 18A3 | 6307 | RO | reserve | FLOAT
| 18A5 | 6309 | RO | reserve | FLOAT
| 18A7 | 6311 | RO | reserve | FLOAT
| 18A9 | 6313 | RO | reserve | FLOAT
| 18AB | 6315 | RO | reserve | FLOAT
| 18AD | 6317 | RO | reserve | FLOAT
| 18AF | 6319 | RO | reserve | FLOAT
| 18B1 | 6321 | RO | reserve | FLOAT
| 18B3 | 6323 | RO | reserve | FLOAT
| 18B5 | 6325 | RO | reserve | FLOAT
| 18B7 | 6327 | RO | reserve | FLOAT
| 18B9 | 6329 | RO | reserve | FLOAT
| 18BB | 6331 | RO | reserve | FLOAT
| 18BD | 6333 | RO | reserve | FLOAT
| 18BF | 6335 | RO | reserve | FLOAT
| 18C1 | 6337 | RO | reserve | FLOAT
| 18C3 | 6339 | RO | reserve | FLOAT
| 18C5 | 6341 | RO | reserve | FLOAT
| 18C7 | 6343 | RO | reserve | FLOAT
| 18C9 | 6345 | RO | reserve | FLOAT
| 18CB | 6347 | RO | reserve | FLOAT
| 18CD | 6349 | RO | reserve | FLOAT
| 18CF | 6351 | RO | reserve | FLOAT
| 18D1 | 6353 | RO | reserve | FLOAT
| 18D3 | 6355 | RO | reserve | FLOAT
| 18D5 | 6357 | RO | reserve | FLOAT
| 18D7 | 6359 | RO | reserve | FLOAT
| 18D9 | 6361 | RO | reserve | FLOAT
| 18DB | 6363 | RO | reserve | FLOAT
| 18DD | 6365 | RO | reserve | FLOAT
| 18DF | 6367 | RO | reserve | FLOAT
| 180 | 6369 | RO | reserve | FLOAT
| 18000 | 6371 | RO | reserve | FLOAT
| 1800000 | 6373 | RO | reserve | FLOAT
| 180000000 | 6375 | RO | reserve | FLOAT
| 18000000000 | 6377 | RO | reserve | FLOAT
| 18EB | 6379 | RO | reserve | FLOAT
| 18ED | 6381 | RO | reserve | FLOAT
| 18EF | 6383 | RO | reserve | FLOAT
| 18F1 | 6385 | RO | reserve | FLOAT
| 18F3 | 6387 | RO | reserve | FLOAT
| 18F5 | 6389 | RO | reserve | FLOAT
| 18F7 | 6391 | RO | reserve | FLOAT
| 18F9 | 6393 | RO | reserve | FLOAT
| 18FB | 6395 | RO | reserve | FLOAT
| 18FD | 6397 | RO | reserve | FLOAT
| 18FF | 6399 | RO | reserve | FLOAT

## Pack Volt
Register Type | Register Address |  | Attributes | Meaning | Data Types | Coefficient | Offset | Decimal pointPrecision required | Units | Remarks
| Hexadecimal | Decimal
Pack voltage data (Each rack Modbus address independent, starting from 2, discrete input registers,function code 0x04, same Modbus address as rack data, same function code, different register addresses) | 1901 | 6401 | RO | 1# pack voltage | FLOAT | 1 | 0 | 0.1 | V | Pack voltage
| 1903 | 6403 | RO | 2# pack voltage | FLOAT | 1 | 0 | 0.1 | V
| 1905 | 6405 | RO | 3# pack voltage | FLOAT | 1 | 0 | 0.1 | V
| 1907 | 6407 | RO | 4# pack voltage | FLOAT | 1 | 0 | 0.1 | V
| 1909 | 6409 | RO | 5# pack voltage | FLOAT | 1 | 0 | 0.1 | V
| 190B | 6411 | RO | 6# pack voltage | FLOAT | 1 | 0 | 0.1 | V
| 190D | 6413 | RO | 7# pack voltage | FLOAT | 1 | 0 | 0.1 | v
| 190F | 6415 | RO | 8# pack voltage | FLOAT | 1 | 0 | 0.1 | v
| 1911 | 6417 | RO | reserve | FLOAT
| 1913 | 6419 | RO | reserve | FLOAT
| 1915 | 6421 | RO | reserve | FLOAT
| 1917 | 6423 | RO | reserve | FLOAT
| 1919 | 6425 | RO | reserve | FLOAT
| 191B | 6427 | RO | reserve | FLOAT
| 191D | 6429 | RO | reserve | FLOAT
| 191F | 6431 | RO | reserve | FLOAT
| 1921 | 6433 | RO | reserve | FLOAT
| 1923 | 6435 | RO | reserve | FLOAT
| 1925 | 6437 | RO | reserve | FLOAT
| 1927 | 6439 | RO | reserve | FLOAT
| 1929 | 6441 | RO | reserve | FLOAT
| 192B | 6443 | RO | reserve | FLOAT
| 192D | 6445 | RO | reserve | FLOAT
| 192F | 6447 | RO | reserve | FLOAT
| 1931 | 6449 | RO | reserve | FLOAT
| 1933 | 6451 | RO | reserve | FLOAT
| 1935 | 6453 | RO | reserve | FLOAT
| 1937 | 6455 | RO | reserve | FLOAT
| 1939 | 6457 | RO | reserve | FLOAT
| 193B | 6459 | RO | reserve | FLOAT
| 193D | 6461 | RO | reserve | FLOAT
| 193F | 6463 | RO | reserve | FLOAT
| 1941 | 6465 | RO | reserve | FLOAT
| 1943 | 6467 | RO | reserve | FLOAT
| 1945 | 6469 | RO | reserve | FLOAT
| 1947 | 6471 | RO | reserve | FLOAT
| 1949 | 6473 | RO | reserve | FLOAT
| 194B | 6475 | RO | reserve | FLOAT
| 194D | 6477 | RO | reserve | FLOAT
| 194F | 6479 | RO | reserve | FLOAT
| 1951 | 6481 | RO | reserve | FLOAT
| 1953 | 6483 | RO | reserve | FLOAT
| 1955 | 6485 | RO | reserve | FLOAT
| 1957 | 6487 | RO | reserve | FLOAT
| 1959 | 6489 | RO | reserve | FLOAT
| 195B | 6491 | RO | reserve | FLOAT
| 195D | 6493 | RO | reserve | FLOAT
| 195F | 6495 | RO | reserve | FLOAT
| 1961 | 6497 | RO | reserve | FLOAT
| 1963 | 6499 | RO | reserve | FLOAT

## Temp&Humidity
Register Type | Register Address |  | Attributes | Meaning | Data Types | Coefficient | Offset | Decimal pointPrecision required | Units | Remarks
| Hexadecimal | Decimal
Read Temp&Humidity Data (Modbus address starting from 101, input registers,function code 0x04) | 191 | 401 | RO | Communication between BMS and sensor | UINT16 | 1 | 0 |  |  | 0--normal, 1--fault
| 192 | 402 | RO | reserve | UINT16 | 1 | 0
| 193 | 403 | RO | reserve | UINT16 | 1 | 0
| 194 | 404 | RO | Alarm state | UINT16 | 1 | 0 |  |  | 0--normal, 1--temp，2--humi，3--temp and humi
| 195 | 405 | RO | reserve | UINT16 | 1 | 0
| 01F4 | 500 | RO | reserve | UINT16 | 1 | 0
The Above is the data of the UINT16 type , and the following is the data of the FLOAT Type
| 01F5 | 501 | RO | indoor temp | FLOAT | 1 | 0 | 0.1 | ℃
| 01F7 | 503 | RO | indoor humidity | FLOAT | 1 | 0 | 0.1 | %RH
| 01F9 | 505 | RO | reserve | FLOAT | 1 | 0
| 02BB | 699 | RO | reserve | FLOAT | 1 | 0

## Water sensor
Register Type | Register Address |  | Attributes | Meaning | Data Types | Coefficient | Offset | Decimal pointPrecision required | Units | Remarks
| Hexadecimal | Decimal
Read Water sensor data (Modbus address starting from 101, input registers,function code 0x04) | 02BD | 701 | RO | Communication between BMS and sensor | UINT16 | 1 | 0 |  |  | 0--normal, 1--fault
| 02BE | 702 | RO | reserve | UINT16 | 1 | 0
| 02BF | 703 | RO | reserve | UINT16 | 1 | 0
| 02C0 | 704 | RO | Alarm state | UINT16 | 1 | 0 |  |  | 0--normal, 1--alarm
| 02C1 | 705 | RO | reserve | UINT16 | 1 | 0
| 320 | 800 | RO | reserve | UINT16 | 1 | 0
The Above is the data of the UINT16 type , and the following is the data of the FLOAT Type
| 321 | 801 | RO | reserve | FLOAT | 1 | 0
| 30000000 | 999 | RO | reserve | FLOAT | 1 | 0

## Chiller
Register Type | Register Address |  | Attributes | Meaning | Data Types | Coefficient | Offset | Decimal pointPrecision required | Units | Remarks
| Hexadecimal | Decimal
Read Chiller data (Modbus address starting from 101, input registers,function code 0x04) | 515 | 1301 | RO | Communication between BMS and Chiller | UINT16 | 1 | 0 |  |  | 0--normal, 1--fault
| 516 | 1302 | RO | Start state | UINT16 | 1 | 0 |  |  | 0--turn off, 1--turn on
| 517 | 1303 | RO | reserve | UINT16 | 1 | 0
| 518 | 1304 | RO | Alarm state | UINT16 | 1 | 0 |  |  | 0--normal, 1--alarm
| 519 | 1305 | RO | Operation mode state | UINT16 | 1 | 0 |  |  | 0--Standby 1--Cooling 2--Heating 3--Circulation 4--Auto
| 051A | 1306 | RO | Fault code | UINT16 | 1 | 0 |  |  | bit 0 - System water shortage alarm , bit1 - 1# Condensing press too high alarm , bit 2 - 2# Condensing press too high alarm bit 3 - Outlet water press too high alarm bit 4 - Inlet water press too low alarm
| 051B | 1307 | RO | Fault code | UINT16 | 1 | 0
| 051C | 1308 | RO | Pump speed | UINT16 | 1 | 0
| 051D | 1309 | RO | Fault code | UINT16 | 1 | 0 |  |  | bit 0 -1# Discharge temp sensor failure , bit 1 -1# Condensation temp senor failure ,bit 2 - 2# Discharge temp sensor failure , bit 3 -2# Condensation temp senor failure , bit 4 -Inlet water temp sensor failure , bit 5 - Outlet water temp sensor failure , bit 6 - Ambient temp sensor failure , bit 7 - Abnormal power down alarm , bit 8 - 1# High press sensor failure , bit 9 - 2# High press sensor failure , bit 10 - Water tank water level low , bit 11 - Return water pressure sensor failure , bit 12 - Outlet water pressure sensor failure
| 051E | 1310 | RO | Fault code | UINT16 | 1 | 0
| 051F | 1311 | RO | Fault code | [5 empty] | bit 0 -1# High press lock , bit 1 - 1# Discharge over temp lock , bit 2 -1# System low press alarm lock , bit 3 - 1# Low press sensor failure , bit 4 - 1# Evap outlet temp senor failure , bit 5 - 1# Comp freq converter failure ,bit 6 - 1# Comp freq converter commun failure , bit 7 - 1# Outdoor fan freq converter failure , bit 8 - 1# Outdoor fan freq converter commu failure , bit 9 -2# High press lock , bit 10 - 2# Discharge over temp lock , bit 11 - 2# System low press alarm lock , bit 12 - 2# Low press sensor failure , bit 13 - 2# Evap outlet temp senor failure , bit 14 - 2# Comp freq converter failure , bit 15 - 2# Comp freq converter commun failure
| 0520 | 1312 | RO | Fault code | [5 empty] | bit 0 -Expansion module commun failure , bit 1 - 2# Outdoor fan freq converter failure , bit 2 - 2# Outdoor fan freq converter commu failure , bit 3 - Water pump low press diff , bit 4 -Inlet water temp sensor failure & Outlet water temp sensor failure , bit 5 - Power supply failure , bit 6 - Inlet water press sensor failure & Outlet water press sensor failure , bit 8 - 1# Circulating water pump freq converter failure , bit 9 - 1# Circulating water pump freq converter commun failure , bit 10 - 1# Electrical heater failure lock , bit 11 - Outlet water high temp , bit 12 - Outlet water low temp , bit 13 - 1# Circulating water pump superheat protection alarm lock , bit 14 - 2# Circulating water pump superheat protection alarm lock , bit 15 -1# Circulating water pump overload protection lock
| 0521 | 1313 | RO | Fault code | [5 empty] | bit 0 - 2# Circulating water pump overload protection lock , bit 1 - 2# Circulating water pump freq converter failure , bit 2 - 2# Circulating water pump freq converter commun failure , bit 3 - 2# Electrical heater failure lock , bit 4 - APF failure , bit 5 - DC_DC1 module failure , bit 6 - DC_DC2 module failure
| 0522 | 1314 | RO | Fault code
| 0523 | 1315 | RO | Comp run status
| 0524 | 1316 | RO | Comp run status
| 0525 | 1317 | RO | Electrical heater run status
| 0526 | 1318 | RO | Condenser fan run status
| 578 | 1400 | RO | reserve |  | 1 | 0 |  |  | 0
| 579 | 1401 | RO | Outlet water temperature | FLOAT | 1 | 0 | 0.1 | ℃
| 057B | 1403 | RO | Inlet water temperature | FLOAT | 1 | 0 | 0.1 | ℃
| 057D | 1405 | RO | Outlet water pressure | FLOAT | 1 | 0 | 0.01 | bar
| 057F | 1407 | RO | Inlet water pressure | FLOAT | 1 | 0 | 0.01 | bar
| 581 | 1409 | RO | Ambient temperature | FLOAT | 1 | 0 | 0.1 | ℃
| 583 | 1411 | RO | Set cooling start temperature | FLOAT | 1 | 0 | 0.1 | ℃
| 585 | 1413 | RO | reserve | UINT16 | 1 | 0
| 587 | 1415 | RO | Set cooling differential temperature | FLOAT | 1 | 0 | 0.1 | ℃
| 589 | 1417 | RO | Set heating start temperature | FLOAT | 1 | 0 | 0.1 | ℃
| 058B | 1419 | RO | reserve | UINT16 | 1 | 0
| 058D | 1421 | RO | Set heating differential temperature | FLOAT | 1 | 0 | 0.1 | ℃
| 058F | 1423 | RO | reserve | UINT16 | 1 | 0
| 591 | 1425 | RO | reserve | UINT16 | 1 | 0
| 593 | 1427 | RO | reserve | UINT16 | 1 | 0
| 595 | 1429 | RO | reserve | UINT16 | 1 | 0
| 597 | 1431 | RO | reserve | UINT16 | 1 | 0
| 599 | 1433 | RO | reserve | UINT16 | 1 | 0
| 059B | 1435 | RO | reserve | UINT16 | 1 | 0
| 059D | 1437 | RO | reserve |  | 1 | 0
| 063F | 1599 | RO | reserve |  | 1 | 0
Write Chiller data (Modbus address starting from 101, save registers,function code 0x06) | 2C25 | 11301 | RW | Control mode | UINT16 | 1 | 0 |  |  | 0--BMS 1--Auto 2--Forced
| 2C26 | 11302 | RW | Start state (reserve) | UINT16 | 1 | 0 |  |  | 0--turn off, 1--turn on
| 2C27 | 11303 | RW | Operation mode state | UINT16 | 1 | 0 |  |  | 0--Standby 1--Cooling 2--Heating 3--Circulation 4--Auto
| 2C28 | 11304 | RW | Set target temperature | UINT16 | 0.01 | -100 | 0.1 | ℃ | Actual value = Register value × 0.01 - 100 Register value = (Actual value + 100) × 100 Actual value range: -100 to 100
| 2C29 | 11305 | RW | Set cooling start temperature | UINT16 | 0.01 | -100 | 0.1 | ℃
| 2C2A | 11306 | RW | reserve | UINT16
| 2C2B | 11307 | RW | Set cooling differential temperature | UINT16 | 0.01 | -100 | 0.1 | ℃
| 2C2C | 11308 | RW | Set heating start temperature | UINT16 | 0.01 | -100 | 0.1 | ℃
| 2C2D | 11309 | RW | reserve | UINT16
| 2C2E | 11310 | RW | Set heating differential temperature | UINT16 | 0.01 | -100 | 0.1 | ℃
| 2C2F | 11311 | W | CoolTemp_Down_Limit_Lev1 | UINT16 | 0.01 | -100 | 0.1 | ℃
| 2C30 | 11312 | W | reserve | UINT16 | 0.01 | -100 | 0.1 | ℃
| 2C31 | 11313 | W | CoolTemp_Avg_Limit_Lev1 | UINT16 | 0.01 | -100 | 0.1 | ℃
| 2C32 | 11314 | W | CoolTemp_Down_Limit_Lev2 | UINT17 | 0.01 | -100 | 0.1 | ℃ | 0
| 2C33 | 11315 | W | CoolTemp_Avg_Limit_Lev2 | UINT18 | 0.01 | -100 | 0.1 | ℃
| 2C34 | 11316 | W | Cool_Stop_Temp | UINT19 | 0.01 | -100 | 0.1 | ℃
| 2C35 | 11317 | W | Cool_Stop_Avg_Temp | UINT20 | 0.01 | -100 | 0.1 | ℃
| 2C36 | 11318 | W | HeatTemp_Down_Limit | UINT21 | 0.01 | -100 | 0.1 | ℃
| 2C37 | 11319 | W | HeatTemp_Avg_Limit | UINT22 | 0.01 | -100 | 0.1 | ℃
| 2C38 | 11320 | W | Heat_Stop_Temp | UINT23 | 0.01 | -100 | 0.1 | ℃
| 2C39 | 11321 | W | Heat_Stop_Avg_Temp | UINT24 | 0.01 | -100 | 0.1 | ℃
| 2C3A | 11322 | W | Cycle_Start_Temp | UINT25 | 0.01 | -100 | 0.1 | ℃
| 2C3B | 11323 | W | Cycle_Stop_Temp | UINT26 | 0.01 | -100 | 0.1 | ℃
| 2C3C | 11324 | W | Cycle_Start_Avg_Start_Temp | UINT27 | 0.01 | -100 | 0.1 | ℃
| 2C3D | 11325 | W | Cycle_Start_Avg_Stop_Temp | UINT28 | 0.01 | -100 | 0.1 | ℃
| 2C3E | 11326 | W | Return_Water_Temp_Cycle | UINT29 | 0.01 | -100 | 0.1 | ℃
| 2C3F | 11327 | W | Cell_Temp_Diff_Start_Cycle | UINT30 | 0.01 | -100 | 0.1 | ℃
| 2C40 | 11328 | W | Cell_Temp_Diff_Stop_Cycle | UINT31 | 0.01 | -100 | 0.1 | ℃
| 2C41 | 11329 | W | Cycle_Stop_Temp | UINT32 | 0.01 | -100 | 0.1 | ℃
| 2C42 | 11330 | W | Cycle_Avg_Temp | UINT33 | 0.01 | -100 | 0.1 | ℃
| 2C88 | 11400 | W | reserve |  | 1 | 0 |  |  | 0
|  |  |  | System water shortage alarm | bit0
|  |  |  | 1# Condensing press too high alarm | bit1
|  |  |  | 2# Condensing press too high alarm | bit2
|  |  |  | Outlet water press too high alarm | bit3
|  |  |  | Inlet water press too low alarm | bit4
|  |  |  | Reserve | bit5-15
|  |  |  | Reserve | bit0-15
|  |  |  | 1# Discharge temp sensor failure | bit0
|  |  |  | 1# Condensation temp senor failure | bit1
|  |  |  | 2# Discharge temp sensor failure | bit2
|  |  |  | 2# Condensation temp senor failure | bit3
|  |  |  | Inlet water temp sensor failure | bit4
|  |  |  | Outlet water temp sensor failure | bit5
|  |  |  | Ambient temp sensor failure | bit6
|  |  |  | Abnormal power down alarm | bit7
|  |  |  | 1# High press sensor failure | bit8
|  |  |  | 2# High press sensor failure | bit9
|  |  |  | Water tank water level low | bit10
|  |  |  | Reserve | bit11
|  |  |  | Reserve | bit12
|  |  |  | Inlet water press sensor failure | bit13
|  |  |  | Outlet water press sensor failure | bit14
|  |  |  | Reserve | bit15
|  |  |  | Reserve | bit0-15
|  |  |  | 1# High press lock | bit0
|  |  |  | 1# Discharge over temp lock | bit1
|  |  |  | 1# System low press alarm lock | bit2
|  |  |  | 1# Low press sensor failure | bit3
|  |  |  | 1# Evap outlet temp senor failure | bit4
|  |  |  | 1# Comp freq converter failure | bit5
|  |  |  | 1# Comp freq converter commun failure | bit6
|  |  |  | 1# Outdoor fan freq converter failure | bit7
|  |  |  | 1# Outdoor fan freq converter commu failure | bit8
|  |  |  | 2# High press lock | bit9
|  |  |  | 2# Discharge over temp lock | bit10
|  |  |  | 2# System low press alarm lock | bit11
|  |  |  | 2# Low press sensor failure | bit12
|  |  |  | 2# Evap outlet temp senor failure | bit13
|  |  |  | 2# Comp freq converter failure | bit14
|  |  |  | 2# Comp freq converter commun failure | bit15
|  |  |  | Expansion module commun failure | bit0
|  |  |  | 2# Outdoor fan freq converter failure | bit1
|  |  |  | 2# Outdoor fan freq converter commu failure | bit2
|  |  |  | Water pump low press diff | bit3
|  |  |  | Inlet water temp sensor failure & Outlet water temp sensor failure | bit4
|  |  |  | Power supply failure | bit5
|  |  |  | Inlet water press sensor failure & Outlet water press sensor failure | bit6
|  |  |  | Reserve | bit7
|  |  |  | 1# Circulating water pump freq converter failure | bit8
|  |  |  | 1# Circulating water pump freq converter commun failure | bit9
|  |  |  | 1# Electrical heater failure lock | bit10
|  |  |  | Outlet water high temp | bit11
|  |  |  | Outlet water low temp | bit12
|  |  |  | 1# Circulating water pump superheat protection alarm lock | bit13
|  |  |  | 2# Circulating water pump superheat protection alarm lock | bit14
|  |  |  | 1# Circulating water pump overload protection lock | bit15
|  |  |  | 2# Circulating water pump overload protection lock | bit0
|  |  |  | 2# Circulating water pump freq converter failure | bit1
|  |  |  | 2# Circulating water pump freq converter commun failure | bit2
|  |  |  | 2# Electrical heater failure lock | bit3
|  |  |  | APF failure | bit4
|  |  |  | DC_DC1 module failure | bit5
|  |  |  | DC_DC2 module failure | bit6
|  |  |  | Reserve | bit7-15
|  |  |  | Reserve | bit0-15

## Dehumidification
Register Type | Register Address |  | Attributes | Meaning | Data Types | Coefficient | Offset | Decimal pointPrecision required | Units | Remarks
| Hexadecimal | Decimal
Read Dehumidification data (Modbus address starting from 101, input registers,function code 0x04) | 0E75 | 3701 | RO | Communication between BMS and Dehumidification | UINT16 | 1 | 0 |  |  | 0--normal, 1--fault
| 0E76 | 3702 | RO | reserve | UINT16
| 0E77 | 3703 | RO | Running state | UINT16 | 1 | 0 |  |  | 0--stop, 1--run
| 0E78 | 3704 | RO | Alarm state | UINT16 | 1 | 0 |  |  | 0--normal, 1--alarm
| 0E79 | 3705 | RO | reserve | UINT16 | 1 | 0
| 0ED8 | 3800 | RO | reserve | UINT16 | 1 | 0
The Above is the data of the UINT16 type , and the following is the data of the FLOAT Type
| 0ED9 | 3801 | RO | indoor temp | FLOAT | 1 | 0 | 0.1 | ℃
| 0EDB | 3803 | RO | indoor humidity | FLOAT | 1 | 0 | 0.1 | %RH
| 0EDD | 3805 | RO | Set start temperature | FLOAT | 1 | 0 | 0.1 | ℃
| 0EDF | 3807 | RO | Set differential temperature | FLOAT | 1 | 0 | 0.1 | ℃
| 0EE1 | 3809 | RO | Set start humidity | FLOAT | 1 | 0 | 0.1 | %RH
| 0EE3 | 3811 | RO | Set differential humidity | FLOAT | 1 | 0 | 0.1 | %RH
| 0EE5 | 3813 | RO | reserve | FLOAT | 1 | 0
| 0F9F | 3999 | RO | reserve | FLOAT | 1 | 0

## Setting
Register Type | Register Address |  | Attributes | Meaning | Data Types | Coefficient | Offset | Decimal pointPrecision required | Units | Remarks
| Hexadecimal | Decimal
Holding Register (System information, Modbus address 1) | 0001 | 1 | WR | delay time before DC Combiner Contactor open | UINT16 |  |  | 1 | s
| 0002 | 2 | WR | year | UINT16
| 0003 | 3 | WR | month | UINT16
| 0004 | 4 | WR | day | UINT16
| 0005 | 5 | WR | hour | UINT16
| 0006 | 6 | WR | minute | UINT16
| 0007 | 7 | WR | second | UINT16
| 0008 | 8 | WR | set date confirmation | UINT16 |  |  |  |  | Automatic reset after confirmation 1--confirm 0--reset
| 0009 | 9 | WR | reserve | UINT16
| 000A | 10 | WR | reserve | UINT16
| 000B | 11 | WR | Fault reset | UINT16 |  |  |  |  | 1 - clean falut
| 000C | 12 | WR
| 000D | 13 | WR
Holding Register (Modbus address 2) | 0001 | 1 | WR | positive contactor in HVB | UINT16 | 1 |  |  |  | 0 - BMS automatic control 1 - EMS forced close(no alarm) 2 - EMS forced open
| 0002 | 2 | WR | negative contactor in HVB | UINT16 | 1