EMS Gateway API, Data Model and Integration Specification
Stable Hardware-Verified Baseline - v1.0

Generated from the uploaded kinetics_grid_gateway_stable_baseline(2).zip codebase.
Audience: Frontend Team, Backend/API Team, Database Team, Dashboard Team, EMS Control Team

| Item | Value |
| --- | --- |
| Source package | kinetics_grid_gateway_stable_baseline(2).zip |
| Gateway folder analyzed | imx93_gateway/ |
| Main API port | 8000 - EMS Web API |
| Log API port | 7000 - HTTP Log API |
| TCP command port | 6000 - TCP Command Server |
| Document purpose | Field-level handoff contract for frontend/backend/database development |

# 1. Executive Overview

The EMS Gateway is an i.MX93 based integration backend that connects physical assets and simulators to web dashboards, Flutter/Desktop dashboards, historical log storage and future EMS control logic.

This document is based on the actual code structure of the stable baseline. It describes the REST APIs, log APIs, data fields, response envelopes, storage schemas, command model, health model and database integration recommendations exposed by the gateway.

The gateway is intentionally modular: asset communication is separated from web APIs, telemetry composition, command dispatching, storage/query handling, health monitoring and operator telemetry filtering.

# 2. Runtime Architecture and Network Ports

The stable baseline includes a small main.py entrypoint, an application orchestration layer, asset adapters, protocol descriptors, storage/query abstractions, health monitoring, dynamic asset runtime catalog and operator telemetry view.

The operating network model used during hardware testing is eth0 for Flutter/Desktop/PC side, eth1 for PCS/Inverter side and mlan0 for Wi-Fi Web Dashboard access.

The gateway exposes three major network services: TCP command server on port 6000, HTTP Log API on port 7000 and EMS Web API on port 8000.

| Service | Default Port | Primary Consumer | Purpose |
| --- | --- | --- | --- |
| EMS Web API | 8000 | Web dashboard, backend services | Asset catalog, latest telemetry, operator telemetry, health, diagnostics and commands |
| HTTP Log API | 7000 | Backend/database, dashboards, reporting tools | Historical telemetry/event/error logs, storage health and CSV download |
| TCP Command Server | 6000 | Flutter/Desktop dashboard | Legacy TCP command execution and telemetry/status commands |
| UDP Telemetry Streamer | 5005 destination | Flutter/Desktop dashboard | Realtime legacy-compatible telemetry broadcast to PC side |

# 3. Folder and Module Map

| Folder / file | Role in gateway | Why frontend/backend teams should care |
| --- | --- | --- |
| main.py | Small entrypoint that parses CLI and starts EMSGatewayApplication | Stable startup point; no API logic should be added here |
| core/app/gateway_application.py | Service orchestration and callback source for APIs | Runtime status/telemetry/command callbacks originate here |
| network/ems_web_api_server.py | REST API and SSE server on port 8000 | Primary source for frontend/backend API contracts |
| network/log_http_server.py | HTTP Log API server on port 7000 | Primary source for historical log/filter API contracts |
| core/assets/runtime_catalog.py | Dynamic asset catalog and RuntimeAssetRecord model | Defines fields exposed by /api/assets |
| core/operator_telemetry_view.py | Operator telemetry filter | Defines what dashboard operator view hides/preserves |
| core/health/health_monitor.py | Health and diagnostics response builder | Defines /api/health and /api/diagnostics response model |
| core/storage/query/* | LogFilter, LogQueryResult and CSVLogQueryBackend | Defines log filters and portable query abstraction |
| services/storage_logger.py | CSV storage backend and log schemas | Defines telemetry/event/error CSV fields |
| models/*.py | EMS-facing asset state models | Defines major data dictionaries for PCS/BMS/Chiller |
| drivers/bms_register_map.py | BMS register and control map | Defines BMS decoded signal source and control registers |
| drivers/pcs_profiles/* | PCS vendor profiles | Defines vendor-specific register maps/scaling |
| configs/*.json | Runtime profiles | Defines IPs, ports, asset profile config and deployment modes |

# 4. EMS Web API Endpoint Inventory - Port 8000

These endpoints are exposed by network/ems_web_api_server.py. They are the primary endpoints for the frontend dashboard and backend integration services.

| Method | Endpoint | Purpose | Query/body parameters | Response fields |
| --- | --- | --- | --- | --- |
| GET | / | API discovery root with endpoint list and server metadata |  | status, server, message, timestamp, endpoints |
| GET | /api/gateway/health | Lightweight Web API server liveness check |  | status, server, message, timestamp, host, port |
| GET | /api/health | Full overall gateway health model |  | status, timestamp, gateway_id, gateway, assets, summary |
| GET | /api/health/gateway | Gateway/service-level health |  | status, gateway_id, timestamp, mode, summary, services, recommended_action |
| GET | /api/health/assets | All asset health map |  | status, timestamp, summary, assets |
| GET | /api/health/assets/{asset_id} | Single asset health |  | status, asset_id, asset_key, asset_type, enabled, running, online, protocol, profile, vendor, connection, last_successful_poll, last_error, consecutive_failures, reason, recommended_action, storage |
| GET | /api/diagnostics | Gateway and all asset diagnostics |  | status, timestamp, gateway, diagnostics |
| GET | /api/diagnostics/assets/{asset_id} | Single asset diagnostics |  | status, timestamp, asset_id, diagnostics, health |
| GET | /api/gateway/status | Full runtime status packet |  | gateway_id, mode, chiller, pcs, bms, network, web_api, log_http, runtime_config, configured_assets, asset_factory_plan |
| GET | /api/gateway/network | Network endpoint summary for frontend/backends |  | gateway_id, tcp_command, udp_telemetry, log_http, web_api, note |
| GET | /api/assets | Runtime asset catalog from configured assets + active services + latest telemetry |  | status, gateway_id, timestamp, assets_count, assets, summary |
| GET | /api/assets/{asset_id} | Single runtime asset record |  | status, asset, timestamp |
| GET | /api/telemetry/latest | Latest full engineering telemetry packet | view=operator optional | type, gateway_id, asset_id, timestamp, data, pcs, bms, assets |
| GET | /api/telemetry/operator | Operator-filtered telemetry packet |  | Same as telemetry/latest but raw/debug/storage fields removed and view=operator |
| GET | /api/assets/{asset_id}/telemetry/latest | Latest engineering telemetry for one asset | view=operator optional | status, asset_id, asset_type, asset_key, timestamp, online, runtime_mode, telemetry |
| GET | /api/assets/{asset_id}/telemetry/operator | Operator-filtered latest telemetry for one asset |  | status, asset_id, asset_type, asset_key, timestamp, online, runtime_mode, telemetry, view |
| GET | /api/assets/{asset_id}/telemetry/keys | Flattened telemetry key list for dynamic frontend screens | view=operator optional | status, asset_id, asset_type, timestamp, keys_count, keys |
| GET | /api/assets/{asset_id}/telemetry/timeseries | Timeseries from log files for charting | key or keys, date, limit | status, asset_id, asset_type, timestamp, keys, date, points |
| GET | /api/stream/telemetry | Server-Sent Events stream for live dashboard | view=operator optional | SSE event: telemetry |
| POST | /api/commands | Generic command execution endpoint | JSON body: command, asset_id or asset_type, request_id, value/parameters | status, timestamp, asset_id, command, request_id, result |
| POST | /api/assets/{asset_id}/commands | Asset-scoped command execution endpoint | JSON body: command, request_id, value/parameters | status, timestamp, asset_id, command, request_id, result |

# 5. HTTP Log API Endpoint Inventory - Port 7000

These endpoints are exposed by network/log_http_server.py. They are intended for historical logs, reporting, database ingestion and CSV export.

| Method | Endpoint | Purpose | Query parameters | Response fields |
| --- | --- | --- | --- | --- |
| GET | / | Log API discovery root |  | status, server, message, endpoints |
| GET | /api/health | Log HTTP server liveness |  | status, server, timestamp |
| GET | /api/logs/assets | List assets with log folders/files |  | status, base_path, assets |
| GET | /api/storage/status | Storage/log file status | asset_id optional | status, asset_id, base_path, telemetry_dir_exists, files, sizes, disk fields |
| GET | /api/storage/health | Operator/diagnostic storage health | asset_id optional | status, message, asset_id, base_path, disk_total_bytes, disk_used_bytes, disk_free_bytes, disk_used_percent, log_total_bytes |
| GET | /api/logs/files | List telemetry/event/error files for asset | asset_id optional | status, asset_id, telemetry_files, event_file, error_file |
| GET | /api/logs/telemetry | Query historical telemetry logs | asset_id, date required, start_time, end_time, fields, exact filters, search, limit, offset, order | status, log_type, asset_id, date, rows, total_rows, filtered_rows, rows_count, filters |
| GET | /api/logs/events | Query event logs | asset_id, event_type, status, source, vendor, command, search, fields, date/time, limit, offset, order | status, log_type, asset_id, rows, total_rows, filtered_rows, rows_count, filters |
| GET | /api/logs/errors | Query error logs | asset_id, error_type, error_source or source, search, fields, date/time, limit, offset, order | status, log_type, asset_id, rows, total_rows, filtered_rows, rows_count, filters |
| GET | /api/logs/metadata | Gateway metadata text from storage |  | status, metadata_file, content |
| GET | /api/logs/download/telemetry | Download telemetry CSV | asset_id, date required | text/csv attachment |

# 6. Runtime Asset Catalog Field Dictionary

The /api/assets endpoint is based on RuntimeAssetCatalog and RuntimeAssetRecord. Frontend code should use this endpoint for asset discovery instead of hardcoding PCS/BMS/Chiller cards.

| Field | Type | Default | Meaning |
| --- | --- | --- | --- |
| asset_id | str |  | Unique asset identifier, for example pcs_1, bms_1, chiller_1. |
| asset_key | str |  | Normalized key used internally for routing, for example pcs/bms/chiller. |
| asset_type | str |  | Logical asset type such as pcs, bms, chiller or future asset type. |
| enabled | bool | False | Whether asset is enabled by config/CLI. |
| running | bool | False | Whether active runtime service is currently running. |
| online | bool | False | Whether latest telemetry/status indicates online communication. |
| protocol | Optional[str] | None | Communication protocol such as modbus_tcp, modbus_rtu, can or mock. |
| profile | Optional[str] | None | Vendor/profile name used for register map and scaling. |
| vendor | Optional[str] | None | Vendor/profile family. |
| configured | bool | False | Runtime asset catalog field exposed in /api/assets responses. |
| telemetry_available | bool | False | Whether latest telemetry exists for this asset. |
| runtime_mode | str | 'configured_only' | active_service, configured_only, configured_future or disabled. |
| compatibility | JsonDict |  | Runtime asset catalog field exposed in /api/assets responses. |
| connection | JsonDict |  | Connection metadata like host/port/unit_id or serial settings. |
| metadata | JsonDict |  | Free-form extra asset metadata. |

# 7. /api/assets - Runtime Asset Catalog

| Item | Details |
| --- | --- |
| Endpoint | GET /api/assets |
| Purpose | Returns every configured/active asset after merging asset config, runtime status and latest telemetry. Use it to create dynamic asset cards. |
| Important response fields | status, gateway_id, timestamp, assets_count, assets, summary |
| Recommended consumer | Web dashboard / backend integration service |

# 8. /api/assets/{asset_id} - Asset Details

| Item | Details |
| --- | --- |
| Endpoint | GET /api/assets/pcs_1 |
| Purpose | Returns one RuntimeAssetRecord. Use for asset detail screens and dynamic configuration displays. |
| Important response fields | status, asset, timestamp |
| Recommended consumer | Web dashboard / backend integration service |

# 9. /api/telemetry/latest - Full Engineering Telemetry

| Item | Details |
| --- | --- |
| Endpoint | GET /api/telemetry/latest |
| Purpose | Returns the combined latest engineering telemetry packet. It may include raw/debug/storage fields and is better for backend/engineering tools than operator dashboard grids. |
| Important response fields | type, gateway_id, asset_id, timestamp, data, pcs, bms, assets |
| Recommended consumer | Web dashboard / backend integration service |

# 10. /api/telemetry/operator - Operator Telemetry

| Item | Details |
| --- | --- |
| Endpoint | GET /api/telemetry/operator |
| Purpose | Returns telemetry filtered for operational dashboards. It removes raw register arrays, storage_logger, *_raw fields and internal/debug fields. |
| Important response fields | view, type/status, gateway_id, asset_id, timestamp, data, pcs, bms, assets |
| Recommended consumer | Web dashboard / backend integration service |

# 11. /api/assets/{asset_id}/telemetry/latest

| Item | Details |
| --- | --- |
| Endpoint | GET /api/assets/bms_1/telemetry/latest |
| Purpose | Returns latest telemetry for a selected asset. This is useful for asset detail cards and backend ingestion of single asset data. |
| Important response fields | status, asset_id, asset_type, asset_key, timestamp, online, runtime_mode, telemetry |
| Recommended consumer | Web dashboard / backend integration service |

# 12. /api/assets/{asset_id}/telemetry/keys

| Item | Details |
| --- | --- |
| Endpoint | GET /api/assets/pcs_1/telemetry/keys?view=operator |
| Purpose | Returns flattened telemetry keys. Use this for dynamic table/chart field pickers. |
| Important response fields | status, asset_id, asset_type, timestamp, keys_count, keys |
| Recommended consumer | Web dashboard / backend integration service |

# 13. /api/assets/{asset_id}/telemetry/timeseries

| Item | Details |
| --- | --- |
| Endpoint | GET /api/assets/pcs_1/telemetry/timeseries?keys=active_power_kw,dc_voltage_v&date=YYYY-MM-DD&limit=100 |
| Purpose | Builds chart-ready points from CSV logs through LogQueryService. This endpoint is suitable for trend charts. |
| Important response fields | status, asset_id, asset_type, timestamp, keys, date, points |
| Recommended consumer | Web dashboard / backend integration service |

# 14. /api/stream/telemetry - SSE

| Item | Details |
| --- | --- |
| Endpoint | GET /api/stream/telemetry?view=operator |
| Purpose | Streams latest telemetry as Server-Sent Events. Use for live browser dashboards where polling is undesirable. |
| Important response fields | event: telemetry, data: JSON telemetry packet |
| Recommended consumer | Web dashboard / backend integration service |

# 15. Operator Telemetry Filtering Contract

Operator telemetry is generated by core/operator_telemetry_view.py. This filter allows the gateway to keep full engineering telemetry while exposing a clean dashboard view.

Hidden exact key

control_mode_raw

debug

diagnostics

fault_active_bits

fault_binary

internal

on_off_raw

on_off_status_raw

raw_log_response

raw_registers

raw_telemetry_registers

register_map

set_temperature_raw

settings_registers_200_to_208

storage_logger

Hidden key substring

raw_telemetry

raw_register

registers_

_registers

register_block

storage_logger

logger_

_logger

debug

internal

binary

active_bits

Allowed top-level key

asset_id

asset_type

assets

bms

chiller

data

gateway_id

last_poll_time

message

online

pcs

status

telemetry

timestamp

type

# 16. Health and Diagnostics API Data Model

Health APIs are built by core/health/health_monitor.py. Health is distinct from telemetry: telemetry tells what values are; health tells whether the gateway can trust those values and what action should be taken.

| Field | Meaning |
| --- | --- |
| status | Status string such as ok, error, healthy, degraded, offline, disabled. |
| gateway_id | Identifier of the gateway instance. |
| timestamp | ISO timestamp for the sample or response. |
| mode | Health/diagnostics response field generated by HealthMonitor. |
| summary | Health/diagnostics response field generated by HealthMonitor. |
| services | Health/diagnostics response field generated by HealthMonitor. |
| recommended_action | Action for operator/backend team to troubleshoot an unhealthy state. |
| asset_id | Unique asset identifier, for example pcs_1, bms_1, chiller_1. |
| asset_key | Normalized key used internally for routing, for example pcs/bms/chiller. |
| asset_type | Logical asset type such as pcs, bms, chiller or future asset type. |
| enabled | Whether asset is enabled by config/CLI. |
| running | Whether active runtime service is currently running. |
| online | Whether latest telemetry/status indicates online communication. |
| protocol | Communication protocol such as modbus_tcp, modbus_rtu, can or mock. |
| profile | Vendor/profile name used for register map and scaling. |
| vendor | Vendor/profile family. |
| connection | Connection metadata like host/port/unit_id or serial settings. |
| last_successful_poll | Timestamp of last successful communication if available. |
| last_error | Latest communication, storage or service error. |
| consecutive_failures | Failure count used by diagnostics/health layers. |
| reason | Human-readable reason for health state. |
| storage | Nested storage health/status for the asset. |

| Status value | Meaning | Frontend color recommendation |
| --- | --- | --- |
| healthy | Asset/service is running and latest state is acceptable | Green |
| degraded | Service may be running but telemetry/storage/error status indicates warning/error | Orange/Yellow |
| offline | Enabled asset/service is not running or communication failed | Red |
| disabled | Asset/service disabled by config/CLI | Grey |
| unknown | Not enough information available yet | Grey |

# 17. Command API and Command Dictionary

Commands can be sent through POST /api/commands or POST /api/assets/{asset_id}/commands. The command dispatcher routes packets based on command prefix, asset_id or asset_type.

| Asset route | Command(s) | Meaning | Notes |
| --- | --- | --- | --- |
| Gateway | STATUS, GATEWAY_STATUS | Read gateway status packet | No write to physical asset |
| Gateway | READ_ALL_ASSETS, READ_GATEWAY_TELEMETRY | Read combined telemetry packet | No write to physical asset |
| PCS | PCS_READ | Read PCS status/telemetry | Routed to PCS asset |
| PCS | PCS_STATUS | Read PCS status/telemetry | Routed to PCS asset |
| PCS | READ_PCS | Read PCS status/telemetry | Routed to PCS asset |
| PCS | PCS_POWER_ON | PCS control command. | Logged as PCS event |
| PCS | PCS_POWER_OFF | PCS control command. | Logged as PCS event |
| PCS | PCS_SET_ACTIVE_POWER | PCS write/control command. SET_ACTIVE_POWER expects active power value; SET_REACTIVE_POWER expects reactive power value. | Logged as PCS event |
| PCS | PCS_SET_REACTIVE_POWER | PCS write/control command. SET_ACTIVE_POWER expects active power value; SET_REACTIVE_POWER expects reactive power value. | Logged as PCS event |
| PCS | PCS_RESET_FAULT | PCS write/control command. SET_ACTIVE_POWER expects active power value; SET_REACTIVE_POWER expects reactive power value. | Logged as PCS event |
| PCS | PCS_HEARTBEAT | PCS control command. | Logged as PCS event |
| PCS | PCS_STANDBY | PCS control command. | Logged as PCS event |
| BMS | READ_BMS | BMS read/control command | Routed to BMS service/driver |
| BMS | READ_BMS_ALARMS | BMS read/control command | Routed to BMS service/driver |
| BMS | READ_BMS_ALL | BMS read/control command | Routed to BMS service/driver |
| BMS | RESET_BCU | BMS read/control command | Routed to BMS service/driver |
| BMS | RESET_BMS | BMS read/control command | Routed to BMS service/driver |
| BMS | START_BMS_INSULATION_TEST | BMS read/control command | Routed to BMS service/driver |
| BMS | START_BMS_PRECHARGE | BMS read/control command | Routed to BMS service/driver |
| BMS | START_INSULATION_TEST | BMS read/control command | Routed to BMS service/driver |
| BMS | STOP_BMS_PRECHARGE | BMS read/control command | Routed to BMS service/driver |
| BMS | BMS_FAN_AUTO | BMS fan control wrapper command | Available through BMS service convenience methods |
| BMS | BMS_FAN_ON | BMS fan control wrapper command | Available through BMS service convenience methods |
| BMS | BMS_FAN_OFF | BMS fan control wrapper command | Available through BMS service convenience methods |
| Chiller | READ_ALL | Chiller read/write command | Default legacy route for dashboard commands |
| Chiller | READ_TEMP | Chiller read/write command | Default legacy route for dashboard commands |
| Chiller | READ_ONOFF | Chiller read/write command | Default legacy route for dashboard commands |
| Chiller | READ_MODE | Chiller read/write command | Default legacy route for dashboard commands |
| Chiller | READ_SETTINGS | Chiller read/write command | Default legacy route for dashboard commands |
| Chiller | SET_TEMP | Chiller read/write command | Default legacy route for dashboard commands |
| Chiller | SET_MODE | Chiller read/write command | Default legacy route for dashboard commands |
| Chiller | CHILLER_ON | Chiller read/write command | Default legacy route for dashboard commands |
| Chiller | CHILLER_OFF | Chiller read/write command | Default legacy route for dashboard commands |

| Request field | Required | Meaning |
| --- | --- | --- |
| command | Yes | Command name normalized to uppercase before dispatch |
| asset_id | Required for /api/commands, injected by /api/assets/{asset_id}/commands | Target asset id such as pcs_1 or bms_1 |
| asset_type | Alternative to asset_id for generic command route | Target type such as pcs/bms/chiller |
| request_id | Optional | Correlation identifier; generated if absent |
| value | Command-dependent | Setpoint value for commands such as SET_TEMP or PCS_SET_ACTIVE_POWER |
| client/source | Auto-added by API server | Source IP and web_api source string |

# 18. Chiller Telemetry Field Dictionary

| Field | Type | Default | Meaning |
| --- | --- | --- | --- |
| water_pump | Optional[str] | None | Decoded chiller engineering telemetry field. |
| compressor1 | Optional[str] | None | Decoded chiller engineering telemetry field. |
| compressor2 | Optional[str] | None | Decoded chiller engineering telemetry field. |
| electric_heater | Optional[str] | None | Decoded chiller engineering telemetry field. |
| condensate_fan | Optional[str] | None | Decoded chiller engineering telemetry field. |
| makeup_pump | Optional[str] | None | Decoded chiller engineering telemetry field. |
| outlet_water_temp | Optional[float] | None | Decoded chiller engineering telemetry field. |
| return_water_temp | Optional[float] | None | Decoded chiller engineering telemetry field. |
| outlet_water_pressure | Optional[float] | None | Decoded chiller engineering telemetry field. |
| return_water_pressure | Optional[float] | None | Decoded chiller engineering telemetry field. |
| ambient_temp | Optional[float] | None | Decoded chiller engineering telemetry field. |
| fault_code | Optional[int] | None | Decoded chiller engineering telemetry field. |
| control_mode | Optional[int] | None | Decoded chiller engineering telemetry field. |
| set_temperature | Optional[float] | None | Decoded chiller engineering telemetry field. |
| communication_status | <class 'str'> | 'unknown' | Decoded chiller engineering telemetry field. |
| last_update_time | Optional[str] | None | Decoded chiller engineering telemetry field. |

# 19. PCS Telemetry Field Dictionary

| Field | Type | Default | Meaning |
| --- | --- | --- | --- |
| asset_id | <class 'str'> | 'pcs_1' | Unique asset identifier, for example pcs_1, bms_1, chiller_1. |
| vendor | <class 'str'> | 'njoy' | Vendor/profile family. |
| comm_status | <class 'str'> | 'offline' | Vendor-independent PCS/Inverter telemetry or status field. |
| last_update_ts | <class 'str'> | '' | Vendor-independent PCS/Inverter telemetry or status field. |
| error | <class 'str'> | '' | Vendor-independent PCS/Inverter telemetry or status field. |
| ab_voltage_v | Optional[float] | None | Vendor-independent PCS/Inverter telemetry or status field. |
| bc_voltage_v | Optional[float] | None | Vendor-independent PCS/Inverter telemetry or status field. |
| ca_voltage_v | Optional[float] | None | Vendor-independent PCS/Inverter telemetry or status field. |
| phase_a_voltage_v | Optional[float] | None | Vendor-independent PCS/Inverter telemetry or status field. |
| phase_b_voltage_v | Optional[float] | None | Vendor-independent PCS/Inverter telemetry or status field. |
| phase_c_voltage_v | Optional[float] | None | Vendor-independent PCS/Inverter telemetry or status field. |
| phase_a_current_a | Optional[float] | None | Vendor-independent PCS/Inverter telemetry or status field. |
| phase_b_current_a | Optional[float] | None | Vendor-independent PCS/Inverter telemetry or status field. |
| phase_c_current_a | Optional[float] | None | Vendor-independent PCS/Inverter telemetry or status field. |
| frequency_hz | Optional[float] | None | Vendor-independent PCS/Inverter telemetry or status field. |
| active_power_kw | Optional[float] | None | Vendor-independent PCS/Inverter telemetry or status field. |
| reactive_power_kvar | Optional[float] | None | Vendor-independent PCS/Inverter telemetry or status field. |
| apparent_power_kva | Optional[float] | None | Vendor-independent PCS/Inverter telemetry or status field. |
| power_factor | Optional[float] | None | Vendor-independent PCS/Inverter telemetry or status field. |
| bus_voltage_v | Optional[float] | None | Vendor-independent PCS/Inverter telemetry or status field. |
| battery_voltage_v | Optional[float] | None | Vendor-independent PCS/Inverter telemetry or status field. |
| battery_current_a | Optional[float] | None | Vendor-independent PCS/Inverter telemetry or status field. |
| dc_power_kw | Optional[float] | None | Vendor-independent PCS/Inverter telemetry or status field. |
| dc_total_current_a | Optional[float] | None | Vendor-independent PCS/Inverter telemetry or status field. |
| operating_status_raw | Optional[int] | None | Vendor-independent PCS/Inverter telemetry or status field. |
| operating_status | <class 'str'> | 'unknown' | Vendor-independent PCS/Inverter telemetry or status field. |
| grid_offgrid_status_raw | Optional[int] | None | Vendor-independent PCS/Inverter telemetry or status field. |
| grid_offgrid_status | <class 'str'> | 'unknown' | Vendor-independent PCS/Inverter telemetry or status field. |
| fault_status | <class 'bool'> | False | Vendor-independent PCS/Inverter telemetry or status field. |
| hardware_fault_word_1_raw | Optional[int] | None | Vendor-independent PCS/Inverter telemetry or status field. |
| hardware_fault_word_2_raw | Optional[int] | None | Vendor-independent PCS/Inverter telemetry or status field. |
| grid_fault_word_raw | Optional[int] | None | Vendor-independent PCS/Inverter telemetry or status field. |
| bus_fault_word_raw | Optional[int] | None | Vendor-independent PCS/Inverter telemetry or status field. |
| ac_capacitor_fault_word_raw | Optional[int] | None | Vendor-independent PCS/Inverter telemetry or status field. |
| system_fault_word_raw | Optional[int] | None | Vendor-independent PCS/Inverter telemetry or status field. |
| switch_fault_word_raw | Optional[int] | None | Vendor-independent PCS/Inverter telemetry or status field. |
| other_fault_word_raw | Optional[int] | None | Vendor-independent PCS/Inverter telemetry or status field. |
| fault_words_raw | Dict[str, Any] | factory/default list or dict | Vendor-independent PCS/Inverter telemetry or status field. |
| fault_categories | Dict[str, Any] | factory/default list or dict | Vendor-independent PCS/Inverter telemetry or status field. |
| active_faults | List[str] | factory/default list or dict | Vendor-independent PCS/Inverter telemetry or status field. |
| fault_count | <class 'int'> | 0 | Vendor-independent PCS/Inverter telemetry or status field. |
| detailed_fault_status | <class 'bool'> | False | Vendor-independent PCS/Inverter telemetry or status field. |
| fault_words_read_error | <class 'str'> | '' | Vendor-independent PCS/Inverter telemetry or status field. |
| igbt_temperature_c | Optional[float] | None | Vendor-independent PCS/Inverter telemetry or status field. |
| ambient_temperature_c | Optional[float] | None | Vendor-independent PCS/Inverter telemetry or status field. |
| inductance_temperature_c | Optional[float] | None | Vendor-independent PCS/Inverter telemetry or status field. |
| raw_telemetry | Dict[str, Any] | factory/default list or dict | Vendor-independent PCS/Inverter telemetry or status field. |

# 20. BMS Telemetry Field Dictionary

| Field | Type | Default | Meaning |
| --- | --- | --- | --- |
| gateway_id | str | 'imx93_gateway_1' | Identifier of the gateway instance. |
| asset_id | str | 'bms_1' | Unique asset identifier, for example pcs_1, bms_1, chiller_1. |
| timestamp | str | factory/default list or dict | ISO timestamp for the sample or response. |
| communication_status | str | 'unknown' | EMS-facing BMS/BCU telemetry, health, alarm or status field. |
| last_error | Optional[str] | None | Latest communication, storage or service error. |
| last_success_ts | Optional[float] | None | EMS-facing BMS/BCU telemetry, health, alarm or status field. |
| soc_percent | Optional[float] | None | EMS-facing BMS/BCU telemetry, health, alarm or status field. |
| soh_percent | Optional[float] | None | EMS-facing BMS/BCU telemetry, health, alarm or status field. |
| rack_inner_soc_percent | Optional[float] | None | EMS-facing BMS/BCU telemetry, health, alarm or status field. |
| rack_voltage_v | Optional[float] | None | EMS-facing BMS/BCU telemetry, health, alarm or status field. |
| rack_current_a | Optional[float] | None | EMS-facing BMS/BCU telemetry, health, alarm or status field. |
| power_kw | Optional[float] | None | EMS-facing BMS/BCU telemetry, health, alarm or status field. |
| max_allowed_charge_current_a | Optional[float] | None | EMS-facing BMS/BCU telemetry, health, alarm or status field. |
| max_allowed_discharge_current_a | Optional[float] | None | EMS-facing BMS/BCU telemetry, health, alarm or status field. |
| max_cell_voltage_mv | Optional[float] | None | EMS-facing BMS/BCU telemetry, health, alarm or status field. |
| min_cell_voltage_mv | Optional[float] | None | EMS-facing BMS/BCU telemetry, health, alarm or status field. |
| avg_cell_voltage_mv | Optional[float] | None | EMS-facing BMS/BCU telemetry, health, alarm or status field. |
| cell_voltage_diff_mv | Optional[float] | None | EMS-facing BMS/BCU telemetry, health, alarm or status field. |
| max_cell_temp_c | Optional[float] | None | EMS-facing BMS/BCU telemetry, health, alarm or status field. |
| min_cell_temp_c | Optional[float] | None | EMS-facing BMS/BCU telemetry, health, alarm or status field. |
| avg_temp_c | Optional[float] | None | EMS-facing BMS/BCU telemetry, health, alarm or status field. |
| max_temp_diff_c | Optional[float] | None | EMS-facing BMS/BCU telemetry, health, alarm or status field. |
| insulation_resistance_kohm | Optional[float] | None | EMS-facing BMS/BCU telemetry, health, alarm or status field. |
| positive_insulation_resistance_kohm | Optional[float] | None | EMS-facing BMS/BCU telemetry, health, alarm or status field. |
| negative_insulation_resistance_kohm | Optional[float] | None | EMS-facing BMS/BCU telemetry, health, alarm or status field. |
| precharge_stage | Optional[str] | None | EMS-facing BMS/BCU telemetry, health, alarm or status field. |
| bcu_state | Optional[str] | None | EMS-facing BMS/BCU telemetry, health, alarm or status field. |
| current_state | Optional[str] | None | EMS-facing BMS/BCU telemetry, health, alarm or status field. |
| heartbeat | Optional[int] | None | EMS-facing BMS/BCU telemetry, health, alarm or status field. |
| contactor_active_flags | List[str] | factory/default list or dict | EMS-facing BMS/BCU telemetry, health, alarm or status field. |
| positive_contactor_closed | bool | False | EMS-facing BMS/BCU telemetry, health, alarm or status field. |
| precharge_contactor_closed | bool | False | EMS-facing BMS/BCU telemetry, health, alarm or status field. |
| negative_contactor_closed | bool | False | EMS-facing BMS/BCU telemetry, health, alarm or status field. |
| active_alarms | List[str] | factory/default list or dict | EMS-facing BMS/BCU telemetry, health, alarm or status field. |
| alarm_count | int | 0 | EMS-facing BMS/BCU telemetry, health, alarm or status field. |
| raw | Dict[str, Any] | factory/default list or dict | EMS-facing BMS/BCU telemetry, health, alarm or status field. |

# 21. CSV Storage Schemas

The CSV schemas are defined in services/storage_logger.py. The Log API and database ingestion should treat these headers as the canonical historical log fields for the current CSV backend.

## chiller_telemetry_header

| # | Field | Meaning |
| --- | --- | --- |
| 1 | timestamp | ISO timestamp for the sample or response. |
| 2 | sequence_no | Monotonic logger sequence number per logger instance. |
| 3 | gateway_id | Identifier of the gateway instance. |
| 4 | asset_id | Unique asset identifier, for example pcs_1, bms_1, chiller_1. |
| 5 | system_on_off | CSV field written by StorageLogger for this log type. |
| 6 | control_mode | CSV field written by StorageLogger for this log type. |
| 7 | set_temperature | CSV field written by StorageLogger for this log type. |
| 8 | outlet_water_temp | CSV field written by StorageLogger for this log type. |
| 9 | return_water_temp | CSV field written by StorageLogger for this log type. |
| 10 | outlet_water_pressure | CSV field written by StorageLogger for this log type. |
| 11 | return_water_pressure | CSV field written by StorageLogger for this log type. |
| 12 | ambient_temp | CSV field written by StorageLogger for this log type. |
| 13 | water_pump_status | CSV field written by StorageLogger for this log type. |
| 14 | compressor_1_status | CSV field written by StorageLogger for this log type. |
| 15 | compressor_2_status | CSV field written by StorageLogger for this log type. |
| 16 | electric_heater_status | CSV field written by StorageLogger for this log type. |
| 17 | condensate_fan_status | CSV field written by StorageLogger for this log type. |
| 18 | modbus_status | CSV field written by StorageLogger for this log type. |
| 19 | logger_status | CSV field written by StorageLogger for this log type. |

## pcs_telemetry_header

| # | Field | Meaning |
| --- | --- | --- |
| 1 | timestamp | ISO timestamp for the sample or response. |
| 2 | sequence_no | Monotonic logger sequence number per logger instance. |
| 3 | gateway_id | Identifier of the gateway instance. |
| 4 | asset_id | Unique asset identifier, for example pcs_1, bms_1, chiller_1. |
| 5 | vendor | Vendor/profile family. |
| 6 | comm_status | CSV field written by StorageLogger for this log type. |
| 7 | active_power_kw | CSV field written by StorageLogger for this log type. |
| 8 | reactive_power_kvar | CSV field written by StorageLogger for this log type. |
| 9 | apparent_power_kva | CSV field written by StorageLogger for this log type. |
| 10 | power_factor | CSV field written by StorageLogger for this log type. |
| 11 | frequency_hz | CSV field written by StorageLogger for this log type. |
| 12 | battery_voltage_v | CSV field written by StorageLogger for this log type. |
| 13 | battery_current_a | CSV field written by StorageLogger for this log type. |
| 14 | dc_power_kw | CSV field written by StorageLogger for this log type. |
| 15 | dc_total_current_a | CSV field written by StorageLogger for this log type. |
| 16 | bus_voltage_v | CSV field written by StorageLogger for this log type. |
| 17 | ab_voltage_v | CSV field written by StorageLogger for this log type. |
| 18 | bc_voltage_v | CSV field written by StorageLogger for this log type. |
| 19 | ca_voltage_v | CSV field written by StorageLogger for this log type. |
| 20 | phase_a_voltage_v | CSV field written by StorageLogger for this log type. |
| 21 | phase_b_voltage_v | CSV field written by StorageLogger for this log type. |
| 22 | phase_c_voltage_v | CSV field written by StorageLogger for this log type. |
| 23 | phase_a_current_a | CSV field written by StorageLogger for this log type. |
| 24 | phase_b_current_a | CSV field written by StorageLogger for this log type. |
| 25 | phase_c_current_a | CSV field written by StorageLogger for this log type. |
| 26 | operating_status | CSV field written by StorageLogger for this log type. |
| 27 | operating_status_raw | CSV field written by StorageLogger for this log type. |
| 28 | grid_offgrid_status | CSV field written by StorageLogger for this log type. |
| 29 | grid_offgrid_status_raw | CSV field written by StorageLogger for this log type. |
| 30 | fault_status | CSV field written by StorageLogger for this log type. |
| 31 | detailed_fault_status | CSV field written by StorageLogger for this log type. |
| 32 | fault_count | CSV field written by StorageLogger for this log type. |
| 33 | hardware_fault_word_1_raw | CSV field written by StorageLogger for this log type. |
| 34 | hardware_fault_word_2_raw | CSV field written by StorageLogger for this log type. |
| 35 | grid_fault_word_raw | CSV field written by StorageLogger for this log type. |
| 36 | bus_fault_word_raw | CSV field written by StorageLogger for this log type. |
| 37 | ac_capacitor_fault_word_raw | CSV field written by StorageLogger for this log type. |
| 38 | system_fault_word_raw | CSV field written by StorageLogger for this log type. |
| 39 | switch_fault_word_raw | CSV field written by StorageLogger for this log type. |
| 40 | other_fault_word_raw | CSV field written by StorageLogger for this log type. |
| 41 | active_faults | CSV field written by StorageLogger for this log type. |
| 42 | fault_words_read_error | CSV field written by StorageLogger for this log type. |
| 43 | igbt_temperature_c | CSV field written by StorageLogger for this log type. |
| 44 | ambient_temperature_c | CSV field written by StorageLogger for this log type. |
| 45 | inductance_temperature_c | CSV field written by StorageLogger for this log type. |
| 46 | error | CSV field written by StorageLogger for this log type. |
| 47 | logger_status | CSV field written by StorageLogger for this log type. |

## bms_telemetry_header

| # | Field | Meaning |
| --- | --- | --- |
| 1 | timestamp | ISO timestamp for the sample or response. |
| 2 | sequence_no | Monotonic logger sequence number per logger instance. |
| 3 | gateway_id | Identifier of the gateway instance. |
| 4 | asset_id | Unique asset identifier, for example pcs_1, bms_1, chiller_1. |
| 5 | communication_status | CSV field written by StorageLogger for this log type. |
| 6 | soc_percent | CSV field written by StorageLogger for this log type. |
| 7 | soh_percent | CSV field written by StorageLogger for this log type. |
| 8 | rack_inner_soc_percent | CSV field written by StorageLogger for this log type. |
| 9 | rack_voltage_v | CSV field written by StorageLogger for this log type. |
| 10 | rack_current_a | CSV field written by StorageLogger for this log type. |
| 11 | power_kw | CSV field written by StorageLogger for this log type. |
| 12 | max_allowed_charge_current_a | CSV field written by StorageLogger for this log type. |
| 13 | max_allowed_discharge_current_a | CSV field written by StorageLogger for this log type. |
| 14 | max_cell_voltage_mv | CSV field written by StorageLogger for this log type. |
| 15 | min_cell_voltage_mv | CSV field written by StorageLogger for this log type. |
| 16 | avg_cell_voltage_mv | CSV field written by StorageLogger for this log type. |
| 17 | cell_voltage_diff_mv | CSV field written by StorageLogger for this log type. |
| 18 | max_cell_temp_c | CSV field written by StorageLogger for this log type. |
| 19 | min_cell_temp_c | CSV field written by StorageLogger for this log type. |
| 20 | avg_temp_c | CSV field written by StorageLogger for this log type. |
| 21 | insulation_resistance_kohm | CSV field written by StorageLogger for this log type. |
| 22 | positive_insulation_resistance_kohm | CSV field written by StorageLogger for this log type. |
| 23 | negative_insulation_resistance_kohm | CSV field written by StorageLogger for this log type. |
| 24 | precharge_stage | CSV field written by StorageLogger for this log type. |
| 25 | bcu_state | CSV field written by StorageLogger for this log type. |
| 26 | current_state | CSV field written by StorageLogger for this log type. |
| 27 | positive_contactor_closed | CSV field written by StorageLogger for this log type. |
| 28 | precharge_contactor_closed | CSV field written by StorageLogger for this log type. |
| 29 | negative_contactor_closed | CSV field written by StorageLogger for this log type. |
| 30 | alarm_count | CSV field written by StorageLogger for this log type. |
| 31 | active_alarms | CSV field written by StorageLogger for this log type. |
| 32 | contactor_active_flags | CSV field written by StorageLogger for this log type. |
| 33 | last_error | Latest communication, storage or service error. |
| 34 | logger_status | CSV field written by StorageLogger for this log type. |

## chiller_event_header

| # | Field | Meaning |
| --- | --- | --- |
| 1 | timestamp | ISO timestamp for the sample or response. |
| 2 | gateway_id | Identifier of the gateway instance. |
| 3 | asset_id | Unique asset identifier, for example pcs_1, bms_1, chiller_1. |
| 4 | event_type | CSV field written by StorageLogger for this log type. |
| 5 | old_value | CSV field written by StorageLogger for this log type. |
| 6 | new_value | CSV field written by StorageLogger for this log type. |
| 7 | source | CSV field written by StorageLogger for this log type. |
| 8 | status | Status string such as ok, error, healthy, degraded, offline, disabled. |
| 9 | description | CSV field written by StorageLogger for this log type. |

## pcs_event_header

| # | Field | Meaning |
| --- | --- | --- |
| 1 | timestamp | ISO timestamp for the sample or response. |
| 2 | gateway_id | Identifier of the gateway instance. |
| 3 | asset_id | Unique asset identifier, for example pcs_1, bms_1, chiller_1. |
| 4 | vendor | Vendor/profile family. |
| 5 | event_type | CSV field written by StorageLogger for this log type. |
| 6 | command | Command string being executed. |
| 7 | old_value | CSV field written by StorageLogger for this log type. |
| 8 | new_value | CSV field written by StorageLogger for this log type. |
| 9 | readback_value | CSV field written by StorageLogger for this log type. |
| 10 | source | CSV field written by StorageLogger for this log type. |
| 11 | status | Status string such as ok, error, healthy, degraded, offline, disabled. |
| 12 | description | CSV field written by StorageLogger for this log type. |
| 13 | error | CSV field written by StorageLogger for this log type. |

## bms_event_header

| # | Field | Meaning |
| --- | --- | --- |
| 1 | timestamp | ISO timestamp for the sample or response. |
| 2 | gateway_id | Identifier of the gateway instance. |
| 3 | asset_id | Unique asset identifier, for example pcs_1, bms_1, chiller_1. |
| 4 | event_type | CSV field written by StorageLogger for this log type. |
| 5 | command | Command string being executed. |
| 6 | status | Status string such as ok, error, healthy, degraded, offline, disabled. |
| 7 | description | CSV field written by StorageLogger for this log type. |
| 8 | message | Human-readable response summary. |
| 9 | communication_status | CSV field written by StorageLogger for this log type. |
| 10 | soc_percent | CSV field written by StorageLogger for this log type. |
| 11 | rack_voltage_v | CSV field written by StorageLogger for this log type. |
| 12 | rack_current_a | CSV field written by StorageLogger for this log type. |
| 13 | precharge_stage | CSV field written by StorageLogger for this log type. |
| 14 | bcu_state | CSV field written by StorageLogger for this log type. |
| 15 | current_state | CSV field written by StorageLogger for this log type. |
| 16 | alarm_count | CSV field written by StorageLogger for this log type. |
| 17 | alarm | CSV field written by StorageLogger for this log type. |
| 18 | error | CSV field written by StorageLogger for this log type. |

## error_header

| # | Field | Meaning |
| --- | --- | --- |
| 1 | timestamp | ISO timestamp for the sample or response. |
| 2 | gateway_id | Identifier of the gateway instance. |
| 3 | asset_id | Unique asset identifier, for example pcs_1, bms_1, chiller_1. |
| 4 | error_type | CSV field written by StorageLogger for this log type. |
| 5 | error_source | CSV field written by StorageLogger for this log type. |
| 6 | description | CSV field written by StorageLogger for this log type. |

# 22. Log Query and Filter Data Model

The log query layer is defined in core/storage/query. The LogFilter model decouples HTTP query parsing from CSV scanning so the same API contract can be preserved if storage later moves to SQLite, InfluxDB or cloud storage.

| Field | Type | Default | Meaning |
| --- | --- | --- | --- |
| log_type | str |  | Log query/filter model field accepted by the query backend. |
| asset_id | Optional[str] | None | Log query/filter model field accepted by the query backend. |
| date | Optional[str] | None | Log query/filter model field accepted by the query backend. |
| start_time | Optional[str] | None | Log query/filter model field accepted by the query backend. |
| end_time | Optional[str] | None | Log query/filter model field accepted by the query backend. |
| fields | Optional[List[str]] | None | Log query/filter model field accepted by the query backend. |
| exact_filters | JsonDict |  | Log query/filter model field accepted by the query backend. |
| search | Optional[str] | None | Log query/filter model field accepted by the query backend. |
| limit | int | 100 | Log query/filter model field accepted by the query backend. |
| offset | int | 0 | Log query/filter model field accepted by the query backend. |
| order | str | 'asc' | Log query/filter model field accepted by the query backend. |

| Filter group | Supported exact filter keys |
| --- | --- |
| Telemetry | bcu_state, comm_status, communication_status, current_state, fault_status, logger_status, modbus_status, operating_status, vendor |
| Events | command, event_type, source, status, vendor |
| Errors | error_source, error_type, source (source is accepted as alias for error_source) |

| Result field | Type | Default | Meaning |
| --- | --- | --- | --- |
| status | str |  | Returned in /api/logs/telemetry, /api/logs/events and /api/logs/errors responses. |
| rows | List[JsonDict] |  | Returned in /api/logs/telemetry, /api/logs/events and /api/logs/errors responses. |
| file | str | '' | Returned in /api/logs/telemetry, /api/logs/events and /api/logs/errors responses. |
| file_name | str | '' | Returned in /api/logs/telemetry, /api/logs/events and /api/logs/errors responses. |
| message | str | '' | Returned in /api/logs/telemetry, /api/logs/events and /api/logs/errors responses. |
| total_rows | int | 0 | Returned in /api/logs/telemetry, /api/logs/events and /api/logs/errors responses. |
| filtered_rows | int | 0 | Returned in /api/logs/telemetry, /api/logs/events and /api/logs/errors responses. |
| rows_count | int | 0 | Returned in /api/logs/telemetry, /api/logs/events and /api/logs/errors responses. |
| limit | int | 100 | Returned in /api/logs/telemetry, /api/logs/events and /api/logs/errors responses. |
| offset | int | 0 | Returned in /api/logs/telemetry, /api/logs/events and /api/logs/errors responses. |
| filters | JsonDict |  | Returned in /api/logs/telemetry, /api/logs/events and /api/logs/errors responses. |

# 23. BMS Register and Signal Dictionary

The following rows are extracted from drivers/bms_register_map.py. They document the BMS/BCU register-level source fields used to build EMS-facing BMS telemetry and control commands.

| Group | Key | Address | Name | Category | Subcategory | Access | Format | Scale | Unit | Description |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| RACK_SIGNAL | functional_safety_warn | 0x10 | Functional Safety Warning | C6 Battery Alarms & Faults | Functional Safety Faults | R | u16 |  |  | Bitfield register for first-level functional safety faults. |
| RACK_SIGNAL | bcu_external_fault_alarm | 0x11 | BCU External Fault Alarm | C6 Battery Alarms & Faults | Critical Faults | R | u16 |  |  | Bitfield register for BCU/BMU external critical faults. |
| RACK_SIGNAL | extern_critical_alarm | 0x12 | External Critical Alarm 1 | C6 Battery Alarms & Faults | Critical Faults | R | u16 |  |  | Bitfield register for first-level voltage/current/temperature/insulation faults. |
| RACK_SIGNAL | extern_alarm | 0x13 | External Alarm 1 | C6 Battery Alarms & Faults | Second-Level Alarms | R | u16 |  |  | Bitfield register for second-level voltage/current/temperature/insulation alarms. |
| RACK_SIGNAL | extern_warn | 0x14 | External Warning 1 | C6 Battery Alarms & Faults | Third-Level Warnings | R | u16 |  |  | Bitfield register for third-level warnings. |
| RACK_SIGNAL | extern_critical_alarm2 | 0x15 | External Critical Alarm 2 | C6 Battery Alarms & Faults | Critical Faults | R | u16 |  |  | Bitfield register for additional first-level rack/module faults. |
| RACK_SIGNAL | extern_alarm2 | 0x16 | External Alarm 2 | C6 Battery Alarms & Faults | Second-Level Alarms | R | u16 |  |  | Bitfield register for additional second-level rack/module alarms. |
| RACK_SIGNAL | extern_warn2 | 0x17 | External Warning 2 | C6 Battery Alarms & Faults | Third-Level Warnings | R | u16 |  |  | Bitfield register for additional third-level rack/module warnings. |
| RACK_SIGNAL | pre_power_stage | 0x18 | Pre-Power / Precharge Stage | C1 Battery System Status | Precharge Status | R | u16 |  |  | 0=Idle, 1/2=Precharging, 3=Precharge success, 4=Precharge failed. |
| RACK_SIGNAL | bcu_state | 0x19 | BCU System State | C1 Battery System Status | System Operating Status | R | u16 |  |  | 0=Normal/Idle, 1=Charge forbidden, 2=Discharge forbidden, 3=Standby, 4=Stop/Shutdown. |
| RACK_SIGNAL | heart_beat_num | 0x1a | Heartbeat Number | C1 Battery System Status | Communication Heartbeat | R | u16 |  |  | Heartbeat frame/counter, expected to increment periodically. |
| RACK_SIGNAL | receive_cfg_state | 0x1b | Receive Configuration State | C6 Battery Alarms & Faults | Vendor Extension | R | u16 |  |  | 0=BMU/slave registration failed, 1=BMU/slave registration success. |
| RACK_SIGNAL | pre_chg_fail_reason | 0x1c | Precharge Failure Reason | C6 Battery Alarms & Faults | Vendor Extension | R | u16 |  |  | Reserved/vendor-specific precharge failure reason. |
| RACK_SIGNAL | current_state | 0x1d | Charge / Discharge State | C1 Battery System Status | Charge / Discharge State | R | u16 |  |  | 0=Idle, 1=Discharge, 2=Charge. |
| RACK_SIGNAL | full_or_empty_flag | 0x1e | Full or Empty Flag | C1 Battery System Status | System Operating Status | R | u16 |  |  | 0=Full, 1=Empty, as per workbook. Field validation recommended. |
| RACK_SIGNAL | bcu_contactor_state | 0x1f | BCU Contactor State | C1 Battery System Status | Contactor / Operating Status | R | u16 |  |  | Bitfield: positive relay, precharge relay, negative relay, disconnector feedback. |
| RACK_MEASURE | max_cell_vol | 0x210 | Maximum Cell Voltage | C2 Battery Electrical Measurements | Cell Voltage Statistics | R | u16 |  | mV |  |
| RACK_MEASURE | max_cell_vol_num | 0x211 | Maximum Cell Voltage Number | C2 Battery Electrical Measurements | Cell Voltage Statistics | R | u16 |  |  |  |
| RACK_MEASURE | max_vol_bmu_num | 0x212 | Maximum Voltage BMU Number | C2 Battery Electrical Measurements | Cell Voltage Statistics | R | u16 |  |  |  |
| RACK_MEASURE | bmu_max_vol_num | 0x213 | BMU Maximum Voltage Cell Number | C2 Battery Electrical Measurements | Cell Voltage Statistics | R | u16 |  |  |  |
| RACK_MEASURE | min_cell_vol | 0x214 | Minimum Cell Voltage | C2 Battery Electrical Measurements | Cell Voltage Statistics | R | u16 |  | mV |  |
| RACK_MEASURE | min_cell_vol_num | 0x215 | Minimum Cell Voltage Number | C2 Battery Electrical Measurements | Cell Voltage Statistics | R | u16 |  |  |  |
| RACK_MEASURE | min_vol_bmu_num | 0x216 | Minimum Voltage BMU Number | C2 Battery Electrical Measurements | Cell Voltage Statistics | R | u16 |  |  |  |
| RACK_MEASURE | bmu_min_vol_num | 0x217 | BMU Minimum Voltage Cell Number | C2 Battery Electrical Measurements | Cell Voltage Statistics | R | u16 |  |  |  |
| RACK_MEASURE | max_cell_vol_diff | 0x218 | Maximum Cell Voltage Difference | C2 Battery Electrical Measurements | Cell Voltage Statistics | R | u16 |  | mV |  |
| RACK_MEASURE | ave_cell_vol | 0x219 | Average Cell Voltage | C2 Battery Electrical Measurements | Cell Voltage Statistics | R | u16 |  | mV |  |
| RACK_MEASURE | max_cell_temp | 0x21a | Maximum Cell Temperature | C3 Battery Thermal Measurements | Thermal Measurements | R | s16 | 0.1 | degC |  |
| RACK_MEASURE | max_cell_temp_num | 0x21b | Maximum Cell Temperature Number | C3 Battery Thermal Measurements | Thermal Measurements | R | u16 |  |  |  |
| RACK_MEASURE | max_temp_bmu_num | 0x21c | Maximum Temperature BMU Number | C3 Battery Thermal Measurements | Thermal Measurements | R | u16 |  |  |  |
| RACK_MEASURE | bmu_max_temp_num | 0x21d | BMU Maximum Temperature Number | C3 Battery Thermal Measurements | Thermal Measurements | R | u16 |  |  |  |
| RACK_MEASURE | min_cell_temp | 0x21e | Minimum Cell Temperature | C3 Battery Thermal Measurements | Thermal Measurements | R | s16 | 0.1 | degC |  |
| RACK_MEASURE | min_cell_temp_num | 0x21f | Minimum Cell Temperature Number | C3 Battery Thermal Measurements | Thermal Measurements | R | u16 |  |  |  |
| RACK_MEASURE | min_temp_bmu_num | 0x220 | Minimum Temperature BMU Number | C3 Battery Thermal Measurements | Thermal Measurements | R | u16 |  |  |  |
| RACK_MEASURE | bmu_min_temp_num | 0x221 | BMU Minimum Temperature Number | C3 Battery Thermal Measurements | Thermal Measurements | R | u16 |  |  |  |
| RACK_MEASURE | rack_ave_temp | 0x222 | Rack Average Temperature | C3 Battery Thermal Measurements | Thermal Measurements | R | s16 | 0.1 | degC |  |
| RACK_MEASURE | max_polarity_temp | 0x223 | Maximum Terminal Temperature | C3 Battery Thermal Measurements | Thermal Measurements | R | s16 | 0.1 | degC |  |
| RACK_MEASURE | max_polarity_num | 0x224 | Maximum Terminal Number | C2 Battery Electrical Measurements | Rack Measurements | R | u16 |  |  |  |
| RACK_MEASURE | max_allowed_chg_cur | 0x225 | Maximum Allowed Charge Current | C2 Battery Electrical Measurements | Charge/Discharge Limits | R | u16 | 0.1 | A |  |
| RACK_MEASURE | max_allowed_dchg_cur | 0x226 | Maximum Allowed Discharge Current | C2 Battery Electrical Measurements | Charge/Discharge Limits | R | u16 | 0.1 | A |  |
| RACK_MEASURE | display_soc | 0x227 | Display SOC | C4 Battery Health & Capacity | SOC/SOH | R | u16 | 0.1 | % | Workbook unit is per-mille; converted to percent by value * 0.1. |
| RACK_MEASURE | soh | 0x228 | SOH | C4 Battery Health & Capacity | SOC/SOH | R | u16 | 0.1 | % | Workbook unit is per-mille; converted to percent by value * 0.1. |
| RACK_MEASURE | max_bat_temp_diff | 0x229 | Maximum Battery Temperature Difference | C3 Battery Thermal Measurements | Thermal Measurements | R | u16 | 0.1 | degC |  |
| RACK_MEASURE | max_bat_temp_rise | 0x22a | Maximum Battery Temperature Rise | C3 Battery Thermal Measurements | Thermal Measurements | R | u16 | 0.1 | degC |  |
| RACK_MEASURE | max_bat_temp_rise_bmu_num | 0x22b | Maximum Battery Temperature Rise BMU Number | C3 Battery Thermal Measurements | Thermal Measurements | R | u16 |  |  |  |
| RACK_MEASURE | max_bat_temp_rise_num_in_bmu | 0x22c | Maximum Battery Temperature Rise Number In BMU | C3 Battery Thermal Measurements | Thermal Measurements | R | u16 |  |  |  |
| RACK_MEASURE | max_bat_temp_rise_num_in_bcu | 0x22d | Maximum Battery Temperature Rise Number In BCU | C3 Battery Thermal Measurements | Thermal Measurements | R | u16 |  |  |  |
| RACK_MEASURE | rack_inner_soc | 0x22e | Rack Internal SOC | C4 Battery Health & Capacity | SOC/SOH | R | u16 | 0.1 | % | Workbook unit is per-mille; converted to percent by value * 0.1. |
| RACK_MEASURE | pre_chg_vol | 0x22f | Precharge Voltage | C2 Battery Electrical Measurements | Electrical Measurements | R | s16 | 0.1 | V |  |
| RACK_MEASURE | bmu_total_vol | 0x230 | BMU Total Voltage | C2 Battery Electrical Measurements | Electrical Measurements | R | s16 | 0.1 | V |  |
| RACK_MEASURE | total_vol | 0x231 | Total Rack Voltage | C2 Battery Electrical Measurements | Electrical Measurements | R | s16 | 0.1 | V |  |
| RACK_MEASURE | total_cur | 0x232 | Total Rack Current | C2 Battery Electrical Measurements | Electrical Measurements | R | s16 | 0.1 | A |  |
| RACK_MEASURE | ncon_total_vol | 0x233 | NCON Total Voltage | C2 Battery Electrical Measurements | Electrical Measurements | R | s16 | 0.1 | V |  |
| RACK_MEASURE | shunt_current | 0x234 | Shunt Current | C2 Battery Electrical Measurements | Electrical Measurements | R | s16 | 0.1 | A |  |
| RACK_MEASURE | can_hall_sample_cur_ori_value | 0x235 | CAN Hall Sample Current Original Value | C2 Battery Electrical Measurements | Electrical Measurements | R | s16 | 0.1 | A |  |
| RACK_MEASURE | cur_vol_hall_sam_cur_ori_value | 0x236 | Current/Voltage Hall Sample Current Original Value | C2 Battery Electrical Measurements | Electrical Measurements | R | s16 | 0.1 | A |  |
| RACK_MEASURE | ir | 0x237 | Insulation Resistance | C5 Battery Safety & Protection | Insulation & Safety | R | u16 |  | kOhm |  |
| RACK_MEASURE | positive_ir | 0x238 | Positive Insulation Resistance | C5 Battery Safety & Protection | Insulation & Safety | R | u16 |  | kOhm |  |
| RACK_MEASURE | negative_ir | 0x239 | Negative Insulation Resistance | C5 Battery Safety & Protection | Insulation & Safety | R | u16 |  | kOhm |  |
| CONTROL | start_insulation_sampling | 0x401 | Start Insulation Sampling | C7 Battery Control Commands | Insulation Test Control | R/W | u16 |  |  | Write 1 to start/reset insulation sampling; other value = no action. |
| CONTROL | start_precharge | 0x402 | Start Precharge Operation | C7 Battery Control Commands | Precharge Control | R/W | u16 |  |  | Write 0x01 to start precharge; other value = stop/open precharge path. |
| CONTROL | bcu_reset | 0x403 | BCU Reset | C7 Battery Control Commands | Commissioning / Reset Control | R/W | u16 |  |  | Write 0x01 to reset BCU; other value = no reset. |
| CONTROL | fan_switch | 0x406 | Fan Force Control | C7 Battery Control Commands | Fan Control | R/W | u16 |  |  | Write 1=Fan ON, 2=Fan OFF. 0 may be used by EMS as auto/no-force if validated. |

| BMS control key | Command value mapping |
| --- | --- |
| start_insulation_sampling | {'start': 1, 'no_action': 0} |
| start_precharge | {'start': 1, 'stop': 0} |
| bcu_reset | {'reset': 1, 'no_action': 0} |
| fan_switch | {'auto': 0, 'on': 1, 'off': 2} |

# 24. Database Integration Recommendation

The database team should not store raw frontend JSON blobs only. The recommended design separates asset metadata, current state, historical telemetry, event logs, error logs, health snapshots and command audit records.

| Table | Primary fields | Purpose |
| --- | --- | --- |
| assets | asset_id, asset_key, asset_type, vendor, protocol, profile, enabled, connection_json | Master asset catalog sourced from /api/assets |
| telemetry_current | asset_id, timestamp, status_json, selected_fields | Latest snapshot per asset for fast dashboard loading |
| telemetry_history | asset_id, timestamp, field_name, value_num, value_text, unit | Long-term timeseries for charts/analytics |
| events | asset_id, timestamp, event_type, command, source, status, old_value, new_value, description | Audit trail for commands and operational events |
| errors | asset_id, timestamp, error_type, error_source, description | Historical failures and diagnostics |
| health_snapshots | asset_id, timestamp, status, reason, recommended_action, connection_json, storage_json | Health monitoring trend and alerts |
| command_audit | request_id, asset_id, command, request_body_json, result_json, status, timestamp | Control/command traceability |

# 25. Frontend and Backend Integration Guide

| Screen/module | Recommended API | Notes |
| --- | --- | --- |
| Dashboard home | GET /api/assets + GET /api/telemetry/operator | Discover assets dynamically and render operator-clean cards |
| Asset detail page | GET /api/assets/{asset_id} + GET /api/assets/{asset_id}/telemetry/operator | Show metadata, runtime mode, latest values and health |
| Live dashboard | GET /api/stream/telemetry?view=operator | Use SSE when browser live updates are required |
| Health page | GET /api/health/assets + GET /api/diagnostics | Show green/yellow/red health cards and recommended actions |
| Historical trend page | GET /api/assets/{asset_id}/telemetry/timeseries or Log API telemetry query | Use date/time/key filters for charts |
| Logs page | GET /api/logs/events, /api/logs/errors, /api/logs/telemetry | Expose field/date/time/search filters |
| Command panel | POST /api/assets/{asset_id}/commands | Use with confirmation prompts and display command result |
| Backend ingestion | GET /api/telemetry/latest or operator endpoint + /api/health | Store in database at 1-5 second interval depending on requirement |

# 26. Example API Calls

### Asset catalog

curl -s http://<IMX_WIFI_IP>:8000/api/assets | python3 -m json.tool

### Operator telemetry

curl -s http://<IMX_WIFI_IP>:8000/api/telemetry/operator | python3 -m json.tool

### PCS telemetry

curl -s http://<IMX_WIFI_IP>:8000/api/assets/pcs_1/telemetry/operator | python3 -m json.tool

### Health

curl -s http://<IMX_WIFI_IP>:8000/api/health | python3 -m json.tool

### Diagnostics

curl -s http://<IMX_WIFI_IP>:8000/api/diagnostics | python3 -m json.tool

### Telemetry logs

curl -s "http://<IMX_ETH_IP>:7000/api/logs/telemetry?asset_id=pcs_1&date=YYYY-MM-DD&fields=timestamp,active_power_kw,dc_voltage_v&limit=20" | python3 -m json.tool

### Command

curl -X POST http://<IMX_WIFI_IP>:8000/api/assets/pcs_1/commands -H "Content-Type: application/json" -d "{\"command\":\"PCS_READ\",\"request_id\":\"web-001\"}"

# 27. Baseline Verification Checklist

python -m compileall . passes without syntax errors.

test_legacy_compatibility.py through test_log_filter_abstraction.py pass.

Gateway starts with configs/actual_network_assets.json.

Ports 6000, 7000 and 8000 are listening.

/api/assets, /api/telemetry/operator, /api/health and /api/diagnostics work from browser/PowerShell.

Log API filters work for date, time range, fields, search, events and errors.

Flutter/Desktop receives UDP telemetry and TCP commands still work.

PCS/BMS/chiller behavior remains hardware-verified for current deployment.

# 28. Future EMS Control Notes

The gateway baseline deliberately stops short of implementing EMS control state machines. That work should start only after the EMS control story, modes, asset interactions and safety policies are defined. The current baseline is ready because telemetry, command routing, health, logging and filters are stable and modular.