## Sheet0
Hexon EMS EUR261kWh North-Bound Register Table
Channel Name | Port No. | Device ID | Register Addr. | Register Qty. | Group No. | Entity Name | Point Name | Point Type | Unit | Description | R/W (0: RO, 1: RW) | Factor
test | 515 | 1 | 0 | 2 | 0 | EMS System Parameters | Available Quantity | Float |  |  | 1 | 1
test | 515 | 1 | 2 | 2 | 0 | EMS System Parameters | Slave Available Quantity | Float |  |  | 1 | 1
test | 515 | 1 | 4 | 2 | 0 | EMS System Parameters | Remote Mode | Float |  | 0, Local; 1, Remote | 1 | 1
test | 515 | 1 | 6 | 2 | 0 | EMS System Parameters | Master/Slave Mode | Float |  | 0, Slave; 1, Master | 1 | 1
test | 515 | 1 | 8 | 2 | 0 | EMS System Parameters | Slave Count | Float |  |  | 1 | 1
test | 515 | 1 | 10 | 2 | 0 | EMS System Parameters | Manual/Auto Mode | Float |  | 0, Manual; 1, Auto | 1 | 1
test | 515 | 1 | 12 | 2 | 0 | EMS System Parameters | Manual Mode Control | Float |  | 1, Shutdown; 2, Standby; 3, Charge; 4, Discharge | 1 | 1
test | 515 | 1 | 14 | 2 | 0 | EMS System Parameters | Auto Mode Control | Float |  | 1, Shutdown; 2, Standby; 3, Charge; 4, Discharge | 1 | 1
test | 515 | 1 | 16 | 2 | 0 | EMS System Parameters | Master Control Mode | Float |  | 1, Shutdown; 2, Standby; 3, Charge; 4, Discharge | 1 | 1
test | 515 | 1 | 18 | 2 | 0 | EMS System Parameters | Remote Control Mode | Float |  | 1, Shutdown; 2, Standby; 3, Charge; 4, Discharge | 1 | 1
test | 515 | 1 | 20 | 2 | 0 | EMS System Parameters | Charge/Discharge Control Mode | Float |  | 1, Shutdown; 2, Standby; 3, Charge; 4, Discharge | 1 | 1
test | 515 | 1 | 22 | 2 | 0 | EMS System Parameters | Start Command | Float |  | 0, Stop; 1, Start | 1 | 1
test | 515 | 1 | 24 | 2 | 0 | EMS System Parameters | Manual Start | Float |  | 0, Stop; 1, Start | 1 | 1
test | 515 | 1 | 26 | 2 | 0 | EMS System Parameters | Auto Start | Float |  | 0, Stop; 1, Start | 1 | 1
test | 515 | 1 | 28 | 2 | 0 | EMS System Parameters | PCS Start/Stop Control | Float |  | 0, Stop; 1, Start | 1 | 1
test | 515 | 1 | 30 | 2 | 0 | EMS System Parameters | Master PCS Start/Stop Control | Float |  | 0, Stop; 1, Start | 1 | 1
test | 515 | 1 | 32 | 2 | 0 | EMS System Parameters | BMS Start/Stop Control | Float |  | 0, Stop; 1, Start | 1 | 1
test | 515 | 1 | 34 | 2 | 0 | EMS System Parameters | PCS Status | Float |  |  | 1 | 1
test | 515 | 1 | 36 | 2 | 0 | EMS System Parameters | Running Slave PCS Count | Float |  |  | 1 | 1
test | 515 | 1 | 38 | 2 | 0 | EMS System Parameters | BMS Status | Float |  | 0, Init; 1, Self-Check; 3, Power-On; 4, Power-On Complete; 5, Charge Disabled; 6, Discharge Disabled; 7, Standby; 8, Fault Power-Off; 9, Fault Cleared After Power-Off; 10, Test Mode | 1 | 1
test | 515 | 1 | 40 | 2 | 0 | EMS System Parameters | PCS Running Status | Float |  | 0, Stopped; 1, Self-Check; 2, Running; 4, Fault; 7, Standby | 1 | 1
test | 515 | 1 | 42 | 2 | 0 | EMS System Parameters | Manual Charge Value Setpoint | Float | kW |  | 1 | 1
test | 515 | 1 | 44 | 2 | 0 | EMS System Parameters | Manual Discharge Value Setpoint | Float | kW |  | 1 | 1
test | 515 | 1 | 46 | 2 | 0 | EMS System Parameters | Auto Charge Schedule Value | Float | kW |  | 1 | 1
test | 515 | 1 | 48 | 2 | 0 | EMS System Parameters | Auto Discharge Schedule Value | Float | kW |  | 1 | 1
test | 515 | 1 | 50 | 2 | 0 | EMS System Parameters | Master Charge Power Command | Float | kW |  | 1 | 1
test | 515 | 1 | 52 | 2 | 0 | EMS System Parameters | Master Discharge Power Command | Float | kW |  | 1 | 1
test | 515 | 1 | 54 | 2 | 0 | EMS System Parameters | Remote Power Command | Float | kW |  | 1 | 1
test | 515 | 1 | 56 | 2 | 0 | EMS System Parameters | Charge Value Setpoint | Float | kW |  | 1 | 1
test | 515 | 1 | 58 | 2 | 0 | EMS System Parameters | Discharge Value Setpoint | Float | kW |  | 1 | 1
test | 515 | 1 | 60 | 2 | 0 | EMS System Parameters | Total Available Charge Power | Float | kW |  | 1 | 1
test | 515 | 1 | 62 | 2 | 0 | EMS System Parameters | Total Available Discharge Power | Float | kW |  | 1 | 1
test | 515 | 1 | 64 | 2 | 0 | EMS System Parameters | Slave Total Available Charge Power | Float | kW |  | 1 | 1
test | 515 | 1 | 66 | 2 | 0 | EMS System Parameters | Slave Total Available Discharge Power | Float | kW |  | 1 | 1
test | 515 | 1 | 68 | 2 | 0 | EMS System Parameters | Charge SOC Setpoint (%) | Float | ％ |  | 1 | 1
test | 515 | 1 | 70 | 2 | 0 | EMS System Parameters | Discharge SOC Setpoint (%) | Float | ％ |  | 1 | 1
test | 515 | 1 | 72 | 2 | 0 | EMS System Parameters | Load Power | Float | kW |  | 1 | 1
test | 515 | 1 | 74 | 2 | 0 | EMS System Parameters | Utility Meter Comm Status | Float |  | 0, Offline; 1, Online | 1 | 1
test | 515 | 1 | 76 | 2 | 0 | EMS System Parameters | Utility Current Total Power | Float | kW |  | 1 | 1
test | 515 | 1 | 78 | 2 | 0 | EMS System Parameters | Meter Current Total Power | Float | kW |  | 1 | 1
test | 515 | 1 | 80 | 2 | 0 | EMS System Parameters | SOC | Float | % |  | 1 | 1
test | 515 | 1 | 82 | 2 | 0 | EMS System Parameters | Slave SOC | Float | % |  | 1 | 1
test | 515 | 1 | 84 | 2 | 0 | EMS System Parameters | SOC Limit Enable | Float |  | 0, Disabled; 1, Enabled | 1 | 1
test | 515 | 1 | 86 | 2 | 0 | EMS System Parameters | Charge Cutoff SOC Setting | Float | kW |  | 1 | 1
test | 515 | 1 | 88 | 2 | 0 | EMS System Parameters | Discharge Cutoff SOC Setting | Float | kW |  | 1 | 1
test | 515 | 1 | 90 | 2 | 0 | EMS System Parameters | Master SOC Limit Enable | Float |  | 0, Disabled; 1, Enabled | 1 | 1
test | 515 | 1 | 92 | 2 | 0 | EMS System Parameters | Master Charge Cutoff SOC Setting | Float | kW |  | 1 | 1
test | 515 | 1 | 94 | 2 | 0 | EMS System Parameters | Master Discharge Cutoff SOC Setting | Float | kW |  | 1 | 1
test | 515 | 1 | 96 | 2 | 0 | EMS System Parameters | Rate Limit Enable | Float |  | 0, Disabled; 1, Enabled | 1 | 1
test | 515 | 1 | 98 | 2 | 0 | EMS System Parameters | Demand Limit Enable | Float |  | 0, Disabled; 1, Enabled | 1 | 1
test | 515 | 1 | 100 | 2 | 0 | EMS System Parameters | Anti-Reverse Flow Enable | Float |  | 0, Disabled; 1, Enabled | 1 | 1
test | 515 | 1 | 102 | 2 | 0 | EMS System Parameters | Control Step | Float | kW |  | 1 | 1
test | 515 | 1 | 104 | 2 | 0 | EMS System Parameters | Control Period | Float | s |  | 1 | 1
test | 515 | 1 | 106 | 2 | 0 | EMS System Parameters | Demand | Float | kW |  | 1 | 1
test | 515 | 1 | 108 | 2 | 0 | EMS System Parameters | Demand Limit Percentage | Float | ％ |  | 1 | 1
test | 515 | 1 | 110 | 2 | 0 | EMS System Parameters | Anti-Reverse Flow Power Lower Limit | Float | kW |  | 1 | 1
test | 515 | 1 | 112 | 2 | 0 | EMS System Parameters | Anti-Reverse Flow Power Upper Limit | Float | kW |  | 1 | 1
test | 515 | 1 | 114 | 2 | 0 | EMS System Parameters | System Fault | Float |  |  | 1 | 1
test | 515 | 1 | 116 | 2 | 0 | EMS System Parameters | Master System Fault | Float |  |  | 1 | 1
test | 515 | 1 | 118 | 2 | 0 | EMS System Parameters | Emergency Stop | Float |  | 0, Normal; 1, Emergency Stop | 1 | 1
test | 515 | 1 | 120 | 2 | 0 | EMS System Parameters | Master Emergency Stop | Float |  | 0, Normal; 1, Emergency Stop | 1 | 1
test | 515 | 1 | 122 | 2 | 0 | EMS System Parameters | Emergency Stop Flag 1 | Float |  |  | 1 | 1
test | 515 | 1 | 124 | 2 | 0 | EMS System Parameters | Emergency Stop Flag 2 | Float |  |  | 1 | 1
test | 515 | 1 | 126 | 2 | 0 | EMS System Parameters | Emergency Stop Timer | Float |  |  | 1 | 1
test | 515 | 1 | 128 | 2 | 0 | EMS System Parameters | Flag | Float |  |  | 1 | 1
test | 515 | 1 | 130 | 2 | 0 | EMS System Parameters | Fire Protection Comm Status | Float |  | 0, Offline; 1, Online | 1 | 1
test | 515 | 1 | 132 | 2 | 0 | EMS System Parameters | Fire Protection Offline | Float |  | 0, Normal; 1, Offline | 1 | 1
test | 515 | 1 | 134 | 2 | 0 | EMS System Parameters | Fire Protection Alarm | Float |  | 0, No Fire Alarm; 1, CO Fire Alarm; 2, Temperature Fire Alarm; 3, Two or More Fire Alarms; 4, Extinguisher Activated | 1 | 1
test | 515 | 1 | 136 | 2 | 0 | EMS System Parameters | Fire Protection Fault | Float |  | 0, No Fault; 1, Extinguisher Activated; 2, Sensor Fault; 3, Two or More Alarms | 1 | 1
test | 515 | 1 | 138 | 2 | 0 | EMS System Parameters | Fire Protection Sprinkler | Float |  | 0, Normal; 1, Alarm | 1 | 1
test | 515 | 1 | 140 | 2 | 0 | EMS System Parameters | Fire Protection Status | Float |  | 0, Normal; 1, Alarm | 1 | 1
test | 515 | 1 | 142 | 2 | 0 | EMS System Parameters | PPS Pulse | Float |  |  | 1 | 1
test | 515 | 1 | 144 | 2 | 0 | EMS System Parameters | PPS Pulse 1 | Float |  |  | 1 | 1
test | 515 | 1 | 146 | 2 | 0 | EMS System Parameters | Status | Float |  | 0, Standby; 1, Discharging; 2, Charging | 1 | 1
test | 515 | 1 | 148 | 2 | 0 | EMS System Parameters | ESS Power | Float | kW |  | 1 | 1
test | 515 | 1 | 150 | 2 | 0 | EMS System Parameters | Slave ESS Power | Float | kW |  | 1 | 1
test | 515 | 1 | 152 | 2 | 0 | EMS System Parameters | Manual Grid On/Off Switch | Float |  | 0, Grid-Connected; 1, Off-Grid | 1 | 1
test | 515 | 1 | 154 | 2 | 0 | EMS System Parameters | Reset | Float |  | 0, Normal; 1, Reset | 1 | 1
test | 515 | 1 | 156 | 2 | 0 | EMS System Parameters | Running Indicator | Float |  | 0, Off; 1, On | 1 | 1
test | 515 | 1 | 158 | 2 | 0 | EMS System Parameters | Fault Indicator | Float |  | 0, Off; 1, On | 1 | 1
test | 515 | 1 | 160 | 2 | 0 | EMS System Parameters | PCS Emergency Stop Control | Float |  | 0, Emergency Stop; 1, Normal | 1 | 1
test | 515 | 1 | 162 | 2 | 0 | EMS System Parameters | Breaker Control | Float |  | 0, Closed; 1, Open | 1 | 1
test | 515 | 1 | 164 | 2 | 0 | EMS System Parameters | Grid On/Off Switch | Float |  | 0, Complete; 1, Grid-Connected; 2, Off-Grid | 1 | 1
test | 515 | 1 | 166 | 2 | 0 | EMS System Parameters | Master Grid On/Off Switch Command | Float |  | 0, Grid-Connected; 1, Off-Grid | 1 | 1
test | 515 | 1 | 168 | 2 | 0 | EMS System Parameters | Battery Precharge Control | Float |  | 0, Complete; 1, Power-Off; 2, Power-On | 1 | 1
test | 515 | 1 | 170 | 2 | 0 | EMS System Parameters | Master Battery Precharge Control Command | Float |  | 0, Complete; 1, Power-Off; 2, Power-On | 1 | 1
test | 515 | 1 | 172 | 2 | 0 | EMS System Parameters | Master Comm Status | Float |  | 0, Offline; 1, Online | 1 | 1
test | 515 | 1 | 174 | 2 | 0 | EMS System Parameters | Master Counter | Float |  |  | 1 | 1
test | 515 | 1 | 176 | 2 | 0 | EMS System Parameters | Off-Grid Shutdown SOC | Float |  |  | 1 | 1
test | 515 | 1 | 178 | 2 | 0 | EMS System Parameters | Master Off-Grid Shutdown SOC Command | Float |  |  | 1 | 1
test | 515 | 1 | 180 | 2 | 0 | EMS System Parameters | PCS Grid On/Off Status | Float |  | 0, Off-Grid; 1, Grid-Connected | 1 | 1
test | 515 | 1 | 182 | 2 | 0 | EMS System Parameters | Off-Grid Start Timer | Float |  |  | 1 | 1
test | 515 | 1 | 184 | 2 | 0 | EMS System Parameters | Master Off-Grid Start Timer Command | Float |  |  | 1 | 1
test | 515 | 1 | 186 | 2 | 0 | BMS Comm Parameters 1 | Online Points | Float |  | 0, Offline; 1, Online | 0 | 1
test | 515 | 1 | 188 | 2 | 0 | BMS Comm Parameters 1 | Total Voltage Difference Too Large | Float |  | 0, Normal; 1, Fault | 0 | 1
test | 515 | 1 | 190 | 2 | 0 | BMS Comm Parameters 1 | Insulation Too Low | Float |  | 0, Normal; 1, Fault | 0 | 1
test | 515 | 1 | 192 | 2 | 0 | BMS Comm Parameters 1 | Cell Voltage Too High | Float |  | 0, Normal; 1, Fault | 0 | 1
test | 515 | 1 | 194 | 2 | 0 | BMS Comm Parameters 1 | Cell Temperature Too High | Float |  | 0, Normal; 1, Fault | 0 | 1
test | 515 | 1 | 196 | 2 | 0 | BMS Comm Parameters 1 | Cell Voltage Update Fault | Float |  | 0, Normal; 1, Fault | 0 | 1
test | 515 | 1 | 198 | 2 | 0 | BMS Comm Parameters 1 | Pole Temperature Too High | Float |  | 0, Normal; 1, Fault | 0 | 1
test | 515 | 1 | 200 | 2 | 0 | BMS Comm Parameters 1 | Current Too High | Float |  | 0, Normal; 1, Fault | 0 | 1
test | 515 | 1 | 202 | 2 | 0 | BMS Comm Parameters 1 | Insulation Fault | Float |  | 0, Normal; 1, Fault | 0 | 1
test | 515 | 1 | 204 | 2 | 0 | BMS Comm Parameters 1 | NTC Fault (Functional Safety Fault) | Float |  | 0, Normal; 1, Fault | 0 | 1
test | 515 | 1 | 206 | 2 | 0 | BMS Comm Parameters 1 | Pole Temperature Sensor Fault | Float |  | 0, Normal; 1, Fault | 0 | 1
test | 515 | 1 | 208 | 2 | 0 | BMS Comm Parameters 1 | Battery Temperature Sensor Fault | Float |  | 0, Normal; 1, Fault | 0 | 1
test | 515 | 1 | 210 | 2 | 0 | BMS Comm Parameters 1 | Voltage Sampling Fault | Float |  | 0, Normal; 1, Fault | 0 | 1
test | 515 | 1 | 212 | 2 | 0 | BMS Comm Parameters 1 | Sampling Chip Fault | Float |  | 0, Normal; 1, Fault | 0 | 1
test | 515 | 1 | 214 | 2 | 0 | BMS Comm Parameters 1 | Current Sampling Fault (Functional Safety Fault) | Float |  | 0, Normal; 1, Fault | 0 | 1
test | 515 | 1 | 216 | 2 | 0 | BMS Comm Parameters 1 | Battery Temperature Too Low | Float |  | 0, Normal; 1, Fault | 0 | 1
test | 515 | 1 | 218 | 2 | 0 | BMS Comm Parameters 1 | Charge Current Too High | Float |  | 0, Normal; 1, Fault | 0 | 1
test | 515 | 1 | 220 | 2 | 0 | BMS Comm Parameters 1 | BMU Self-Check | Float |  | 0, Normal; 1, Fault | 0 | 1
test | 515 | 1 | 222 | 2 | 0 | BMS Comm Parameters 1 | BCU Self-Check | Float |  | 0, Normal; 1, Fault | 0 | 1
test | 515 | 1 | 224 | 2 | 0 | BMS Comm Parameters 1 | Fuse Fault | Float |  | 0, Normal; 1, Fault | 0 | 1
test | 515 | 1 | 226 | 2 | 0 | BMS Comm Parameters 1 | Contactor Fault | Float |  | 0, Normal; 1, Fault | 0 | 1
test | 515 | 1 | 228 | 2 | 0 | BMS Comm Parameters 1 | BMU Comm Fault | Float |  | 0, Normal; 1, Fault | 0 | 1
test | 515 | 1 | 230 | 2 | 0 | BMS Comm Parameters 1 | BAU Comm Fault | Float |  | 0, Normal; 1, Fault | 0 | 1
test | 515 | 1 | 232 | 2 | 0 | BMS Comm Parameters 1 | Current Sampling Fault | Float |  | 0, Normal; 1, Fault | 0 | 1
test | 515 | 1 | 234 | 2 | 0 | BMS Comm Parameters 1 | Insulation Monitoring Fault | Float |  | 0, Normal; 1, Fault | 0 | 1
test | 515 | 1 | 236 | 2 | 0 | BMS Comm Parameters 1 | Isolator Switch Status | Float |  | 0, Normal; 1, Fault | 0 | 1
test | 515 | 1 | 238 | 2 | 0 | BMS Comm Parameters 1 | NTC Fault | Float |  | 0, Normal; 1, Fault | 0 | 1
test | 515 | 1 | 240 | 2 | 0 | BMS Comm Parameters 1 | HV Box Temperature Fault | Float |  | 0, Normal; 1, Fault | 0 | 1
test | 515 | 1 | 242 | 2 | 0 | BMS Comm Parameters 1 | HV Circuit Fault | Float |  | 0, Normal; 1, Fault | 0 | 1
test | 515 | 1 | 244 | 2 | 0 | BMS Comm Parameters 1 | Functional Safety Fault | Float |  | 0, Normal; 1, Fault | 0 | 1
test | 515 | 1 | 246 | 2 | 0 | BMS Comm Parameters 1 | PCS Comm Fault | Float |  | 0, Normal; 1, Fault | 0 | 1
test | 515 | 1 | 248 | 2 | 0 | BMS Comm Parameters 1 | Total Voltage Overvoltage (Level 1) | Float |  | 0, Normal; 1, Fault | 0 | 1
test | 515 | 1 | 250 | 2 | 0 | BMS Comm Parameters 1 | Total Voltage Undervoltage (Level 1) | Float |  | 0, Normal; 1, Fault | 0 | 1
test | 515 | 1 | 252 | 2 | 0 | BMS Comm Parameters 1 | Cell Overvoltage (Level 1) | Float |  | 0, Normal; 1, Fault | 0 | 1
test | 515 | 1 | 254 | 2 | 0 | BMS Comm Parameters 1 | Cell Undervoltage (Level 1) | Float |  | 0, Normal; 1, Fault | 0 | 1
test | 515 | 1 | 256 | 2 | 0 | BMS Comm Parameters 1 | Discharge Overcurrent (Level 1) | Float |  | 0, Normal; 1, Fault | 0 | 1
test | 515 | 1 | 258 | 2 | 0 | BMS Comm Parameters 1 | Charge Overcurrent (Level 1) | Float |  | 0, Normal; 1, Fault | 0 | 1
test | 515 | 1 | 260 | 2 | 0 | BMS Comm Parameters 1 | Discharge Over-Temperature (Level 1) | Float |  | 0, Normal; 1, Fault | 0 | 1
test | 515 | 1 | 262 | 2 | 0 | BMS Comm Parameters 1 | Discharge Under-Temperature (Level 1) | Float |  | 0, Normal; 1, Fault | 0 | 1
test | 515 | 1 | 264 | 2 | 0 | BMS Comm Parameters 1 | Charge Over-Temperature (Level 1) | Float |  | 0, Normal; 1, Fault | 0 | 1
test | 515 | 1 | 266 | 2 | 0 | BMS Comm Parameters 1 | Charge Under-Temperature (Level 1) | Float |  | 0, Normal; 1, Fault | 0 | 1
test | 515 | 1 | 268 | 2 | 0 | BMS Comm Parameters 1 | Insulation Too Low (Level 1) | Float |  | 0, Normal; 1, Fault | 0 | 1
test | 515 | 1 | 270 | 2 | 0 | BMS Comm Parameters 1 | Pole Over-Temperature (Level 1) | Float |  | 0, Normal; 1, Fault | 0 | 1
test | 515 | 1 | 272 | 2 | 0 | BMS Comm Parameters 1 | HV Box Over-Temperature (Level 1) | Float |  | 0, Normal; 1, Fault | 0 | 1
test | 515 | 1 | 274 | 2 | 0 | BMS Comm Parameters 1 | Cell Voltage Difference (Level 1) | Float |  | 0, Normal; 1, Fault | 0 | 1
test | 515 | 1 | 276 | 2 | 0 | BMS Comm Parameters 1 | Cell Temperature Difference (Level 1) | Float |  | 0, Normal; 1, Fault | 0 | 1
test | 515 | 1 | 278 | 2 | 0 | BMS Comm Parameters 1 | Total Voltage Overvoltage (Level 2) | Float |  | 0, Normal; 1, Fault | 0 | 1
test | 515 | 1 | 280 | 2 | 0 | BMS Comm Parameters 1 | Total Voltage Undervoltage (Level 2) | Float |  | 0, Normal; 1, Fault | 0 | 1
test | 515 | 1 | 282 | 2 | 0 | BMS Comm Parameters 1 | Cell Overvoltage (Level 2) | Float |  | 0, Normal; 1, Fault | 0 | 1
test | 515 | 1 | 284 | 2 | 0 | BMS Comm Parameters 1 | Cell Undervoltage (Level 2) | Float |  | 0, Normal; 1, Fault | 0 | 1
test | 515 | 1 | 286 | 2 | 0 | BMS Comm Parameters 1 | Discharge Overcurrent (Level 2) | Float |  | 0, Normal; 1, Fault | 0 | 1
test | 515 | 1 | 288 | 2 | 0 | BMS Comm Parameters 1 | Charge Overcurrent (Level 2) | Float |  | 0, Normal; 1, Fault | 0 | 1
test | 515 | 1 | 290 | 2 | 0 | BMS Comm Parameters 1 | Discharge Over-Temperature (Level 2) | Float |  | 0, Normal; 1, Fault | 0 | 1
test | 515 | 1 | 292 | 2 | 0 | BMS Comm Parameters 1 | Discharge Under-Temperature (Level 2) | Float |  | 0, Normal; 1, Fault | 0 | 1
test | 515 | 1 | 294 | 2 | 0 | BMS Comm Parameters 1 | Charge Over-Temperature (Level 2) | Float |  | 0, Normal; 1, Fault | 0 | 1
test | 515 | 1 | 296 | 2 | 0 | BMS Comm Parameters 1 | Charge Under-Temperature (Level 2) | Float |  | 0, Normal; 1, Fault | 0 | 1
test | 515 | 1 | 298 | 2 | 0 | BMS Comm Parameters 1 | Insulation Too Low (Level 2) | Float |  | 0, Normal; 1, Fault | 0 | 1
test | 515 | 1 | 300 | 2 | 0 | BMS Comm Parameters 1 | Pole Over-Temperature (Level 2) | Float |  | 0, Normal; 1, Fault | 0 | 1
test | 515 | 1 | 302 | 2 | 0 | BMS Comm Parameters 1 | HV Box Over-Temperature (Level 2) | Float |  | 0, Normal; 1, Fault | 0 | 1
test | 515 | 1 | 304 | 2 | 0 | BMS Comm Parameters 1 | Cell Voltage Difference (Level 2) | Float |  | 0, Normal; 1, Fault | 0 | 1
test | 515 | 1 | 306 | 2 | 0 | BMS Comm Parameters 1 | Cell Temperature Difference (Level 2) | Float |  | 0, Normal; 1, Fault | 0 | 1
test | 515 | 1 | 308 | 2 | 0 | BMS Comm Parameters 1 | Total Voltage Overvoltage (Level 3) | Float |  | 0, Normal; 1, Fault | 0 | 1
test | 515 | 1 | 310 | 2 | 0 | BMS Comm Parameters 1 | Total Voltage Undervoltage (Level 3) | Float |  | 0, Normal; 1, Fault | 0 | 1
test | 515 | 1 | 312 | 2 | 0 | BMS Comm Parameters 1 | Cell Overvoltage (Level 3) | Float |  | 0, Normal; 1, Fault | 0 | 1
test | 515 | 1 | 314 | 2 | 0 | BMS Comm Parameters 1 | Cell Undervoltage (Level 3) | Float |  | 0, Normal; 1, Fault | 0 | 1
test | 515 | 1 | 316 | 2 | 0 | BMS Comm Parameters 1 | Discharge Overcurrent (Level 3) | Float |  | 0, Normal; 1, Fault | 0 | 1
test | 515 | 1 | 318 | 2 | 0 | BMS Comm Parameters 1 | Charge Overcurrent (Level 3) | Float |  | 0, Normal; 1, Fault | 0 | 1
test | 515 | 1 | 320 | 2 | 0 | BMS Comm Parameters 1 | Discharge Over-Temperature (Level 3) | Float |  | 0, Normal; 1, Fault | 0 | 1
test | 515 | 1 | 322 | 2 | 0 | BMS Comm Parameters 1 | Discharge Under-Temperature (Level 3) | Float |  | 0, Normal; 1, Fault | 0 | 1
test | 515 | 1 | 324 | 2 | 0 | BMS Comm Parameters 1 | Charge Over-Temperature (Level 3) | Float |  | 0, Normal; 1, Fault | 0 | 1
test | 515 | 1 | 326 | 2 | 0 | BMS Comm Parameters 1 | Charge Under-Temperature (Level 3) | Float |  | 0, Normal; 1, Fault | 0 | 1
test | 515 | 1 | 328 | 2 | 0 | BMS Comm Parameters 1 | Insulation Too Low (Level 3) | Float |  | 0, Normal; 1, Fault | 0 | 1
test | 515 | 1 | 330 | 2 | 0 | BMS Comm Parameters 1 | Pole Over-Temperature (Level 3) | Float |  | 0, Normal; 1, Fault | 0 | 1
test | 515 | 1 | 332 | 2 | 0 | BMS Comm Parameters 1 | HV Box Over-Temperature (Level 3) | Float |  | 0, Normal; 1, Fault | 0 | 1
test | 515 | 1 | 334 | 2 | 0 | BMS Comm Parameters 1 | Cell Voltage Difference (Level 3) | Float |  | 0, Normal; 1, Fault | 0 | 1
test | 515 | 1 | 336 | 2 | 0 | BMS Comm Parameters 1 | Cell Temperature Difference (Level 3) | Float |  | 0, Normal; 1, Fault | 0 | 1
test | 515 | 1 | 338 | 2 | 0 | BMS Comm Parameters 1 | SOC Too Low (Level 3) | Float |  | 0, Normal; 1, Fault | 0 | 1
test | 515 | 1 | 340 | 2 | 0 | BMS Comm Parameters 1 | Total Voltage Difference Too High (Level 1) | Float |  | 0, Normal; 1, Fault | 0 | 1
test | 515 | 1 | 342 | 2 | 0 | BMS Comm Parameters 1 | Module Overvoltage (Level 1) | Float |  | 0, Normal; 1, Fault | 0 | 1
test | 515 | 1 | 344 | 2 | 0 | BMS Comm Parameters 1 | Module Undervoltage (Level 1) | Float |  | 0, Normal; 1, Fault | 0 | 1
test | 515 | 1 | 346 | 2 | 0 | BMS Comm Parameters 1 | Temperature Rise Too High (Level 1) | Float |  | 0, Normal; 1, Fault | 0 | 1
test | 515 | 1 | 348 | 2 | 0 | BMS Comm Parameters 1 | Module Voltage Difference Too Large (Level 1) | Float |  | 0, Normal; 1, Fault | 0 | 1
test | 515 | 1 | 350 | 2 | 0 | BMS Comm Parameters 1 | Total Voltage Difference Too High (Level 2) | Float |  | 0, Normal; 1, Fault | 0 | 1
test | 515 | 1 | 352 | 2 | 0 | BMS Comm Parameters 1 | Module Overvoltage (Level 2) | Float |  | 0, Normal; 1, Fault | 0 | 1
test | 515 | 1 | 354 | 2 | 0 | BMS Comm Parameters 1 | Module Undervoltage (Level 2) | Float |  | 0, Normal; 1, Fault | 0 | 1
test | 515 | 1 | 356 | 2 | 0 | BMS Comm Parameters 1 | Temperature Rise Too High (Level 2) | Float |  | 0, Normal; 1, Fault | 0 | 1
test | 515 | 1 | 358 | 2 | 0 | BMS Comm Parameters 1 | Module Voltage Difference Too Large (Level 2) | Float |  | 0, Normal; 1, Fault | 0 | 1
test | 515 | 1 | 360 | 2 | 0 | BMS Comm Parameters 1 | Total Voltage Difference Too High (Level 3) | Float |  | 0, Normal; 1, Fault | 0 | 1
test | 515 | 1 | 362 | 2 | 0 | BMS Comm Parameters 1 | Module Overvoltage (Level 3) | Float |  | 0, Normal; 1, Fault | 0 | 1
test | 515 | 1 | 364 | 2 | 0 | BMS Comm Parameters 1 | Module Undervoltage (Level 3) | Float |  | 0, Normal; 1, Fault | 0 | 1
test | 515 | 1 | 366 | 2 | 0 | BMS Comm Parameters 1 | Temperature Rise Too High (Level 3) | Float |  | 0, Normal; 1, Fault | 0 | 1
test | 515 | 1 | 368 | 2 | 0 | BMS Comm Parameters 1 | Module Voltage Difference Too Large (Level 3) | Float |  | 0, Normal; 1, Fault | 0 | 1
test | 515 | 1 | 370 | 2 | 0 | BMS Comm Parameters 1 | Pre-Power-On Phase | Float |  | 0, Pending Start; 1, Precharging; 2, Precharging; 3, Precharge Success; 4, Precharge Failure | 0 | 1
test | 515 | 1 | 372 | 2 | 0 | BMS Comm Parameters 1 | System Status | Float |  | 0, Normal; 1, Charge Disabled; 2, Discharge Disabled; 3, Standby; 4, Stopped | 0 | 1
test | 515 | 1 | 374 | 2 | 0 | BMS Comm Parameters 1 | Heartbeat Frame | Float |  |  | 0 | 1
test | 515 | 1 | 376 | 2 | 0 | BMS Comm Parameters 1 | Slave Registration Status | Float |  | 0, Slave Registration Failed; 1, Slave Registration Success | 0 | 1
test | 515 | 1 | 378 | 2 | 0 | BMS Comm Parameters 1 | Precharge Failure Reason | Float |  |  | 0 | 1
test | 515 | 1 | 380 | 2 | 0 | BMS Comm Parameters 1 | Charge/Discharge Status | Float |  | 0, Resting; 1, Discharging; 2, Charging | 0 | 1
test | 515 | 1 | 382 | 2 | 0 | BMS Comm Parameters 1 | Full/Empty Flag | Float |  | 0, Invalid; 1, Fully Charged; 2, Fully Discharged | 0 | 1
test | 515 | 1 | 384 | 2 | 0 | BMS Comm Parameters 1 | Positive Contactor Status | Float |  | 0, Open; 1, Closed | 0 | 1
test | 515 | 1 | 386 | 2 | 0 | BMS Comm Parameters 1 | Precharge Contactor Status | Float |  | 0, Open; 1, Closed | 0 | 1
test | 515 | 1 | 388 | 2 | 0 | BMS Comm Parameters 1 | Negative Contactor Status | Float |  | 0, Open; 1, Closed | 0 | 1
test | 515 | 1 | 390 | 2 | 0 | BMS Comm Parameters 1 | Isolator Switch Feedback Status | Float |  | 0, Open; 1, Closed | 0 | 1
test | 515 | 1 | 392 | 2 | 0 | BMS Comm Parameters 1 | Slave Initialization Fault (Level 1) | Float |  | 0, Normal; 1, Fault | 0 | 1
test | 515 | 1 | 394 | 2 | 0 | BMS Comm Parameters 1 | Sampling Wire Fault (Level 1) | Float |  | 0, Normal; 1, Fault | 0 | 1
test | 515 | 1 | 396 | 2 | 0 | BMS Comm Parameters 1 | Connection Wire Fault (Level 1) | Float |  | 0, Normal; 1, Fault | 0 | 1
test | 515 | 1 | 398 | 2 | 0 | BMS Comm Parameters 1 | Sampling Chip Fault (Level 1) | Float |  | 0, Normal; 1, Fault | 0 | 1
test | 515 | 1 | 400 | 2 | 0 | BMS Comm Parameters 1 | Voltage Sampling Fault (Level 1) | Float |  | 0, Normal; 1, Fault | 0 | 1
test | 515 | 1 | 402 | 2 | 0 | BMS Comm Parameters 1 | Battery Temp Sampling Fault (Level 1) | Float |  | 0, Normal; 1, Fault | 0 | 1
test | 515 | 1 | 404 | 2 | 0 | BMS Comm Parameters 1 | Temperature Sensor Fault (Level 1) | Float |  | 0, Normal; 1, Fault | 0 | 1
test | 515 | 1 | 406 | 2 | 0 | BMS Comm Parameters 1 | Spare (Level 1) | Float |  | 0, Normal; 1, Fault | 0 | 1
test | 515 | 1 | 408 | 2 | 0 | BMS Comm Parameters 1 | EEPROM Fault (Level 1) | Float |  | 0, Normal; 1, Fault | 0 | 1
test | 515 | 1 | 410 | 2 | 0 | BMS Comm Parameters 1 | Passive Balancing Fault (Level 3) | Float |  | 0, Normal; 1, Fault | 0 | 1
test | 515 | 1 | 412 | 2 | 0 | BMS Comm Parameters 1 | Passive Balancing Temp Fault (Level 3) | Float |  | 0, Normal; 1, Fault | 0 | 1
test | 515 | 1 | 414 | 2 | 0 | BMS Comm Parameters 1 | Active Balancing Fault (Level 3) | Float |  | 0, Normal; 1, Fault | 0 | 1
test | 515 | 1 | 416 | 2 | 0 | BMS Comm Parameters 1 | Active Balancing Temp Fault (Level 3) | Float |  | 0, Normal; 1, Fault | 0 | 1
test | 515 | 1 | 418 | 2 | 0 | BMS Comm Parameters 1 | Pole Temperature Fault (Level 1) | Float |  | 0, Normal; 1, Fault | 0 | 1
test | 515 | 1 | 420 | 2 | 0 | BMS Comm Parameters 1 | Inter-Group Balancing Fault (Level 3) | Float |  | 0, Normal; 1, Fault | 0 | 1
test | 515 | 1 | 422 | 2 | 0 | BMS Comm Parameters 1 | Cell Voltage 1 | Float | mV |  | 0 | 1
test | 515 | 1 | 424 | 2 | 0 | BMS Comm Parameters 1 | Cell Voltage 2 | Float | mV |  | 0 | 1
test | 515 | 1 | 426 | 2 | 0 | BMS Comm Parameters 1 | Cell Voltage 3 | Float | mV |  | 0 | 1
test | 515 | 1 | 428 | 2 | 0 | BMS Comm Parameters 1 | Cell Voltage 4 | Float | mV |  | 0 | 1
test | 515 | 1 | 430 | 2 | 0 | BMS Comm Parameters 1 | Cell Voltage 5 | Float | mV |  | 0 | 1
test | 515 | 1 | 432 | 2 | 0 | BMS Comm Parameters 1 | Cell Voltage 6 | Float | mV |  | 0 | 1
test | 515 | 1 | 434 | 2 | 0 | BMS Comm Parameters 1 | Cell Voltage 7 | Float | mV |  | 0 | 1
test | 515 | 1 | 436 | 2 | 0 | BMS Comm Parameters 1 | Cell Voltage 8 | Float | mV |  | 0 | 1
test | 515 | 1 | 438 | 2 | 0 | BMS Comm Parameters 1 | Cell Voltage 9 | Float | mV |  | 0 | 1
test | 515 | 1 | 440 | 2 | 0 | BMS Comm Parameters 1 | Cell Voltage 10 | Float | mV |  | 0 | 1
test | 515 | 1 | 442 | 2 | 0 | BMS Comm Parameters 1 | Cell Voltage 11 | Float | mV |  | 0 | 1
test | 515 | 1 | 444 | 2 | 0 | BMS Comm Parameters 1 | Cell Voltage 12 | Float | mV |  | 0 | 1
test | 515 | 1 | 446 | 2 | 0 | BMS Comm Parameters 1 | Cell Voltage 13 | Float | mV |  | 0 | 1
test | 515 | 1 | 448 | 2 | 0 | BMS Comm Parameters 1 | Cell Voltage 14 | Float | mV |  | 0 | 1
test | 515 | 1 | 450 | 2 | 0 | BMS Comm Parameters 1 | Cell Voltage 15 | Float | mV |  | 0 | 1
test | 515 | 1 | 452 | 2 | 0 | BMS Comm Parameters 1 | Cell Voltage 16 | Float | mV |  | 0 | 1
test | 515 | 1 | 454 | 2 | 0 | BMS Comm Parameters 1 | Cell Voltage 17 | Float | mV |  | 0 | 1
test | 515 | 1 | 456 | 2 | 0 | BMS Comm Parameters 1 | Cell Voltage 18 | Float | mV |  | 0 | 1
test | 515 | 1 | 458 | 2 | 0 | BMS Comm Parameters 1 | Cell Voltage 19 | Float | mV |  | 0 | 1
test | 515 | 1 | 460 | 2 | 0 | BMS Comm Parameters 1 | Cell Voltage 20 | Float | mV |  | 0 | 1
test | 515 | 1 | 462 | 2 | 0 | BMS Comm Parameters 1 | Cell Voltage 21 | Float | mV |  | 0 | 1
test | 515 | 1 | 464 | 2 | 0 | BMS Comm Parameters 1 | Cell Voltage 22 | Float | mV |  | 0 | 1
test | 515 | 1 | 466 | 2 | 0 | BMS Comm Parameters 1 | Cell Voltage 23 | Float | mV |  | 0 | 1
test | 515 | 1 | 468 | 2 | 0 | BMS Comm Parameters 1 | Cell Voltage 24 | Float | mV |  | 0 | 1
test | 515 | 1 | 470 | 2 | 0 | BMS Comm Parameters 1 | Cell Voltage 25 | Float | mV |  | 0 | 1
test | 515 | 1 | 472 | 2 | 0 | BMS Comm Parameters 1 | Cell Voltage 26 | Float | mV |  | 0 | 1
test | 515 | 1 | 474 | 2 | 0 | BMS Comm Parameters 1 | Cell Voltage 27 | Float | mV |  | 0 | 1
test | 515 | 1 | 476 | 2 | 0 | BMS Comm Parameters 1 | Cell Voltage 28 | Float | mV |  | 0 | 1
test | 515 | 1 | 478 | 2 | 0 | BMS Comm Parameters 1 | Cell Voltage 29 | Float | mV |  | 0 | 1
test | 515 | 1 | 480 | 2 | 0 | BMS Comm Parameters 1 | Cell Voltage 30 | Float | mV |  | 0 | 1
test | 515 | 1 | 482 | 2 | 0 | BMS Comm Parameters 1 | Cell Voltage 31 | Float | mV |  | 0 | 1
test | 515 | 1 | 484 | 2 | 0 | BMS Comm Parameters 1 | Cell Voltage 32 | Float | mV |  | 0 | 1
test | 515 | 1 | 486 | 2 | 0 | BMS Comm Parameters 1 | Cell Voltage 33 | Float | mV |  | 0 | 1
test | 515 | 1 | 488 | 2 | 0 | BMS Comm Parameters 1 | Cell Voltage 34 | Float | mV |  | 0 | 1
test | 515 | 1 | 490 | 2 | 0 | BMS Comm Parameters 1 | Cell Voltage 35 | Float | mV |  | 0 | 1
test | 515 | 1 | 492 | 2 | 0 | BMS Comm Parameters 1 | Cell Voltage 36 | Float | mV |  | 0 | 1
test | 515 | 1 | 494 | 2 | 0 | BMS Comm Parameters 1 | Cell Voltage 37 | Float | mV |  | 0 | 1
test | 515 | 1 | 496 | 2 | 0 | BMS Comm Parameters 1 | Cell Voltage 38 | Float | mV |  | 0 | 1
test | 515 | 1 | 498 | 2 | 0 | BMS Comm Parameters 1 | Cell Voltage 39 | Float | mV |  | 0 | 1
test | 515 | 1 | 500 | 2 | 0 | BMS Comm Parameters 1 | Cell Voltage 40 | Float | mV |  | 0 | 1
test | 515 | 1 | 502 | 2 | 0 | BMS Comm Parameters 1 | Cell Voltage 41 | Float | mV |  | 0 | 1
test | 515 | 1 | 504 | 2 | 0 | BMS Comm Parameters 1 | Cell Voltage 42 | Float | mV |  | 0 | 1
test | 515 | 1 | 506 | 2 | 0 | BMS Comm Parameters 1 | Cell Voltage 43 | Float | mV |  | 0 | 1
test | 515 | 1 | 508 | 2 | 0 | BMS Comm Parameters 1 | Cell Voltage 44 | Float | mV |  | 0 | 1
test | 515 | 1 | 510 | 2 | 0 | BMS Comm Parameters 1 | Cell Voltage 45 | Float | mV |  | 0 | 1
test | 515 | 1 | 512 | 2 | 0 | BMS Comm Parameters 1 | Cell Voltage 46 | Float | mV |  | 0 | 1
test | 515 | 1 | 514 | 2 | 0 | BMS Comm Parameters 1 | Cell Voltage 47 | Float | mV |  | 0 | 1
test | 515 | 1 | 516 | 2 | 0 | BMS Comm Parameters 1 | Cell Voltage 48 | Float | mV |  | 0 | 1
test | 515 | 1 | 518 | 2 | 0 | BMS Comm Parameters 1 | Cell Voltage 49 | Float | mV |  | 0 | 1
test | 515 | 1 | 520 | 2 | 0 | BMS Comm Parameters 1 | Cell Voltage 50 | Float | mV |  | 0 | 1
test | 515 | 1 | 522 | 2 | 0 | BMS Comm Parameters 1 | Cell Voltage 51 | Float | mV |  | 0 | 1
test | 515 | 1 | 524 | 2 | 0 | BMS Comm Parameters 1 | Cell Voltage 52 | Float | mV |  | 0 | 1
test | 515 | 1 | 526 | 2 | 0 | BMS Comm Parameters 1 | Cell Voltage 53 | Float | mV |  | 0 | 1
test | 515 | 1 | 528 | 2 | 0 | BMS Comm Parameters 1 | Cell Voltage 54 | Float | mV |  | 0 | 1
test | 515 | 1 | 530 | 2 | 0 | BMS Comm Parameters 1 | Cell Voltage 55 | Float | mV |  | 0 | 1
test | 515 | 1 | 532 | 2 | 0 | BMS Comm Parameters 1 | Cell Voltage 56 | Float | mV |  | 0 | 1
test | 515 | 1 | 534 | 2 | 0 | BMS Comm Parameters 1 | Cell Voltage 57 | Float | mV |  | 0 | 1
test | 515 | 1 | 536 | 2 | 0 | BMS Comm Parameters 1 | Cell Voltage 58 | Float | mV |  | 0 | 1
test | 515 | 1 | 538 | 2 | 0 | BMS Comm Parameters 1 | Cell Voltage 59 | Float | mV |  | 0 | 1
test | 515 | 1 | 540 | 2 | 0 | BMS Comm Parameters 1 | Cell Voltage 60 | Float | mV |  | 0 | 1
test | 515 | 1 | 542 | 2 | 0 | BMS Comm Parameters 1 | Cell Voltage 61 | Float | mV |  | 0 | 1
test | 515 | 1 | 544 | 2 | 0 | BMS Comm Parameters 1 | Cell Voltage 62 | Float | mV |  | 0 | 1
test | 515 | 1 | 546 | 2 | 0 | BMS Comm Parameters 1 | Cell Voltage 63 | Float | mV |  | 0 | 1
test | 515 | 1 | 548 | 2 | 0 | BMS Comm Parameters 1 | Cell Voltage 64 | Float | mV |  | 0 | 1
test | 515 | 1 | 550 | 2 | 0 | BMS Comm Parameters 1 | Cell Voltage 65 | Float | mV |  | 0 | 1
test | 515 | 1 | 552 | 2 | 0 | BMS Comm Parameters 1 | Cell Voltage 66 | Float | mV |  | 0 | 1
test | 515 | 1 | 554 | 2 | 0 | BMS Comm Parameters 1 | Cell Voltage 67 | Float | mV |  | 0 | 1
test | 515 | 1 | 556 | 2 | 0 | BMS Comm Parameters 1 | Cell Voltage 68 | Float | mV |  | 0 | 1
test | 515 | 1 | 558 | 2 | 0 | BMS Comm Parameters 1 | Cell Voltage 69 | Float | mV |  | 0 | 1
test | 515 | 1 | 560 | 2 | 0 | BMS Comm Parameters 1 | Cell Voltage 70 | Float | mV |  | 0 | 1
test | 515 | 1 | 562 | 2 | 0 | BMS Comm Parameters 1 | Cell Voltage 71 | Float | mV |  | 0 | 1
test | 515 | 1 | 564 | 2 | 0 | BMS Comm Parameters 1 | Cell Voltage 72 | Float | mV |  | 0 | 1
test | 515 | 1 | 566 | 2 | 0 | BMS Comm Parameters 1 | Cell Voltage 73 | Float | mV |  | 0 | 1
test | 515 | 1 | 568 | 2 | 0 | BMS Comm Parameters 1 | Cell Voltage 74 | Float | mV |  | 0 | 1
test | 515 | 1 | 570 | 2 | 0 | BMS Comm Parameters 1 | Cell Voltage 75 | Float | mV |  | 0 | 1
test | 515 | 1 | 572 | 2 | 0 | BMS Comm Parameters 1 | Cell Voltage 76 | Float | mV |  | 0 | 1
test | 515 | 1 | 574 | 2 | 0 | BMS Comm Parameters 1 | Cell Voltage 77 | Float | mV |  | 0 | 1
test | 515 | 1 | 576 | 2 | 0 | BMS Comm Parameters 1 | Cell Voltage 78 | Float | mV |  | 0 | 1
test | 515 | 1 | 578 | 2 | 0 | BMS Comm Parameters 1 | Cell Voltage 79 | Float | mV |  | 0 | 1
test | 515 | 1 | 580 | 2 | 0 | BMS Comm Parameters 1 | Cell Voltage 80 | Float | mV |  | 0 | 1
test | 515 | 1 | 582 | 2 | 0 | BMS Comm Parameters 1 | Cell Voltage 81 | Float | mV |  | 0 | 1
test | 515 | 1 | 584 | 2 | 0 | BMS Comm Parameters 1 | Cell Voltage 82 | Float | mV |  | 0 | 1
test | 515 | 1 | 586 | 2 | 0 | BMS Comm Parameters 1 | Cell Voltage 83 | Float | mV |  | 0 | 1
test | 515 | 1 | 588 | 2 | 0 | BMS Comm Parameters 1 | Cell Voltage 84 | Float | mV |  | 0 | 1
test | 515 | 1 | 590 | 2 | 0 | BMS Comm Parameters 1 | Cell Voltage 85 | Float | mV |  | 0 | 1
test | 515 | 1 | 592 | 2 | 0 | BMS Comm Parameters 1 | Cell Voltage 86 | Float | mV |  | 0 | 1
test | 515 | 1 | 594 | 2 | 0 | BMS Comm Parameters 1 | Cell Voltage 87 | Float | mV |  | 0 | 1
test | 515 | 1 | 596 | 2 | 0 | BMS Comm Parameters 1 | Cell Voltage 88 | Float | mV |  | 0 | 1
test | 515 | 1 | 598 | 2 | 0 | BMS Comm Parameters 1 | Cell Voltage 89 | Float | mV |  | 0 | 1
test | 515 | 1 | 600 | 2 | 0 | BMS Comm Parameters 1 | Cell Voltage 90 | Float | mV |  | 0 | 1
test | 515 | 1 | 602 | 2 | 0 | BMS Comm Parameters 1 | Cell Voltage 91 | Float | mV |  | 0 | 1
test | 515 | 1 | 604 | 2 | 0 | BMS Comm Parameters 1 | Cell Voltage 92 | Float | mV |  | 0 | 1
test | 515 | 1 | 606 | 2 | 0 | BMS Comm Parameters 1 | Cell Voltage 93 | Float | mV |  | 0 | 1
test | 515 | 1 | 608 | 2 | 0 | BMS Comm Parameters 1 | Cell Voltage 94 | Float | mV |  | 0 | 1
test | 515 | 1 | 610 | 2 | 0 | BMS Comm Parameters 1 | Cell Voltage 95 | Float | mV |  | 0 | 1
test | 515 | 1 | 612 | 2 | 0 | BMS Comm Parameters 1 | Cell Voltage 96 | Float | mV |  | 0 | 1
test | 515 | 1 | 614 | 2 | 0 | BMS Comm Parameters 1 | Cell Voltage 97 | Float | mV |  | 0 | 1
test | 515 | 1 | 616 | 2 | 0 | BMS Comm Parameters 1 | Cell Voltage 98 | Float | mV |  | 0 | 1
test | 515 | 1 | 618 | 2 | 0 | BMS Comm Parameters 1 | Cell Voltage 99 | Float | mV |  | 0 | 1
test | 515 | 1 | 620 | 2 | 0 | BMS Comm Parameters 1 | Cell Voltage 100 | Float | mV |  | 0 | 1
test | 515 | 1 | 622 | 2 | 0 | BMS Comm Parameters 1 | Cell Voltage 101 | Float | mV |  | 0 | 1
test | 515 | 1 | 624 | 2 | 0 | BMS Comm Parameters 1 | Cell Voltage 102 | Float | mV |  | 0 | 1
test | 515 | 1 | 626 | 2 | 0 | BMS Comm Parameters 1 | Cell Voltage 103 | Float | mV |  | 0 | 1
test | 515 | 1 | 628 | 2 | 0 | BMS Comm Parameters 1 | Cell Voltage 104 | Float | mV |  | 0 | 1
test | 515 | 1 | 630 | 2 | 0 | BMS Comm Parameters 1 | Cell Voltage 105 | Float | mV |  | 0 | 1
test | 515 | 1 | 632 | 2 | 0 | BMS Comm Parameters 1 | Cell Voltage 106 | Float | mV |  | 0 | 1
test | 515 | 1 | 634 | 2 | 0 | BMS Comm Parameters 1 | Cell Voltage 107 | Float | mV |  | 0 | 1
test | 515 | 1 | 636 | 2 | 0 | BMS Comm Parameters 1 | Cell Voltage 108 | Float | mV |  | 0 | 1
test | 515 | 1 | 638 | 2 | 0 | BMS Comm Parameters 1 | Cell Voltage 109 | Float | mV |  | 0 | 1
test | 515 | 1 | 640 | 2 | 0 | BMS Comm Parameters 1 | Cell Voltage 110 | Float | mV |  | 0 | 1
test | 515 | 1 | 642 | 2 | 0 | BMS Comm Parameters 1 | Cell Voltage 111 | Float | mV |  | 0 | 1
test | 515 | 1 | 644 | 2 | 0 | BMS Comm Parameters 1 | Cell Voltage 112 | Float | mV |  | 0 | 1
test | 515 | 1 | 646 | 2 | 0 | BMS Comm Parameters 1 | Cell Voltage 113 | Float | mV |  | 0 | 1
test | 515 | 1 | 648 | 2 | 0 | BMS Comm Parameters 1 | Cell Voltage 114 | Float | mV |  | 0 | 1
test | 515 | 1 | 650 | 2 | 0 | BMS Comm Parameters 1 | Cell Voltage 115 | Float | mV |  | 0 | 1
test | 515 | 1 | 652 | 2 | 0 | BMS Comm Parameters 1 | Cell Voltage 116 | Float | mV |  | 0 | 1
test | 515 | 1 | 654 | 2 | 0 | BMS Comm Parameters 1 | Cell Voltage 117 | Float | mV |  | 0 | 1
test | 515 | 1 | 656 | 2 | 0 | BMS Comm Parameters 1 | Cell Voltage 118 | Float | mV |  | 0 | 1
test | 515 | 1 | 658 | 2 | 0 | BMS Comm Parameters 1 | Cell Voltage 119 | Float | mV |  | 0 | 1
test | 515 | 1 | 660 | 2 | 0 | BMS Comm Parameters 1 | Cell Voltage 120 | Float | mV |  | 0 | 1
test | 515 | 1 | 662 | 2 | 0 | BMS Comm Parameters 1 | Cell Voltage 121 | Float | mV |  | 0 | 1
test | 515 | 1 | 664 | 2 | 0 | BMS Comm Parameters 1 | Cell Voltage 122 | Float | mV |  | 0 | 1
test | 515 | 1 | 666 | 2 | 0 | BMS Comm Parameters 1 | Cell Voltage 123 | Float | mV |  | 0 | 1
test | 515 | 1 | 668 | 2 | 0 | BMS Comm Parameters 1 | Cell Voltage 124 | Float | mV |  | 0 | 1
test | 515 | 1 | 670 | 2 | 0 | BMS Comm Parameters 1 | Cell Voltage 125 | Float | mV |  | 0 | 1
test | 515 | 1 | 672 | 2 | 0 | BMS Comm Parameters 1 | Cell Voltage 126 | Float | mV |  | 0 | 1
test | 515 | 1 | 674 | 2 | 0 | BMS Comm Parameters 1 | Cell Voltage 127 | Float | mV |  | 0 | 1
test | 515 | 1 | 676 | 2 | 0 | BMS Comm Parameters 1 | Cell Voltage 128 | Float | mV |  | 0 | 1
test | 515 | 1 | 678 | 2 | 0 | BMS Comm Parameters 1 | Cell Voltage 129 | Float | mV |  | 0 | 1
test | 515 | 1 | 680 | 2 | 0 | BMS Comm Parameters 1 | Cell Voltage 130 | Float | mV |  | 0 | 1
test | 515 | 1 | 682 | 2 | 0 | BMS Comm Parameters 1 | Cell Voltage 131 | Float | mV |  | 0 | 1
test | 515 | 1 | 684 | 2 | 0 | BMS Comm Parameters 1 | Cell Voltage 132 | Float | mV |  | 0 | 1
test | 515 | 1 | 686 | 2 | 0 | BMS Comm Parameters 1 | Cell Voltage 133 | Float | mV |  | 0 | 1
test | 515 | 1 | 688 | 2 | 0 | BMS Comm Parameters 1 | Cell Voltage 134 | Float | mV |  | 0 | 1
test | 515 | 1 | 690 | 2 | 0 | BMS Comm Parameters 1 | Cell Voltage 135 | Float | mV |  | 0 | 1
test | 515 | 1 | 692 | 2 | 0 | BMS Comm Parameters 1 | Cell Voltage 136 | Float | mV |  | 0 | 1
test | 515 | 1 | 694 | 2 | 0 | BMS Comm Parameters 1 | Cell Voltage 137 | Float | mV |  | 0 | 1
test | 515 | 1 | 696 | 2 | 0 | BMS Comm Parameters 1 | Cell Voltage 138 | Float | mV |  | 0 | 1
test | 515 | 1 | 698 | 2 | 0 | BMS Comm Parameters 1 | Cell Voltage 139 | Float | mV |  | 0 | 1
test | 515 | 1 | 700 | 2 | 0 | BMS Comm Parameters 1 | Cell Voltage 140 | Float | mV |  | 0 | 1
test | 515 | 1 | 702 | 2 | 0 | BMS Comm Parameters 1 | Cell Voltage 141 | Float | mV |  | 0 | 1
test | 515 | 1 | 704 | 2 | 0 | BMS Comm Parameters 1 | Cell Voltage 142 | Float | mV |  | 0 | 1
test | 515 | 1 | 706 | 2 | 0 | BMS Comm Parameters 1 | Cell Voltage 143 | Float | mV |  | 0 | 1
test | 515 | 1 | 708 | 2 | 0 | BMS Comm Parameters 1 | Cell Voltage 144 | Float | mV |  | 0 | 1
test | 515 | 1 | 710 | 2 | 0 | BMS Comm Parameters 1 | Cell Voltage 145 | Float | mV |  | 0 | 1
test | 515 | 1 | 712 | 2 | 0 | BMS Comm Parameters 1 | Cell Voltage 146 | Float | mV |  | 0 | 1
test | 515 | 1 | 714 | 2 | 0 | BMS Comm Parameters 1 | Cell Voltage 147 | Float | mV |  | 0 | 1
test | 515 | 1 | 716 | 2 | 0 | BMS Comm Parameters 1 | Cell Voltage 148 | Float | mV |  | 0 | 1
test | 515 | 1 | 718 | 2 | 0 | BMS Comm Parameters 1 | Cell Voltage 149 | Float | mV |  | 0 | 1
test | 515 | 1 | 720 | 2 | 0 | BMS Comm Parameters 1 | Cell Voltage 150 | Float | mV |  | 0 | 1
test | 515 | 1 | 722 | 2 | 0 | BMS Comm Parameters 1 | Cell Voltage 151 | Float | mV |  | 0 | 1
test | 515 | 1 | 724 | 2 | 0 | BMS Comm Parameters 1 | Cell Voltage 152 | Float | mV |  | 0 | 1
test | 515 | 1 | 726 | 2 | 0 | BMS Comm Parameters 1 | Cell Voltage 153 | Float | mV |  | 0 | 1
test | 515 | 1 | 728 | 2 | 0 | BMS Comm Parameters 1 | Cell Voltage 154 | Float | mV |  | 0 | 1
test | 515 | 1 | 730 | 2 | 0 | BMS Comm Parameters 1 | Cell Voltage 155 | Float | mV |  | 0 | 1
test | 515 | 1 | 732 | 2 | 0 | BMS Comm Parameters 1 | Cell Voltage 156 | Float | mV |  | 0 | 1
test | 515 | 1 | 734 | 2 | 0 | BMS Comm Parameters 1 | Cell Voltage 157 | Float | mV |  | 0 | 1
test | 515 | 1 | 736 | 2 | 0 | BMS Comm Parameters 1 | Cell Voltage 158 | Float | mV |  | 0 | 1
test | 515 | 1 | 738 | 2 | 0 | BMS Comm Parameters 1 | Cell Voltage 159 | Float | mV |  | 0 | 1
test | 515 | 1 | 740 | 2 | 0 | BMS Comm Parameters 1 | Cell Voltage 160 | Float | mV |  | 0 | 1
test | 515 | 1 | 742 | 2 | 0 | BMS Comm Parameters 1 | Cell Voltage 161 | Float | mV |  | 0 | 1
test | 515 | 1 | 744 | 2 | 0 | BMS Comm Parameters 1 | Cell Voltage 162 | Float | mV |  | 0 | 1
test | 515 | 1 | 746 | 2 | 0 | BMS Comm Parameters 1 | Cell Voltage 163 | Float | mV |  | 0 | 1
test | 515 | 1 | 748 | 2 | 0 | BMS Comm Parameters 1 | Cell Voltage 164 | Float | mV |  | 0 | 1
test | 515 | 1 | 750 | 2 | 0 | BMS Comm Parameters 1 | Cell Voltage 165 | Float | mV |  | 0 | 1
test | 515 | 1 | 752 | 2 | 0 | BMS Comm Parameters 1 | Cell Voltage 166 | Float | mV |  | 0 | 1
test | 515 | 1 | 754 | 2 | 0 | BMS Comm Parameters 1 | Cell Voltage 167 | Float | mV |  | 0 | 1
test | 515 | 1 | 756 | 2 | 0 | BMS Comm Parameters 1 | Cell Voltage 168 | Float | mV |  | 0 | 1
test | 515 | 1 | 758 | 2 | 0 | BMS Comm Parameters 1 | Cell Voltage 169 | Float | mV |  | 0 | 1
test | 515 | 1 | 760 | 2 | 0 | BMS Comm Parameters 1 | Cell Voltage 170 | Float | mV |  | 0 | 1
test | 515 | 1 | 762 | 2 | 0 | BMS Comm Parameters 1 | Cell Voltage 171 | Float | mV |  | 0 | 1
test | 515 | 1 | 764 | 2 | 0 | BMS Comm Parameters 1 | Cell Voltage 172 | Float | mV |  | 0 | 1
test | 515 | 1 | 766 | 2 | 0 | BMS Comm Parameters 1 | Cell Voltage 173 | Float | mV |  | 0 | 1
test | 515 | 1 | 768 | 2 | 0 | BMS Comm Parameters 1 | Cell Voltage 174 | Float | mV |  | 0 | 1
test | 515 | 1 | 770 | 2 | 0 | BMS Comm Parameters 1 | Cell Voltage 175 | Float | mV |  | 0 | 1
test | 515 | 1 | 772 | 2 | 0 | BMS Comm Parameters 1 | Cell Voltage 176 | Float | mV |  | 0 | 1
test | 515 | 1 | 774 | 2 | 0 | BMS Comm Parameters 1 | Cell Voltage 177 | Float | mV |  | 0 | 1
test | 515 | 1 | 776 | 2 | 0 | BMS Comm Parameters 1 | Cell Voltage 178 | Float | mV |  | 0 | 1
test | 515 | 1 | 778 | 2 | 0 | BMS Comm Parameters 1 | Cell Voltage 179 | Float | mV |  | 0 | 1
test | 515 | 1 | 780 | 2 | 0 | BMS Comm Parameters 1 | Cell Voltage 180 | Float | mV |  | 0 | 1
test | 515 | 1 | 782 | 2 | 0 | BMS Comm Parameters 1 | Cell Voltage 181 | Float | mV |  | 0 | 1
test | 515 | 1 | 784 | 2 | 0 | BMS Comm Parameters 1 | Cell Voltage 182 | Float | mV |  | 0 | 1
test | 515 | 1 | 786 | 2 | 0 | BMS Comm Parameters 1 | Cell Voltage 183 | Float | mV |  | 0 | 1
test | 515 | 1 | 788 | 2 | 0 | BMS Comm Parameters 1 | Cell Voltage 184 | Float | mV |  | 0 | 1
test | 515 | 1 | 790 | 2 | 0 | BMS Comm Parameters 1 | Cell Voltage 185 | Float | mV |  | 0 | 1
test | 515 | 1 | 792 | 2 | 0 | BMS Comm Parameters 1 | Cell Voltage 186 | Float | mV |  | 0 | 1
test | 515 | 1 | 794 | 2 | 0 | BMS Comm Parameters 1 | Cell Voltage 187 | Float | mV |  | 0 | 1
test | 515 | 1 | 796 | 2 | 0 | BMS Comm Parameters 1 | Cell Voltage 188 | Float | mV |  | 0 | 1
test | 515 | 1 | 798 | 2 | 0 | BMS Comm Parameters 1 | Cell Voltage 189 | Float | mV |  | 0 | 1
test | 515 | 1 | 800 | 2 | 0 | BMS Comm Parameters 1 | Cell Voltage 190 | Float | mV |  | 0 | 1
test | 515 | 1 | 802 | 2 | 0 | BMS Comm Parameters 1 | Cell Voltage 191 | Float | mV |  | 0 | 1
test | 515 | 1 | 804 | 2 | 0 | BMS Comm Parameters 1 | Cell Voltage 192 | Float | mV |  | 0 | 1
test | 515 | 1 | 806 | 2 | 0 | BMS Comm Parameters 1 | Cell Voltage 193 | Float | mV |  | 0 | 1
test | 515 | 1 | 808 | 2 | 0 | BMS Comm Parameters 1 | Cell Voltage 194 | Float | mV |  | 0 | 1
test | 515 | 1 | 810 | 2 | 0 | BMS Comm Parameters 1 | Cell Voltage 195 | Float | mV |  | 0 | 1
test | 515 | 1 | 812 | 2 | 0 | BMS Comm Parameters 1 | Cell Voltage 196 | Float | mV |  | 0 | 1
test | 515 | 1 | 814 | 2 | 0 | BMS Comm Parameters 1 | Cell Voltage 197 | Float | mV |  | 0 | 1
test | 515 | 1 | 816 | 2 | 0 | BMS Comm Parameters 1 | Cell Voltage 198 | Float | mV |  | 0 | 1
test | 515 | 1 | 818 | 2 | 0 | BMS Comm Parameters 1 | Cell Voltage 199 | Float | mV |  | 0 | 1
test | 515 | 1 | 820 | 2 | 0 | BMS Comm Parameters 1 | Cell Voltage 200 | Float | mV |  | 0 | 1
test | 515 | 1 | 822 | 2 | 0 | BMS Comm Parameters 1 | Cell Voltage 201 | Float | mV |  | 0 | 1
test | 515 | 1 | 824 | 2 | 0 | BMS Comm Parameters 1 | Cell Voltage 202 | Float | mV |  | 0 | 1
test | 515 | 1 | 826 | 2 | 0 | BMS Comm Parameters 1 | Cell Voltage 203 | Float | mV |  | 0 | 1
test | 515 | 1 | 828 | 2 | 0 | BMS Comm Parameters 1 | Cell Voltage 204 | Float | mV |  | 0 | 1
test | 515 | 1 | 830 | 2 | 0 | BMS Comm Parameters 1 | Cell Voltage 205 | Float | mV |  | 0 | 1
test | 515 | 1 | 832 | 2 | 0 | BMS Comm Parameters 1 | Cell Voltage 206 | Float | mV |  | 0 | 1
test | 515 | 1 | 834 | 2 | 0 | BMS Comm Parameters 1 | Cell Voltage 207 | Float | mV |  | 0 | 1
test | 515 | 1 | 836 | 2 | 0 | BMS Comm Parameters 1 | Cell Voltage 208 | Float | mV |  | 0 | 1
test | 515 | 1 | 838 | 2 | 0 | BMS Comm Parameters 1 | Cell Voltage 209 | Float | mV |  | 0 | 1
test | 515 | 1 | 840 | 2 | 0 | BMS Comm Parameters 1 | Cell Voltage 210 | Float | mV |  | 0 | 1
test | 515 | 1 | 842 | 2 | 0 | BMS Comm Parameters 1 | Cell Voltage 211 | Float | mV |  | 0 | 1
test | 515 | 1 | 844 | 2 | 0 | BMS Comm Parameters 1 | Cell Voltage 212 | Float | mV |  | 0 | 1
test | 515 | 1 | 846 | 2 | 0 | BMS Comm Parameters 1 | Cell Voltage 213 | Float | mV |  | 0 | 1
test | 515 | 1 | 848 | 2 | 0 | BMS Comm Parameters 1 | Cell Voltage 214 | Float | mV |  | 0 | 1
test | 515 | 1 | 850 | 2 | 0 | BMS Comm Parameters 1 | Cell Voltage 215 | Float | mV |  | 0 | 1
test | 515 | 1 | 852 | 2 | 0 | BMS Comm Parameters 1 | Cell Voltage 216 | Float | mV |  | 0 | 1
test | 515 | 1 | 854 | 2 | 0 | BMS Comm Parameters 1 | Cell Voltage 217 | Float | mV |  | 0 | 1
test | 515 | 1 | 856 | 2 | 0 | BMS Comm Parameters 1 | Cell Voltage 218 | Float | mV |  | 0 | 1
test | 515 | 1 | 858 | 2 | 0 | BMS Comm Parameters 1 | Cell Voltage 219 | Float | mV |  | 0 | 1
test | 515 | 1 | 860 | 2 | 0 | BMS Comm Parameters 1 | Cell Voltage 220 | Float | mV |  | 0 | 1
test | 515 | 1 | 862 | 2 | 0 | BMS Comm Parameters 1 | Cell Voltage 221 | Float | mV |  | 0 | 1
test | 515 | 1 | 864 | 2 | 0 | BMS Comm Parameters 1 | Cell Voltage 222 | Float | mV |  | 0 | 1
test | 515 | 1 | 866 | 2 | 0 | BMS Comm Parameters 1 | Cell Voltage 223 | Float | mV |  | 0 | 1
test | 515 | 1 | 868 | 2 | 0 | BMS Comm Parameters 1 | Cell Voltage 224 | Float | mV |  | 0 | 1
test | 515 | 1 | 870 | 2 | 0 | BMS Comm Parameters 1 | Cell Voltage 225 | Float | mV |  | 0 | 1
test | 515 | 1 | 872 | 2 | 0 | BMS Comm Parameters 1 | Cell Voltage 226 | Float | mV |  | 0 | 1
test | 515 | 1 | 874 | 2 | 0 | BMS Comm Parameters 1 | Cell Voltage 227 | Float | mV |  | 0 | 1
test | 515 | 1 | 876 | 2 | 0 | BMS Comm Parameters 1 | Cell Voltage 228 | Float | mV |  | 0 | 1
test | 515 | 1 | 878 | 2 | 0 | BMS Comm Parameters 1 | Cell Voltage 229 | Float | mV |  | 0 | 1
test | 515 | 1 | 880 | 2 | 0 | BMS Comm Parameters 1 | Cell Voltage 230 | Float | mV |  | 0 | 1
test | 515 | 1 | 882 | 2 | 0 | BMS Comm Parameters 1 | Cell Voltage 231 | Float | mV |  | 0 | 1
test | 515 | 1 | 884 | 2 | 0 | BMS Comm Parameters 1 | Cell Voltage 232 | Float | mV |  | 0 | 1
test | 515 | 1 | 886 | 2 | 0 | BMS Comm Parameters 1 | Cell Voltage 233 | Float | mV |  | 0 | 1
test | 515 | 1 | 888 | 2 | 0 | BMS Comm Parameters 1 | Cell Voltage 234 | Float | mV |  | 0 | 1
test | 515 | 1 | 890 | 2 | 0 | BMS Comm Parameters 1 | Cell Voltage 235 | Float | mV |  | 0 | 1
test | 515 | 1 | 892 | 2 | 0 | BMS Comm Parameters 1 | Cell Voltage 236 | Float | mV |  | 0 | 1
test | 515 | 1 | 894 | 2 | 0 | BMS Comm Parameters 1 | Cell Voltage 237 | Float | mV |  | 0 | 1
test | 515 | 1 | 896 | 2 | 0 | BMS Comm Parameters 1 | Cell Voltage 238 | Float | mV |  | 0 | 1
test | 515 | 1 | 898 | 2 | 0 | BMS Comm Parameters 1 | Cell Voltage 239 | Float | mV |  | 0 | 1
test | 515 | 1 | 900 | 2 | 0 | BMS Comm Parameters 1 | Cell Voltage 240 | Float | mV |  | 0 | 1
test | 515 | 1 | 902 | 2 | 0 | BMS Comm Parameters 1 | Cell Voltage 241 | Float | mV |  | 0 | 1
test | 515 | 1 | 904 | 2 | 0 | BMS Comm Parameters 1 | Cell Voltage 242 | Float | mV |  | 0 | 1
test | 515 | 1 | 906 | 2 | 0 | BMS Comm Parameters 1 | Cell Voltage 243 | Float | mV |  | 0 | 1
test | 515 | 1 | 908 | 2 | 0 | BMS Comm Parameters 1 | Cell Voltage 244 | Float | mV |  | 0 | 1
test | 515 | 1 | 910 | 2 | 0 | BMS Comm Parameters 1 | Cell Voltage 245 | Float | mV |  | 0 | 1
test | 515 | 1 | 912 | 2 | 0 | BMS Comm Parameters 1 | Cell Voltage 246 | Float | mV |  | 0 | 1
test | 515 | 1 | 914 | 2 | 0 | BMS Comm Parameters 1 | Cell Voltage 247 | Float | mV |  | 0 | 1
test | 515 | 1 | 916 | 2 | 0 | BMS Comm Parameters 1 | Cell Voltage 248 | Float | mV |  | 0 | 1
test | 515 | 1 | 918 | 2 | 0 | BMS Comm Parameters 1 | Cell Voltage 249 | Float | mV |  | 0 | 1
test | 515 | 1 | 920 | 2 | 0 | BMS Comm Parameters 1 | Cell Voltage 250 | Float | mV |  | 0 | 1
test | 515 | 1 | 922 | 2 | 0 | BMS Comm Parameters 1 | Cell Voltage 251 | Float | mV |  | 0 | 1
test | 515 | 1 | 924 | 2 | 0 | BMS Comm Parameters 1 | Cell Voltage 252 | Float | mV |  | 0 | 1
test | 515 | 1 | 926 | 2 | 0 | BMS Comm Parameters 1 | Cell Voltage 253 | Float | mV |  | 0 | 1
test | 515 | 1 | 928 | 2 | 0 | BMS Comm Parameters 1 | Cell Voltage 254 | Float | mV |  | 0 | 1
test | 515 | 1 | 930 | 2 | 0 | BMS Comm Parameters 1 | Cell Voltage 255 | Float | mV |  | 0 | 1
test | 515 | 1 | 932 | 2 | 0 | BMS Comm Parameters 1 | Cell Voltage 256 | Float | mV |  | 0 | 1
test | 515 | 1 | 934 | 2 | 0 | BMS Comm Parameters 1 | Cell Voltage 257 | Float | mV |  | 0 | 1
test | 515 | 1 | 936 | 2 | 0 | BMS Comm Parameters 1 | Cell Voltage 258 | Float | mV |  | 0 | 1
test | 515 | 1 | 938 | 2 | 0 | BMS Comm Parameters 1 | Cell Voltage 259 | Float | mV |  | 0 | 1
test | 515 | 1 | 940 | 2 | 0 | BMS Comm Parameters 1 | Cell Voltage 260 | Float | mV |  | 0 | 1
test | 515 | 1 | 942 | 2 | 0 | BMS Comm Parameters 1 | Battery Temperature 1 | Float | ℃ |  | 0 | 1
test | 515 | 1 | 944 | 2 | 0 | BMS Comm Parameters 1 | Battery Temperature 2 | Float | ℃ |  | 0 | 1
test | 515 | 1 | 946 | 2 | 0 | BMS Comm Parameters 1 | Battery Temperature 3 | Float | ℃ |  | 0 | 1
test | 515 | 1 | 948 | 2 | 0 | BMS Comm Parameters 1 | Battery Temperature 4 | Float | ℃ |  | 0 | 1
test | 515 | 1 | 950 | 2 | 0 | BMS Comm Parameters 1 | Battery Temperature 5 | Float | ℃ |  | 0 | 1
test | 515 | 1 | 952 | 2 | 0 | BMS Comm Parameters 1 | Battery Temperature 6 | Float | ℃ |  | 0 | 1
test | 515 | 1 | 954 | 2 | 0 | BMS Comm Parameters 1 | Battery Temperature 7 | Float | ℃ |  | 0 | 1
test | 515 | 1 | 956 | 2 | 0 | BMS Comm Parameters 1 | Battery Temperature 8 | Float | ℃ |  | 0 | 1
test | 515 | 1 | 958 | 2 | 0 | BMS Comm Parameters 1 | Battery Temperature 9 | Float | ℃ |  | 0 | 1
test | 515 | 1 | 960 | 2 | 0 | BMS Comm Parameters 1 | Battery Temperature 10 | Float | ℃ |  | 0 | 1
test | 515 | 1 | 962 | 2 | 0 | BMS Comm Parameters 1 | Battery Temperature 11 | Float | ℃ |  | 0 | 1
test | 515 | 1 | 964 | 2 | 0 | BMS Comm Parameters 1 | Battery Temperature 12 | Float | ℃ |  | 0 | 1
test | 515 | 1 | 966 | 2 | 0 | BMS Comm Parameters 1 | Battery Temperature 13 | Float | ℃ |  | 0 | 1
test | 515 | 1 | 968 | 2 | 0 | BMS Comm Parameters 1 | Battery Temperature 14 | Float | ℃ |  | 0 | 1
test | 515 | 1 | 970 | 2 | 0 | BMS Comm Parameters 1 | Battery Temperature 15 | Float | ℃ |  | 0 | 1
test | 515 | 1 | 972 | 2 | 0 | BMS Comm Parameters 1 | Battery Temperature 16 | Float | ℃ |  | 0 | 1
test | 515 | 1 | 974 | 2 | 0 | BMS Comm Parameters 1 | Battery Temperature 17 | Float | ℃ |  | 0 | 1
test | 515 | 1 | 976 | 2 | 0 | BMS Comm Parameters 1 | Battery Temperature 18 | Float | ℃ |  | 0 | 1
test | 515 | 1 | 978 | 2 | 0 | BMS Comm Parameters 1 | Battery Temperature 19 | Float | ℃ |  | 0 | 1
test | 515 | 1 | 980 | 2 | 0 | BMS Comm Parameters 1 | Battery Temperature 20 | Float | ℃ |  | 0 | 1
test | 515 | 1 | 982 | 2 | 0 | BMS Comm Parameters 1 | Battery Temperature 21 | Float | ℃ |  | 0 | 1
test | 515 | 1 | 984 | 2 | 0 | BMS Comm Parameters 1 | Battery Temperature 22 | Float | ℃ |  | 0 | 1
test | 515 | 1 | 986 | 2 | 0 | BMS Comm Parameters 1 | Battery Temperature 23 | Float | ℃ |  | 0 | 1
test | 515 | 1 | 988 | 2 | 0 | BMS Comm Parameters 1 | Battery Temperature 24 | Float | ℃ |  | 0 | 1
test | 515 | 1 | 990 | 2 | 0 | BMS Comm Parameters 1 | Battery Temperature 25 | Float | ℃ |  | 0 | 1
test | 515 | 1 | 992 | 2 | 0 | BMS Comm Parameters 1 | Battery Temperature 26 | Float | ℃ |  | 0 | 1
test | 515 | 1 | 994 | 2 | 0 | BMS Comm Parameters 1 | Battery Temperature 27 | Float | ℃ |  | 0 | 1
test | 515 | 1 | 996 | 2 | 0 | BMS Comm Parameters 1 | Battery Temperature 28 | Float | ℃ |  | 0 | 1
test | 515 | 1 | 998 | 2 | 0 | BMS Comm Parameters 1 | Battery Temperature 29 | Float | ℃ |  | 0 | 1
test | 515 | 1 | 1000 | 2 | 0 | BMS Comm Parameters 1 | Battery Temperature 30 | Float | ℃ |  | 0 | 1
test | 515 | 1 | 1002 | 2 | 0 | BMS Comm Parameters 1 | Battery Temperature 31 | Float | ℃ |  | 0 | 1
test | 515 | 1 | 1004 | 2 | 0 | BMS Comm Parameters 1 | Battery Temperature 32 | Float | ℃ |  | 0 | 1
test | 515 | 1 | 1006 | 2 | 0 | BMS Comm Parameters 1 | Battery Temperature 33 | Float | ℃ |  | 0 | 1
test | 515 | 1 | 1008 | 2 | 0 | BMS Comm Parameters 1 | Battery Temperature 34 | Float | ℃ |  | 0 | 1
test | 515 | 1 | 1010 | 2 | 0 | BMS Comm Parameters 1 | Battery Temperature 35 | Float | ℃ |  | 0 | 1
test | 515 | 1 | 1012 | 2 | 0 | BMS Comm Parameters 1 | Battery Temperature 36 | Float | ℃ |  | 0 | 1
test | 515 | 1 | 1014 | 2 | 0 | BMS Comm Parameters 1 | Battery Temperature 37 | Float | ℃ |  | 0 | 1
test | 515 | 1 | 1016 | 2 | 0 | BMS Comm Parameters 1 | Battery Temperature 38 | Float | ℃ |  | 0 | 1
test | 515 | 1 | 1018 | 2 | 0 | BMS Comm Parameters 1 | Battery Temperature 39 | Float | ℃ |  | 0 | 1
test | 515 | 1 | 1020 | 2 | 0 | BMS Comm Parameters 1 | Battery Temperature 40 | Float | ℃ |  | 0 | 1
test | 515 | 1 | 1022 | 2 | 0 | BMS Comm Parameters 1 | Battery Temperature 41 | Float | ℃ |  | 0 | 1
test | 515 | 1 | 1024 | 2 | 0 | BMS Comm Parameters 1 | Battery Temperature 42 | Float | ℃ |  | 0 | 1
test | 515 | 1 | 1026 | 2 | 0 | BMS Comm Parameters 1 | Battery Temperature 43 | Float | ℃ |  | 0 | 1
test | 515 | 1 | 1028 | 2 | 0 | BMS Comm Parameters 1 | Battery Temperature 44 | Float | ℃ |  | 0 | 1
test | 515 | 1 | 1030 | 2 | 0 | BMS Comm Parameters 1 | Battery Temperature 45 | Float | ℃ |  | 0 | 1
test | 515 | 1 | 1032 | 2 | 0 | BMS Comm Parameters 1 | Battery Temperature 46 | Float | ℃ |  | 0 | 1
test | 515 | 1 | 1034 | 2 | 0 | BMS Comm Parameters 1 | Battery Temperature 47 | Float | ℃ |  | 0 | 1
test | 515 | 1 | 1036 | 2 | 0 | BMS Comm Parameters 1 | Battery Temperature 48 | Float | ℃ |  | 0 | 1
test | 515 | 1 | 1038 | 2 | 0 | BMS Comm Parameters 1 | Battery Temperature 49 | Float | ℃ |  | 0 | 1
test | 515 | 1 | 1040 | 2 | 0 | BMS Comm Parameters 1 | Battery Temperature 50 | Float | ℃ |  | 0 | 1
test | 515 | 1 | 1042 | 2 | 0 | BMS Comm Parameters 1 | Battery Temperature 51 | Float | ℃ |  | 0 | 1
test | 515 | 1 | 1044 | 2 | 0 | BMS Comm Parameters 1 | Battery Temperature 52 | Float | ℃ |  | 0 | 1
test | 515 | 1 | 1046 | 2 | 0 | BMS Comm Parameters 1 | Battery Temperature 53 | Float | ℃ |  | 0 | 1
test | 515 | 1 | 1048 | 2 | 0 | BMS Comm Parameters 1 | Battery Temperature 54 | Float | ℃ |  | 0 | 1
test | 515 | 1 | 1050 | 2 | 0 | BMS Comm Parameters 1 | Battery Temperature 55 | Float | ℃ |  | 0 | 1
test | 515 | 1 | 1052 | 2 | 0 | BMS Comm Parameters 1 | Battery Temperature 56 | Float | ℃ |  | 0 | 1
test | 515 | 1 | 1054 | 2 | 0 | BMS Comm Parameters 1 | Battery Temperature 57 | Float | ℃ |  | 0 | 1
test | 515 | 1 | 1056 | 2 | 0 | BMS Comm Parameters 1 | Battery Temperature 58 | Float | ℃ |  | 0 | 1
test | 515 | 1 | 1058 | 2 | 0 | BMS Comm Parameters 1 | Battery Temperature 59 | Float | ℃ |  | 0 | 1
test | 515 | 1 | 1060 | 2 | 0 | BMS Comm Parameters 1 | Battery Temperature 60 | Float | ℃ |  | 0 | 1
test | 515 | 1 | 1062 | 2 | 0 | BMS Comm Parameters 1 | Battery Temperature 61 | Float | ℃ |  | 0 | 1
test | 515 | 1 | 1064 | 2 | 0 | BMS Comm Parameters 1 | Battery Temperature 62 | Float | ℃ |  | 0 | 1
test | 515 | 1 | 1066 | 2 | 0 | BMS Comm Parameters 1 | Battery Temperature 63 | Float | ℃ |  | 0 | 1
test | 515 | 1 | 1068 | 2 | 0 | BMS Comm Parameters 1 | Battery Temperature 64 | Float | ℃ |  | 0 | 1
test | 515 | 1 | 1070 | 2 | 0 | BMS Comm Parameters 1 | Battery Temperature 65 | Float | ℃ |  | 0 | 1
test | 515 | 1 | 1072 | 2 | 0 | BMS Comm Parameters 1 | Battery Temperature 66 | Float | ℃ |  | 0 | 1
test | 515 | 1 | 1074 | 2 | 0 | BMS Comm Parameters 1 | Battery Temperature 67 | Float | ℃ |  | 0 | 1
test | 515 | 1 | 1076 | 2 | 0 | BMS Comm Parameters 1 | Battery Temperature 68 | Float | ℃ |  | 0 | 1
test | 515 | 1 | 1078 | 2 | 0 | BMS Comm Parameters 1 | Battery Temperature 69 | Float | ℃ |  | 0 | 1
test | 515 | 1 | 1080 | 2 | 0 | BMS Comm Parameters 1 | Battery Temperature 70 | Float | ℃ |  | 0 | 1
test | 515 | 1 | 1082 | 2 | 0 | BMS Comm Parameters 1 | Battery Temperature 71 | Float | ℃ |  | 0 | 1
test | 515 | 1 | 1084 | 2 | 0 | BMS Comm Parameters 1 | Battery Temperature 72 | Float | ℃ |  | 0 | 1
test | 515 | 1 | 1086 | 2 | 0 | BMS Comm Parameters 1 | Battery Temperature 73 | Float | ℃ |  | 0 | 1
test | 515 | 1 | 1088 | 2 | 0 | BMS Comm Parameters 1 | Battery Temperature 74 | Float | ℃ |  | 0 | 1
test | 515 | 1 | 1090 | 2 | 0 | BMS Comm Parameters 1 | Battery Temperature 75 | Float | ℃ |  | 0 | 1
test | 515 | 1 | 1092 | 2 | 0 | BMS Comm Parameters 1 | Battery Temperature 76 | Float | ℃ |  | 0 | 1
test | 515 | 1 | 1094 | 2 | 0 | BMS Comm Parameters 1 | Battery Temperature 77 | Float | ℃ |  | 0 | 1
test | 515 | 1 | 1096 | 2 | 0 | BMS Comm Parameters 1 | Battery Temperature 78 | Float | ℃ |  | 0 | 1
test | 515 | 1 | 1098 | 2 | 0 | BMS Comm Parameters 1 | Battery Temperature 79 | Float | ℃ |  | 0 | 1
test | 515 | 1 | 1100 | 2 | 0 | BMS Comm Parameters 1 | Battery Temperature 80 | Float | ℃ |  | 0 | 1
test | 515 | 1 | 1102 | 2 | 0 | BMS Comm Parameters 1 | Battery Temperature 81 | Float | ℃ |  | 0 | 1
test | 515 | 1 | 1104 | 2 | 0 | BMS Comm Parameters 1 | Battery Temperature 82 | Float | ℃ |  | 0 | 1
test | 515 | 1 | 1106 | 2 | 0 | BMS Comm Parameters 1 | Battery Temperature 83 | Float | ℃ |  | 0 | 1
test | 515 | 1 | 1108 | 2 | 0 | BMS Comm Parameters 1 | Battery Temperature 84 | Float | ℃ |  | 0 | 1
test | 515 | 1 | 1110 | 2 | 0 | BMS Comm Parameters 1 | Battery Temperature 85 | Float | ℃ |  | 0 | 1
test | 515 | 1 | 1112 | 2 | 0 | BMS Comm Parameters 1 | Battery Temperature 86 | Float | ℃ |  | 0 | 1
test | 515 | 1 | 1114 | 2 | 0 | BMS Comm Parameters 1 | Battery Temperature 87 | Float | ℃ |  | 0 | 1
test | 515 | 1 | 1116 | 2 | 0 | BMS Comm Parameters 1 | Battery Temperature 88 | Float | ℃ |  | 0 | 1
test | 515 | 1 | 1118 | 2 | 0 | BMS Comm Parameters 1 | Battery Temperature 89 | Float | ℃ |  | 0 | 1
test | 515 | 1 | 1120 | 2 | 0 | BMS Comm Parameters 1 | Battery Temperature 90 | Float | ℃ |  | 0 | 1
test | 515 | 1 | 1122 | 2 | 0 | BMS Comm Parameters 1 | Battery Temperature 91 | Float | ℃ |  | 0 | 1
test | 515 | 1 | 1124 | 2 | 0 | BMS Comm Parameters 1 | Battery Temperature 92 | Float | ℃ |  | 0 | 1
test | 515 | 1 | 1126 | 2 | 0 | BMS Comm Parameters 1 | Battery Temperature 93 | Float | ℃ |  | 0 | 1
test | 515 | 1 | 1128 | 2 | 0 | BMS Comm Parameters 1 | Battery Temperature 94 | Float | ℃ |  | 0 | 1
test | 515 | 1 | 1130 | 2 | 0 | BMS Comm Parameters 1 | Battery Temperature 95 | Float | ℃ |  | 0 | 1
test | 515 | 1 | 1132 | 2 | 0 | BMS Comm Parameters 1 | Battery Temperature 96 | Float | ℃ |  | 0 | 1
test | 515 | 1 | 1134 | 2 | 0 | BMS Comm Parameters 1 | Battery Temperature 97 | Float | ℃ |  | 0 | 1
test | 515 | 1 | 1136 | 2 | 0 | BMS Comm Parameters 1 | Battery Temperature 98 | Float | ℃ |  | 0 | 1
test | 515 | 1 | 1138 | 2 | 0 | BMS Comm Parameters 1 | Battery Temperature 99 | Float | ℃ |  | 0 | 1
test | 515 | 1 | 1140 | 2 | 0 | BMS Comm Parameters 1 | Battery Temperature 100 | Float | ℃ |  | 0 | 1
test | 515 | 1 | 1142 | 2 | 0 | BMS Comm Parameters 1 | Battery Temperature 101 | Float | ℃ |  | 0 | 1
test | 515 | 1 | 1144 | 2 | 0 | BMS Comm Parameters 1 | Battery Temperature 102 | Float | ℃ |  | 0 | 1
test | 515 | 1 | 1146 | 2 | 0 | BMS Comm Parameters 1 | Battery Temperature 103 | Float | ℃ |  | 0 | 1
test | 515 | 1 | 1148 | 2 | 0 | BMS Comm Parameters 1 | Battery Temperature 104 | Float | ℃ |  | 0 | 1
test | 515 | 1 | 1150 | 2 | 0 | BMS Comm Parameters 1 | Battery Temperature 105 | Float | ℃ |  | 0 | 1
test | 515 | 1 | 1152 | 2 | 0 | BMS Comm Parameters 1 | Battery Temperature 106 | Float | ℃ |  | 0 | 1
test | 515 | 1 | 1154 | 2 | 0 | BMS Comm Parameters 1 | Battery Temperature 107 | Float | ℃ |  | 0 | 1
test | 515 | 1 | 1156 | 2 | 0 | BMS Comm Parameters 1 | Battery Temperature 108 | Float | ℃ |  | 0 | 1
test | 515 | 1 | 1158 | 2 | 0 | BMS Comm Parameters 1 | Battery Temperature 109 | Float | ℃ |  | 0 | 1
test | 515 | 1 | 1160 | 2 | 0 | BMS Comm Parameters 1 | Battery Temperature 110 | Float | ℃ |  | 0 | 1
test | 515 | 1 | 1162 | 2 | 0 | BMS Comm Parameters 1 | Battery Temperature 111 | Float | ℃ |  | 0 | 1
test | 515 | 1 | 1164 | 2 | 0 | BMS Comm Parameters 1 | Battery Temperature 112 | Float | ℃ |  | 0 | 1
test | 515 | 1 | 1166 | 2 | 0 | BMS Comm Parameters 1 | Battery Temperature 113 | Float | ℃ |  | 0 | 1
test | 515 | 1 | 1168 | 2 | 0 | BMS Comm Parameters 1 | Battery Temperature 114 | Float | ℃ |  | 0 | 1
test | 515 | 1 | 1170 | 2 | 0 | BMS Comm Parameters 1 | Battery Temperature 115 | Float | ℃ |  | 0 | 1
test | 515 | 1 | 1172 | 2 | 0 | BMS Comm Parameters 1 | Battery Temperature 116 | Float | ℃ |  | 0 | 1
test | 515 | 1 | 1174 | 2 | 0 | BMS Comm Parameters 1 | Battery Temperature 117 | Float | ℃ |  | 0 | 1
test | 515 | 1 | 1176 | 2 | 0 | BMS Comm Parameters 1 | Battery Temperature 118 | Float | ℃ |  | 0 | 1
test | 515 | 1 | 1178 | 2 | 0 | BMS Comm Parameters 1 | Battery Temperature 119 | Float | ℃ |  | 0 | 1
test | 515 | 1 | 1180 | 2 | 0 | BMS Comm Parameters 1 | Battery Temperature 120 | Float | ℃ |  | 0 | 1
test | 515 | 1 | 1182 | 2 | 0 | BMS Comm Parameters 1 | Battery Temperature 121 | Float | ℃ |  | 0 | 1
test | 515 | 1 | 1184 | 2 | 0 | BMS Comm Parameters 1 | Battery Temperature 122 | Float | ℃ |  | 0 | 1
test | 515 | 1 | 1186 | 2 | 0 | BMS Comm Parameters 1 | Battery Temperature 123 | Float | ℃ |  | 0 | 1
test | 515 | 1 | 1188 | 2 | 0 | BMS Comm Parameters 1 | Battery Temperature 124 | Float | ℃ |  | 0 | 1
test | 515 | 1 | 1190 | 2 | 0 | BMS Comm Parameters 1 | Battery Temperature 125 | Float | ℃ |  | 0 | 1
test | 515 | 1 | 1192 | 2 | 0 | BMS Comm Parameters 1 | Battery Temperature 126 | Float | ℃ |  | 0 | 1
test | 515 | 1 | 1194 | 2 | 0 | BMS Comm Parameters 1 | Battery Temperature 127 | Float | ℃ |  | 0 | 1
test | 515 | 1 | 1196 | 2 | 0 | BMS Comm Parameters 1 | Battery Temperature 128 | Float | ℃ |  | 0 | 1
test | 515 | 1 | 1198 | 2 | 0 | BMS Comm Parameters 1 | Battery Temperature 129 | Float | ℃ |  | 0 | 1
test | 515 | 1 | 1200 | 2 | 0 | BMS Comm Parameters 1 | Battery Temperature 130 | Float | ℃ |  | 0 | 1
test | 515 | 1 | 1202 | 2 | 0 | BMS Comm Parameters 1 | Battery Temperature 131 | Float | ℃ |  | 0 | 1
test | 515 | 1 | 1204 | 2 | 0 | BMS Comm Parameters 1 | Battery Temperature 132 | Float | ℃ |  | 0 | 1
test | 515 | 1 | 1206 | 2 | 0 | BMS Comm Parameters 1 | Battery Temperature 133 | Float | ℃ |  | 0 | 1
test | 515 | 1 | 1208 | 2 | 0 | BMS Comm Parameters 1 | Battery Temperature 134 | Float | ℃ |  | 0 | 1
test | 515 | 1 | 1210 | 2 | 0 | BMS Comm Parameters 1 | Battery Temperature 135 | Float | ℃ |  | 0 | 1
test | 515 | 1 | 1212 | 2 | 0 | BMS Comm Parameters 1 | Battery Temperature 136 | Float | ℃ |  | 0 | 1
test | 515 | 1 | 1214 | 2 | 0 | BMS Comm Parameters 1 | Battery Temperature 137 | Float | ℃ |  | 0 | 1
test | 515 | 1 | 1216 | 2 | 0 | BMS Comm Parameters 1 | Battery Temperature 138 | Float | ℃ |  | 0 | 1
test | 515 | 1 | 1218 | 2 | 0 | BMS Comm Parameters 1 | Battery Temperature 139 | Float | ℃ |  | 0 | 1
test | 515 | 1 | 1220 | 2 | 0 | BMS Comm Parameters 1 | Battery Temperature 140 | Float | ℃ |  | 0 | 1
test | 515 | 1 | 1222 | 2 | 0 | BMS Comm Parameters 1 | Battery Temperature 141 | Float | ℃ |  | 0 | 1
test | 515 | 1 | 1224 | 2 | 0 | BMS Comm Parameters 1 | Battery Temperature 142 | Float | ℃ |  | 0 | 1
test | 515 | 1 | 1226 | 2 | 0 | BMS Comm Parameters 1 | Battery Temperature 143 | Float | ℃ |  | 0 | 1
test | 515 | 1 | 1228 | 2 | 0 | BMS Comm Parameters 1 | Battery Temperature 144 | Float | ℃ |  | 0 | 1
test | 515 | 1 | 1230 | 2 | 0 | BMS Comm Parameters 1 | Battery Temperature 145 | Float | ℃ |  | 0 | 1
test | 515 | 1 | 1232 | 2 | 0 | BMS Comm Parameters 1 | Battery Temperature 146 | Float | ℃ |  | 0 | 1
test | 515 | 1 | 1234 | 2 | 0 | BMS Comm Parameters 1 | Battery Temperature 147 | Float | ℃ |  | 0 | 1
test | 515 | 1 | 1236 | 2 | 0 | BMS Comm Parameters 1 | Battery Temperature 148 | Float | ℃ |  | 0 | 1
test | 515 | 1 | 1238 | 2 | 0 | BMS Comm Parameters 1 | Battery Temperature 149 | Float | ℃ |  | 0 | 1
test | 515 | 1 | 1240 | 2 | 0 | BMS Comm Parameters 1 | Battery Temperature 150 | Float | ℃ |  | 0 | 1
test | 515 | 1 | 1242 | 2 | 0 | BMS Comm Parameters 1 | Battery Temperature 151 | Float | ℃ |  | 0 | 1
test | 515 | 1 | 1244 | 2 | 0 | BMS Comm Parameters 1 | Battery Temperature 152 | Float | ℃ |  | 0 | 1
test | 515 | 1 | 1246 | 2 | 0 | BMS Comm Parameters 1 | Battery Temperature 153 | Float | ℃ |  | 0 | 1
test | 515 | 1 | 1248 | 2 | 0 | BMS Comm Parameters 1 | Battery Temperature 154 | Float | ℃ |  | 0 | 1
test | 515 | 1 | 1250 | 2 | 0 | BMS Comm Parameters 1 | Battery Temperature 155 | Float | ℃ |  | 0 | 1
test | 515 | 1 | 1252 | 2 | 0 | BMS Comm Parameters 1 | Battery Temperature 156 | Float | ℃ |  | 0 | 1
test | 515 | 1 | 1254 | 2 | 0 | BMS Comm Parameters 1 | Battery Temperature 157 | Float | ℃ |  | 0 | 1
test | 515 | 1 | 1256 | 2 | 0 | BMS Comm Parameters 1 | Battery Temperature 158 | Float | ℃ |  | 0 | 1
test | 515 | 1 | 1258 | 2 | 0 | BMS Comm Parameters 1 | Battery Temperature 159 | Float | ℃ |  | 0 | 1
test | 515 | 1 | 1260 | 2 | 0 | BMS Comm Parameters 1 | Battery Temperature 160 | Float | ℃ |  | 0 | 1
test | 515 | 1 | 1262 | 2 | 0 | BMS Comm Parameters 1 | Rack Cell Overvoltage Level 3 Alarm Threshold (Warning) | Float | mV |  | 0 | 1
test | 515 | 1 | 1264 | 2 | 0 | BMS Comm Parameters 1 | Rack Cell Overvoltage Level 3 Recovery Threshold (Warning) | Float | mV |  | 0 | 1
test | 515 | 1 | 1266 | 2 | 0 | BMS Comm Parameters 1 | Rack Cell Undervoltage Level 3 Alarm Threshold (Warning) | Float | mV |  | 0 | 1
test | 515 | 1 | 1268 | 2 | 0 | BMS Comm Parameters 1 | Rack Cell Undervoltage Level 3 Recovery Threshold (Warning) | Float | mV |  | 0 | 1
test | 515 | 1 | 1270 | 2 | 0 | BMS Comm Parameters 1 | Rack Total Voltage Overvoltage Level 3 Alarm Threshold (Warning) | Float | V |  | 0 | 1
test | 515 | 1 | 1272 | 2 | 0 | BMS Comm Parameters 1 | Rack Total Voltage Overvoltage Level 3 Recovery Threshold (Warning) | Float | V |  | 0 | 1
test | 515 | 1 | 1274 | 2 | 0 | BMS Comm Parameters 1 | Rack Total Voltage Undervoltage Level 3 Alarm Threshold (Warning) | Float | V |  | 0 | 1
test | 515 | 1 | 1276 | 2 | 0 | BMS Comm Parameters 1 | Rack Total Voltage Undervoltage Level 3 Recovery Threshold (Warning) | Float | V |  | 0 | 1
test | 515 | 1 | 1278 | 2 | 0 | BMS Comm Parameters 1 | Rack Charge Overcurrent Level 3 Alarm Threshold (Warning) | Float | A |  | 0 | 1
test | 515 | 1 | 1280 | 2 | 0 | BMS Comm Parameters 1 | Rack Charge Overcurrent Level 3 Recovery Threshold (Warning) | Float | A |  | 0 | 1
test | 515 | 1 | 1282 | 2 | 0 | BMS Comm Parameters 1 | Rack Discharge Overcurrent Level 3 Alarm Threshold (Warning) | Float | A |  | 0 | 1
test | 515 | 1 | 1284 | 2 | 0 | BMS Comm Parameters 1 | Rack Discharge Overcurrent Level 3 Recovery Threshold (Warning) | Float | A |  | 0 | 1
test | 515 | 1 | 1286 | 2 | 0 | BMS Comm Parameters 1 | Rack Charge Over-Temperature Level 3 Alarm Threshold (Warning) | Float | ℃ |  | 0 | 1
test | 515 | 1 | 1288 | 2 | 0 | BMS Comm Parameters 1 | Rack Charge Over-Temperature Level 3 Recovery Threshold (Warning) | Float | ℃ |  | 0 | 1
test | 515 | 1 | 1290 | 2 | 0 | BMS Comm Parameters 1 | Rack Charge Under-Temperature Level 3 Alarm Threshold (Warning) | Float | ℃ |  | 0 | 1
test | 515 | 1 | 1292 | 2 | 0 | BMS Comm Parameters 1 | Rack Charge Under-Temperature Level 3 Recovery Threshold (Warning) | Float | ℃ |  | 0 | 1
test | 515 | 1 | 1294 | 2 | 0 | BMS Comm Parameters 1 | Rack SOC Too Low Level 3 Alarm Threshold (Warning) | Float | % |  | 0 | 1
test | 515 | 1 | 1296 | 2 | 0 | BMS Comm Parameters 1 | Rack SOC Too Low Level 3 Recovery Threshold (Warning) | Float | % |  | 0 | 1
test | 515 | 1 | 1298 | 2 | 0 | BMS Comm Parameters 1 | Rack Pole Over-Temperature Level 3 Alarm Threshold (Warning) | Float | ℃ |  | 0 | 1
test | 515 | 1 | 1300 | 2 | 0 | BMS Comm Parameters 1 | Rack Pole Over-Temperature Level 3 Recovery Threshold (Warning) | Float | ℃ |  | 0 | 1
test | 515 | 1 | 1302 | 2 | 0 | BMS Comm Parameters 1 | Rack Insulation Failure Level 3 Alarm Threshold (Warning) | Float | Ω/V |  | 0 | 1
test | 515 | 1 | 1304 | 2 | 0 | BMS Comm Parameters 1 | Rack Insulation Failure Level 3 Recovery Threshold (Warning) | Float | Ω/V |  | 0 | 1
test | 515 | 1 | 1306 | 2 | 0 | BMS Comm Parameters 1 | Rack Cell Voltage Difference Too High Level 3 Alarm Threshold (Warning) | Float | mV |  | 0 | 1
test | 515 | 1 | 1308 | 2 | 0 | BMS Comm Parameters 1 | Rack Cell Voltage Difference Too High Level 3 Recovery Threshold (Warning) | Float | mV |  | 0 | 1
test | 515 | 1 | 1310 | 2 | 0 | BMS Comm Parameters 1 | Rack Total Voltage Difference Too High Level 3 Alarm Threshold (Warning) | Float | V |  | 0 | 1
test | 515 | 1 | 1312 | 2 | 0 | BMS Comm Parameters 1 | Rack Total Voltage Difference Too High Level 3 Recovery Threshold (Warning) | Float | V |  | 0 | 1
test | 515 | 1 | 1314 | 2 | 0 | BMS Comm Parameters 1 | Rack Discharge Over-Temperature Level 3 Alarm Threshold (Warning) | Float | ℃ |  | 0 | 1
test | 515 | 1 | 1316 | 2 | 0 | BMS Comm Parameters 1 | Rack Discharge Over-Temperature Level 3 Recovery Threshold (Warning) | Float | ℃ |  | 0 | 1
test | 515 | 1 | 1318 | 2 | 0 | BMS Comm Parameters 1 | Rack Discharge Under-Temperature Level 3 Alarm Threshold (Warning) | Float | ℃ |  | 0 | 1
test | 515 | 1 | 1320 | 2 | 0 | BMS Comm Parameters 1 | Rack Discharge Under-Temperature Level 3 Recovery Threshold (Warning) | Float | ℃ |  | 0 | 1
test | 515 | 1 | 1322 | 2 | 0 | BMS Comm Parameters 1 | Rack Temperature Difference Too High Level 3 Alarm Threshold (Warning) | Float | ℃ |  | 0 | 1
test | 515 | 1 | 1324 | 2 | 0 | BMS Comm Parameters 1 | Rack Temperature Difference Too High Level 3 Recovery Threshold (Warning) | Float | ℃ |  | 0 | 1
test | 515 | 1 | 1326 | 2 | 0 | BMS Comm Parameters 1 | Rack HV Box Connector Over-Temperature Level 3 Alarm Threshold (Warning) | Float | ℃ |  | 0 | 1
test | 515 | 1 | 1328 | 2 | 0 | BMS Comm Parameters 1 | Rack HV Box Connector Over-Temperature Level 3 Recovery Threshold (Warning) | Float | ℃ |  | 0 | 1
test | 515 | 1 | 1330 | 2 | 0 | BMS Comm Parameters 1 | Rack Cell Overvoltage Level 2 Alarm Threshold | Float | mV |  | 0 | 1
test | 515 | 1 | 1332 | 2 | 0 | BMS Comm Parameters 1 | Rack Cell Overvoltage Level 2 Recovery Threshold | Float | mV |  | 0 | 1
test | 515 | 1 | 1334 | 2 | 0 | BMS Comm Parameters 1 | Rack Cell Undervoltage Level 2 Alarm Threshold | Float | mV |  | 0 | 1
test | 515 | 1 | 1336 | 2 | 0 | BMS Comm Parameters 1 | Rack Cell Undervoltage Level 2 Recovery Threshold | Float | mV |  | 0 | 1
test | 515 | 1 | 1338 | 2 | 0 | BMS Comm Parameters 1 | Rack Total Voltage Overvoltage Level 2 Alarm Threshold | Float | V |  | 0 | 1
test | 515 | 1 | 1340 | 2 | 0 | BMS Comm Parameters 1 | Rack Total Voltage Overvoltage Level 2 Recovery Threshold | Float | V |  | 0 | 1
test | 515 | 1 | 1342 | 2 | 0 | BMS Comm Parameters 1 | Rack Total Voltage Undervoltage Level 2 Alarm Threshold | Float | V |  | 0 | 1
test | 515 | 1 | 1344 | 2 | 0 | BMS Comm Parameters 1 | Rack Total Voltage Undervoltage Level 2 Recovery Threshold | Float | V |  | 0 | 1
test | 515 | 1 | 1346 | 2 | 0 | BMS Comm Parameters 1 | Rack Charge Overcurrent Level 2 Alarm Threshold | Float | A |  | 0 | 1
test | 515 | 1 | 1348 | 2 | 0 | BMS Comm Parameters 1 | Rack Charge Overcurrent Level 2 Recovery Threshold | Float | A |  | 0 | 1
test | 515 | 1 | 1350 | 2 | 0 | BMS Comm Parameters 1 | Rack Discharge Overcurrent Level 2 Alarm Threshold | Float | A |  | 0 | 1
test | 515 | 1 | 1352 | 2 | 0 | BMS Comm Parameters 1 | Rack Discharge Overcurrent Level 2 Recovery Threshold | Float | A |  | 0 | 1
test | 515 | 1 | 1354 | 2 | 0 | BMS Comm Parameters 1 | Rack Charge Over-Temperature Level 2 Alarm Threshold | Float | ℃ |  | 0 | 1
test | 515 | 1 | 1356 | 2 | 0 | BMS Comm Parameters 1 | Rack Charge Over-Temperature Level 2 Recovery Threshold | Float | ℃ |  | 0 | 1
test | 515 | 1 | 1358 | 2 | 0 | BMS Comm Parameters 1 | Rack Charge Under-Temperature Level 2 Alarm Threshold | Float | ℃ |  | 0 | 1
test | 515 | 1 | 1360 | 2 | 0 | BMS Comm Parameters 1 | Rack Charge Under-Temperature Level 2 Recovery Threshold | Float | ℃ |  | 0 | 1
test | 515 | 1 | 1362 | 2 | 0 | BMS Comm Parameters 1 | Rack SOC Too Low Level 2 Alarm Threshold | Float | % |  | 0 | 1
test | 515 | 1 | 1364 | 2 | 0 | BMS Comm Parameters 1 | Rack SOC Too Low Level 2 Recovery Threshold | Float | % |  | 0 | 1
test | 515 | 1 | 1366 | 2 | 0 | BMS Comm Parameters 1 | Rack Pole Over-Temperature Level 2 Alarm Threshold | Float | ℃ |  | 0 | 1
test | 515 | 1 | 1368 | 2 | 0 | BMS Comm Parameters 1 | Rack Pole Over-Temperature Level 2 Recovery Threshold | Float | ℃ |  | 0 | 1
test | 515 | 1 | 1370 | 2 | 0 | BMS Comm Parameters 1 | Rack Insulation Failure Level 2 Alarm Threshold | Float | Ω/V |  | 0 | 1
test | 515 | 1 | 1372 | 2 | 0 | BMS Comm Parameters 1 | Rack Insulation Failure Level 2 Recovery Threshold | Float | Ω/V |  | 0 | 1
test | 515 | 1 | 1374 | 2 | 0 | BMS Comm Parameters 1 | Rack Cell Voltage Difference Too High Level 2 Alarm Threshold | Float | mV |  | 0 | 1
test | 515 | 1 | 1376 | 2 | 0 | BMS Comm Parameters 1 | Rack Cell Voltage Difference Too High Level 2 Recovery Threshold | Float | mV |  | 0 | 1
test | 515 | 1 | 1378 | 2 | 0 | BMS Comm Parameters 1 | Rack Total Voltage Difference Too High Level 2 Alarm Threshold | Float | V |  | 0 | 1
test | 515 | 1 | 1380 | 2 | 0 | BMS Comm Parameters 1 | Rack Total Voltage Difference Too High Level 2 Recovery Threshold | Float | V |  | 0 | 1
test | 515 | 1 | 1382 | 2 | 0 | BMS Comm Parameters 1 | Rack Discharge Over-Temperature Level 2 Alarm Threshold | Float | ℃ |  | 0 | 1
test | 515 | 1 | 1384 | 2 | 0 | BMS Comm Parameters 1 | Rack Discharge Over-Temperature Level 2 Recovery Threshold | Float | ℃ |  | 0 | 1
test | 515 | 1 | 1386 | 2 | 0 | BMS Comm Parameters 1 | Rack Discharge Under-Temperature Level 2 Alarm Threshold | Float | ℃ |  | 0 | 1
test | 515 | 1 | 1388 | 2 | 0 | BMS Comm Parameters 1 | Rack Discharge Under-Temperature Level 2 Recovery Threshold | Float | ℃ |  | 0 | 1
test | 515 | 1 | 1390 | 2 | 0 | BMS Comm Parameters 1 | Rack Temperature Difference Too High Level 2 Alarm Threshold | Float | ℃ |  | 0 | 1
test | 515 | 1 | 1392 | 2 | 0 | BMS Comm Parameters 1 | Rack Temperature Difference Too High Level 2 Recovery Threshold | Float | ℃ |  | 0 | 1
test | 515 | 1 | 1394 | 2 | 0 | BMS Comm Parameters 1 | Rack HV Box Connector Over-Temperature Level 2 Alarm Threshold | Float | ℃ |  | 0 | 1
test | 515 | 1 | 1396 | 2 | 0 | BMS Comm Parameters 1 | Rack HV Box Connector Over-Temperature Level 2 Recovery Threshold | Float | ℃ |  | 0 | 1
test | 515 | 1 | 1398 | 2 | 0 | BMS Comm Parameters 1 | Rack Cell Overvoltage Level 1 Alarm Threshold (Critical) | Float | mV |  | 0 | 1
test | 515 | 1 | 1400 | 2 | 0 | BMS Comm Parameters 1 | Rack Cell Overvoltage Level 1 Recovery Threshold (Critical) | Float | mV |  | 0 | 1
test | 515 | 1 | 1402 | 2 | 0 | BMS Comm Parameters 1 | Rack Cell Undervoltage Level 1 Alarm Threshold (Critical) | Float | mV |  | 0 | 1
test | 515 | 1 | 1404 | 2 | 0 | BMS Comm Parameters 1 | Rack Cell Undervoltage Level 1 Recovery Threshold (Critical) | Float | mV |  | 0 | 1
test | 515 | 1 | 1406 | 2 | 0 | BMS Comm Parameters 1 | Rack Total Voltage Overvoltage Level 1 Alarm Threshold (Critical) | Float | V |  | 0 | 1
test | 515 | 1 | 1408 | 2 | 0 | BMS Comm Parameters 1 | Rack Total Voltage Overvoltage Level 1 Recovery Threshold (Critical) | Float | V |  | 0 | 1
test | 515 | 1 | 1410 | 2 | 0 | BMS Comm Parameters 1 | Rack Total Voltage Undervoltage Level 1 Alarm Threshold (Critical) | Float | V |  | 0 | 1
test | 515 | 1 | 1412 | 2 | 0 | BMS Comm Parameters 1 | Rack Total Voltage Undervoltage Level 1 Recovery Threshold (Critical) | Float | V |  | 0 | 1
test | 515 | 1 | 1414 | 2 | 0 | BMS Comm Parameters 1 | Rack Charge Overcurrent Level 1 Alarm Threshold (Critical) | Float | A |  | 0 | 1
test | 515 | 1 | 1416 | 2 | 0 | BMS Comm Parameters 1 | Rack Charge Overcurrent Level 1 Recovery Threshold (Critical) | Float | A |  | 0 | 1
test | 515 | 1 | 1418 | 2 | 0 | BMS Comm Parameters 1 | Rack Discharge Overcurrent Level 1 Alarm Threshold (Critical) | Float | A |  | 0 | 1
test | 515 | 1 | 1420 | 2 | 0 | BMS Comm Parameters 1 | Rack Discharge Overcurrent Level 1 Recovery Threshold (Critical) | Float | A |  | 0 | 1
test | 515 | 1 | 1422 | 2 | 0 | BMS Comm Parameters 1 | Rack Charge Over-Temperature Level 1 Alarm Threshold (Critical) | Float | ℃ |  | 0 | 1
test | 515 | 1 | 1424 | 2 | 0 | BMS Comm Parameters 1 | Rack Charge Over-Temperature Level 1 Recovery Threshold (Critical) | Float | ℃ |  | 0 | 1
test | 515 | 1 | 1426 | 2 | 0 | BMS Comm Parameters 1 | Rack Charge Under-Temperature Level 1 Alarm Threshold (Critical) | Float | ℃ |  | 0 | 1
test | 515 | 1 | 1428 | 2 | 0 | BMS Comm Parameters 1 | Rack Charge Under-Temperature Level 1 Recovery Threshold (Critical) | Float | ℃ |  | 0 | 1
test | 515 | 1 | 1430 | 2 | 0 | BMS Comm Parameters 1 | Rack SOC Too Low Level 1 Alarm Threshold (Critical) | Float | % |  | 0 | 1
test | 515 | 1 | 1432 | 2 | 0 | BMS Comm Parameters 1 | Rack SOC Too Low Level 1 Recovery Threshold (Critical) | Float | % |  | 0 | 1
test | 515 | 1 | 1434 | 2 | 0 | BMS Comm Parameters 1 | Rack Pole Over-Temperature Level 1 Alarm Threshold (Critical) | Float | ℃ |  | 0 | 1
test | 515 | 1 | 1436 | 2 | 0 | BMS Comm Parameters 1 | Rack Pole Over-Temperature Level 1 Recovery Threshold (Critical) | Float | ℃ |  | 0 | 1
test | 515 | 1 | 1438 | 2 | 0 | BMS Comm Parameters 1 | Rack Insulation Failure Level 1 Alarm Threshold (Critical) | Float | Ω/V |  | 0 | 1
test | 515 | 1 | 1440 | 2 | 0 | BMS Comm Parameters 1 | Rack Insulation Failure Level 1 Recovery Threshold (Critical) | Float | Ω/V |  | 0 | 1
test | 515 | 1 | 1442 | 2 | 0 | BMS Comm Parameters 1 | Rack Cell Voltage Difference Too High Level 1 Alarm Threshold (Critical) | Float | mV |  | 0 | 1
test | 515 | 1 | 1444 | 2 | 0 | BMS Comm Parameters 1 | Rack Cell Voltage Difference Too High Level 1 Recovery Threshold (Critical) | Float | mV |  | 0 | 1
test | 515 | 1 | 1446 | 2 | 0 | BMS Comm Parameters 1 | Rack Total Voltage Difference Too High Level 1 Alarm Threshold (Critical) | Float | V |  | 0 | 1
test | 515 | 1 | 1448 | 2 | 0 | BMS Comm Parameters 1 | Rack Total Voltage Difference Too High Level 1 Recovery Threshold (Critical) | Float | V |  | 0 | 1
test | 515 | 1 | 1450 | 2 | 0 | BMS Comm Parameters 1 | Rack Discharge Over-Temperature Level 1 Alarm Threshold (Critical) | Float | ℃ |  | 0 | 1
test | 515 | 1 | 1452 | 2 | 0 | BMS Comm Parameters 1 | Rack Discharge Over-Temperature Level 1 Recovery Threshold (Critical) | Float | ℃ |  | 0 | 1
test | 515 | 1 | 1454 | 2 | 0 | BMS Comm Parameters 1 | Rack Discharge Under-Temperature Level 1 Alarm Threshold (Critical) | Float | ℃ |  | 0 | 1
test | 515 | 1 | 1456 | 2 | 0 | BMS Comm Parameters 1 | Rack Discharge Under-Temperature Level 1 Recovery Threshold (Critical) | Float | ℃ |  | 0 | 1
test | 515 | 1 | 1458 | 2 | 0 | BMS Comm Parameters 1 | Rack Temperature Difference Too High Level 1 Alarm Threshold (Critical) | Float | ℃ |  | 0 | 1
test | 515 | 1 | 1460 | 2 | 0 | BMS Comm Parameters 1 | Rack Temperature Difference Too High Level 1 Recovery Threshold (Critical) | Float | ℃ |  | 0 | 1
test | 515 | 1 | 1462 | 2 | 0 | BMS Comm Parameters 1 | Rack HV Box Connector Over-Temperature Level 1 Alarm Threshold (Critical) | Float | ℃ |  | 0 | 1
test | 515 | 1 | 1464 | 2 | 0 | BMS Comm Parameters 1 | Rack HV Box Connector Over-Temperature Level 1 Recovery Threshold (Critical) | Float | ℃ |  | 0 | 1
test | 515 | 1 | 1466 | 2 | 0 | BMS Comm Parameters 1 | Rack Module Voltage Difference Too High Alarm Level 1 Threshold | Float | V |  | 0 | 1
test | 515 | 1 | 1468 | 2 | 0 | BMS Comm Parameters 1 | Rack Module Voltage Difference Too High Alarm Level 2 Threshold | Float | V |  | 0 | 1
test | 515 | 1 | 1470 | 2 | 0 | BMS Comm Parameters 1 | Rack Module Voltage Difference Too High Alarm Level 3 Threshold | Float | V |  | 0 | 1
test | 515 | 1 | 1472 | 2 | 0 | BMS Comm Parameters 1 | Rack Module Voltage Difference Too High Alarm Level 1 Recovery Threshold | Float | V |  | 0 | 1
test | 515 | 1 | 1474 | 2 | 0 | BMS Comm Parameters 1 | Rack Module Voltage Difference Too High Alarm Level 2 Recovery Threshold | Float | V |  | 0 | 1
test | 515 | 1 | 1476 | 2 | 0 | BMS Comm Parameters 1 | Rack Module Voltage Difference Too High Alarm Level 3 Recovery Threshold | Float | V |  | 0 | 1
test | 515 | 1 | 1478 | 2 | 0 | BMS Comm Parameters 1 | BCU Time | Float |  |  | 0 | 1
test | 515 | 1 | 1480 | 2 | 0 | BMS Comm Parameters 1 | Precharge End Voltage Diff | Float | V |  | 0 | 1
test | 515 | 1 | 1482 | 2 | 0 | BMS Comm Parameters 1 | Fan On Temperature | Float | ℃ |  | 0 | 1
test | 515 | 1 | 1484 | 2 | 0 | BMS Comm Parameters 1 | Fan Off Temperature | Float | ℃ |  | 0 | 1
test | 515 | 1 | 1486 | 2 | 0 | BMS Comm Parameters 1 | Max Cell Voltage | Float | mV |  | 0 | 1
test | 515 | 1 | 1488 | 2 | 0 | BMS Comm Parameters 1 | Max Cell Voltage No. | Float |  |  | 0 | 1
test | 515 | 1 | 1490 | 2 | 0 | BMS Comm Parameters 1 | Module No. of Max Cell Voltage | Float |  |  | 0 | 1
test | 515 | 1 | 1492 | 2 | 0 | BMS Comm Parameters 1 | Cell No. of Max Voltage in Module | Float |  |  | 0 | 1
test | 515 | 1 | 1494 | 2 | 0 | BMS Comm Parameters 1 | Min Cell Voltage | Float | mV |  | 0 | 1
test | 515 | 1 | 1496 | 2 | 0 | BMS Comm Parameters 1 | Min Cell Voltage No. | Float |  |  | 0 | 1
test | 515 | 1 | 1498 | 2 | 0 | BMS Comm Parameters 1 | Module No. of Min Cell Voltage | Float |  |  | 0 | 1
test | 515 | 1 | 1500 | 2 | 0 | BMS Comm Parameters 1 | Cell No. of Min Voltage in Module | Float |  |  | 0 | 1
test | 515 | 1 | 1502 | 2 | 0 | BMS Comm Parameters 1 | Max-Min Cell Voltage Diff | Float | mV |  | 0 | 1
test | 515 | 1 | 1504 | 2 | 0 | BMS Comm Parameters 1 | Average Cell Voltage | Float | mV |  | 0 | 1
test | 515 | 1 | 1506 | 2 | 0 | BMS Comm Parameters 1 | Max Battery Temperature | Float | ℃ |  | 0 | 1
test | 515 | 1 | 1508 | 2 | 0 | BMS Comm Parameters 1 | Max Battery Temperature No. | Float |  |  | 0 | 1
test | 515 | 1 | 1510 | 2 | 0 | BMS Comm Parameters 1 | Slave No. of Max Temperature | Float |  |  | 0 | 1
test | 515 | 1 | 1512 | 2 | 0 | BMS Comm Parameters 1 | Temp No. of Max Temperature in Module | Float |  |  | 0 | 1
test | 515 | 1 | 1514 | 2 | 0 | BMS Comm Parameters 1 | Min Battery Temperature | Float | ℃ |  | 0 | 1
test | 515 | 1 | 1516 | 2 | 0 | BMS Comm Parameters 1 | Min Battery Temperature No. | Float |  |  | 0 | 1
test | 515 | 1 | 1518 | 2 | 0 | BMS Comm Parameters 1 | Module No. of Min Temperature | Float |  |  | 0 | 1
test | 515 | 1 | 1520 | 2 | 0 | BMS Comm Parameters 1 | Temp No. of Min Temperature in Module | Float |  |  | 0 | 1
test | 515 | 1 | 1522 | 2 | 0 | BMS Comm Parameters 1 | Average Temperature | Float | ℃ |  | 0 | 1
test | 515 | 1 | 1524 | 2 | 0 | BMS Comm Parameters 1 | Max Pole Temperature | Float | ℃ |  | 0 | 1
test | 515 | 1 | 1526 | 2 | 0 | BMS Comm Parameters 1 | Module No. of Max Pole Temperature | Float |  |  | 0 | 1
test | 515 | 1 | 1528 | 2 | 0 | BMS Comm Parameters 1 | Max Acceptable Charge Current | Float | A |  | 0 | 1
test | 515 | 1 | 1530 | 2 | 0 | BMS Comm Parameters 1 | Max Acceptable Discharge Current | Float | A |  | 0 | 1
test | 515 | 1 | 1532 | 2 | 0 | BMS Comm Parameters 1 | Display SOC | Float | ％ |  | 0 | 1
test | 515 | 1 | 1534 | 2 | 0 | BMS Comm Parameters 1 | SOH | Float | ％ |  | 0 | 1
test | 515 | 1 | 1536 | 2 | 0 | BMS Comm Parameters 1 | Max Battery Temperature Diff | Float | ℃ |  | 0 | 1
test | 515 | 1 | 1538 | 2 | 0 | BMS Comm Parameters 1 | Cluster Max Cell Temp Rise | Float | ℃ |  | 0 | 1
test | 515 | 1 | 1540 | 2 | 0 | BMS Comm Parameters 1 | Battery Pack No. of Cluster Max Cell Temp Rise | Float |  |  | 0 | 1
test | 515 | 1 | 1542 | 2 | 0 | BMS Comm Parameters 1 | Cell Temp No. of Cluster Max Cell Temp Rise in Pack | Float |  |  | 0 | 1
test | 515 | 1 | 1544 | 2 | 0 | BMS Comm Parameters 1 | Cell No. of Cluster Max Cell Temp Rise Among All Cells | Float |  |  | 0 | 1
test | 515 | 1 | 1546 | 2 | 0 | BMS Comm Parameters 1 | Cluster Internal SOC | Float | ％ |  | 0 | 1
test | 515 | 1 | 1548 | 2 | 0 | BMS Comm Parameters 1 | Precharge Total Voltage | Float | V |  | 0 | 1
test | 515 | 1 | 1550 | 2 | 0 | BMS Comm Parameters 1 | Summed Cell Total Voltage | Float | V |  | 0 | 1
test | 515 | 1 | 1552 | 2 | 0 | BMS Comm Parameters 1 | Cluster Total Voltage (Acquired) | Float | V |  | 0 | 1
test | 515 | 1 | 1554 | 2 | 0 | BMS Comm Parameters 1 | Cluster Total Current | Float | A |  | 0 | 1
test | 515 | 1 | 1556 | 2 | 0 | BMS Comm Parameters 1 | K_Total Voltage | Float | V |  | 0 | 1
test | 515 | 1 | 1558 | 2 | 0 | BMS Comm Parameters 1 | Shunt Sampling Current | Float | A |  | 0 | 1
test | 515 | 1 | 1560 | 2 | 0 | BMS Comm Parameters 1 | CAN Hall Sampling Current | Float | A |  | 0 | 1
test | 515 | 1 | 1562 | 2 | 0 | BMS Comm Parameters 1 | Current/Voltage Hall Sampling Current | Float | A |  | 0 | 1
test | 515 | 1 | 1564 | 2 | 0 | BMS Comm Parameters 1 | Insulation Resistance | Float | kΩ |  | 0 | 1
test | 515 | 1 | 1566 | 2 | 0 | BMS Comm Parameters 1 | Positive Terminal Insulation Resistance | Float | kΩ |  | 0 | 1
test | 515 | 1 | 1568 | 2 | 0 | BMS Comm Parameters 1 | Negative Terminal Insulation Resistance | Float | kΩ |  | 0 | 1
test | 515 | 1 | 1570 | 2 | 0 | BMS Comm Parameters 1 | Power Supply Sampling Voltage | Float | mV |  | 0 | 1
test | 515 | 1 | 1572 | 2 | 0 | BMS Comm Parameters 1 | HV Box Max Temperature | Float | ℃ |  | 0 | 1
test | 515 | 1 | 1574 | 2 | 0 | BMS Comm Parameters 1 | HV Box Temperature 1 | Float | ℃ |  | 0 | 1
test | 515 | 1 | 1576 | 2 | 0 | BMS Comm Parameters 1 | HV Box Temperature 2 | Float | ℃ |  | 0 | 1
test | 515 | 1 | 1578 | 2 | 0 | BMS Comm Parameters 1 | HV Box Temperature 3 | Float | ℃ |  | 0 | 1
test | 515 | 1 | 1580 | 2 | 0 | BMS Comm Parameters 1 | HV Box Temperature 4 | Float | ℃ |  | 0 | 1
test | 515 | 1 | 1582 | 2 | 0 | BMS Comm Parameters 1 | Battery Cluster Internal Resistance | Float | mΩ |  | 0 | 1
test | 515 | 1 | 1584 | 2 | 0 | BMS Comm Parameters 1 | Monthly Cumulative Charge Energy | Float | kWh |  | 0 | 1
test | 515 | 1 | 1586 | 2 | 0 | BMS Comm Parameters 1 | Monthly Cumulative Discharge Energy | Float | kWh |  | 0 | 1
test | 515 | 1 | 1588 | 2 | 0 | BMS Comm Parameters 1 | Yearly Cumulative Charge Energy | Float | kWh |  | 0 | 1
test | 515 | 1 | 1590 | 2 | 0 | BMS Comm Parameters 1 | Yearly Cumulative Discharge Energy | Float | kWh |  | 0 | 1
test | 515 | 1 | 1592 | 2 | 0 | BMS Comm Parameters 1 | Total Cumulative Charge Capacity | Float | AH |  | 0 | 1
test | 515 | 1 | 1594 | 2 | 0 | BMS Comm Parameters 1 | Total Cumulative Discharge Capacity | Float | AH |  | 0 | 1
test | 515 | 1 | 1596 | 2 | 0 | BMS Comm Parameters 1 | Battery No. at Alarm Max Voltage | Float |  |  | 0 | 1
test | 515 | 1 | 1598 | 2 | 0 | BMS Comm Parameters 1 | Max Voltage at Alarm | Float | mV |  | 0 | 1
test | 515 | 1 | 1600 | 2 | 0 | BMS Comm Parameters 1 | Battery No. at Shutdown Max Voltage | Float |  |  | 0 | 1
test | 515 | 1 | 1602 | 2 | 0 | BMS Comm Parameters 1 | Max Voltage at Shutdown | Float | mV |  | 0 | 1
test | 515 | 1 | 1604 | 2 | 0 | BMS Comm Parameters 1 | Battery No. at Alarm Min Voltage | Float |  |  | 0 | 1
test | 515 | 1 | 1606 | 2 | 0 | BMS Comm Parameters 1 | Min Voltage at Alarm | Float | mV |  | 0 | 1
test | 515 | 1 | 1608 | 2 | 0 | BMS Comm Parameters 1 | Battery No. at Shutdown Min Voltage | Float |  |  | 0 | 1
test | 515 | 1 | 1610 | 2 | 0 | BMS Comm Parameters 1 | Min Voltage at Shutdown | Float | mV |  | 0 | 1
test | 515 | 1 | 1612 | 2 | 0 | BMS Comm Parameters 1 | Voltage at Battery Overvoltage Alarm | Float | V |  | 0 | 1
test | 515 | 1 | 1614 | 2 | 0 | BMS Comm Parameters 1 | Voltage at Battery Overvoltage Shutdown | Float | V |  | 0 | 1
test | 515 | 1 | 1616 | 2 | 0 | BMS Comm Parameters 1 | Voltage at Battery Undervoltage Alarm | Float | V |  | 0 | 1
test | 515 | 1 | 1618 | 2 | 0 | BMS Comm Parameters 1 | Voltage at Battery Undervoltage Shutdown | Float | V |  | 0 | 1
test | 515 | 1 | 1620 | 2 | 0 | BMS Comm Parameters 1 | Current at Charge Overcurrent Alarm | Float | A |  | 0 | 1
test | 515 | 1 | 1622 | 2 | 0 | BMS Comm Parameters 1 | Current at Charge Overcurrent Shutdown | Float | A |  | 0 | 1
test | 515 | 1 | 1624 | 2 | 0 | BMS Comm Parameters 1 | Current at Discharge Overcurrent Alarm | Float | A |  | 0 | 1
test | 515 | 1 | 1626 | 2 | 0 | BMS Comm Parameters 1 | Current at Discharge Overcurrent Shutdown | Float | A |  | 0 | 1
test | 515 | 1 | 1628 | 2 | 0 | BMS Comm Parameters 1 | Temp Point No. at Alarm Max Battery Temp | Float |  |  | 0 | 1
test | 515 | 1 | 1630 | 2 | 0 | BMS Comm Parameters 1 | Max Battery Temp at Alarm | Float | ℃ |  | 0 | 1
test | 515 | 1 | 1632 | 2 | 0 | BMS Comm Parameters 1 | Temp Point No. at Shutdown Max Battery Temp | Float |  |  | 0 | 1
test | 515 | 1 | 1634 | 2 | 0 | BMS Comm Parameters 1 | Max Battery Temp at Shutdown | Float | ℃ |  | 0 | 1
test | 515 | 1 | 1636 | 2 | 0 | BMS Comm Parameters 1 | Temp Point No. at Alarm Min Battery Temp | Float |  |  | 0 | 1
test | 515 | 1 | 1638 | 2 | 0 | BMS Comm Parameters 1 | Min Battery Temp at Alarm | Float | ℃ |  | 0 | 1
test | 515 | 1 | 1640 | 2 | 0 | BMS Comm Parameters 1 | Temp Point No. at Shutdown Min Battery Temp | Float |  |  | 0 | 1
test | 515 | 1 | 1642 | 2 | 0 | BMS Comm Parameters 1 | Min Battery Temp at Shutdown | Float | ℃ |  | 0 | 1
test | 515 | 1 | 1644 | 2 | 0 | BMS Comm Parameters 1 | HV Box Max Temp at Alarm | Float | ℃ |  | 0 | 1
test | 515 | 1 | 1646 | 2 | 0 | BMS Comm Parameters 1 | HV Box Max Temp at Shutdown | Float | ℃ |  | 0 | 1
test | 515 | 1 | 1648 | 2 | 0 | BMS Comm Parameters 1 | Battery No. at Temp Rise Alarm | Float |  |  | 0 | 1
test | 515 | 1 | 1650 | 2 | 0 | BMS Comm Parameters 1 | Temp Rise Value at Alarm | Float | ℃ |  | 0 | 1
test | 515 | 1 | 1652 | 2 | 0 | BMS Comm Parameters 1 | Battery No. at Temp Rise Shutdown | Float |  |  | 0 | 1
test | 515 | 1 | 1654 | 2 | 0 | BMS Comm Parameters 1 | Temp Rise Value at Shutdown | Float | ℃ |  | 0 | 1
test | 515 | 1 | 1656 | 2 | 0 | BMS Comm Parameters 1 | Max Power Temp Point No. at Alarm (Pole Temp) | Float |  |  | 0 | 1
test | 515 | 1 | 1658 | 2 | 0 | BMS Comm Parameters 1 | Max Power Temp Value at Alarm (Pole Temp) | Float | ℃ |  | 0 | 1
test | 515 | 1 | 1660 | 2 | 0 | BMS Comm Parameters 1 | Max Power Temp Point No. at Shutdown (Pole Temp) | Float |  |  | 0 | 1
test | 515 | 1 | 1662 | 2 | 0 | BMS Comm Parameters 1 | Max Power Temp Value at Shutdown (Pole Temp) | Float | ℃ |  | 0 | 1
test | 515 | 1 | 1664 | 2 | 0 | BMS Comm Parameters 1 | Voltage Diff at Cell Max-Min Diff Over-Alarm | Float | mV |  | 0 | 1
test | 515 | 1 | 1666 | 2 | 0 | BMS Comm Parameters 1 | Voltage Diff at Cell Max-Min Diff Over-Shutdown | Float | mV |  | 0 | 1
test | 515 | 1 | 1668 | 2 | 0 | BMS Comm Parameters 1 | Insulation Resistance at Alarm | Float | Ω/V |  | 0 | 1
test | 515 | 1 | 1670 | 2 | 0 | BMS Comm Parameters 1 | Insulation Resistance at Shutdown | Float | Ω/V |  | 0 | 1
test | 515 | 1 | 1672 | 2 | 0 | BMS Comm Parameters 1 | Voltage Diff at Total vs Slave Total Voltage Over-Alarm | Float | V |  | 0 | 1
test | 515 | 1 | 1674 | 2 | 0 | BMS Comm Parameters 1 | Voltage Diff at Total vs Slave Total Voltage Over-Shutdown | Float | V |  | 0 | 1
test | 515 | 1 | 1676 | 2 | 0 | BMS Comm Parameters 1 | Temp Diff at Cell Max-Min Temp Over-Alarm | Float | ℃ |  | 0 | 1
test | 515 | 1 | 1678 | 2 | 0 | BMS Comm Parameters 1 | Temp Diff at Cell Max-Min Temp Over-Shutdown | Float | ℃ |  | 0 | 1
test | 515 | 1 | 1680 | 2 | 0 | BMS Comm Parameters 1 | Module No. at Alarm Max Module Voltage | Float |  |  | 0 | 1
test | 515 | 1 | 1682 | 2 | 0 | BMS Comm Parameters 1 | Voltage at Module Overvoltage Alarm | Float | V |  | 0 | 1
test | 515 | 1 | 1684 | 2 | 0 | BMS Comm Parameters 1 | Module No. at Shutdown Max Module Voltage | Float |  |  | 0 | 1
test | 515 | 1 | 1686 | 2 | 0 | BMS Comm Parameters 1 | Voltage at Module Overvoltage Shutdown | Float | V |  | 0 | 1
test | 515 | 1 | 1688 | 2 | 0 | BMS Comm Parameters 1 | Module No. at Alarm Min Module Voltage | Float |  |  | 0 | 1
test | 515 | 1 | 1690 | 2 | 0 | BMS Comm Parameters 1 | Voltage at Module Undervoltage Alarm | Float | V |  | 0 | 1
test | 515 | 1 | 1692 | 2 | 0 | BMS Comm Parameters 1 | Module No. at Shutdown Min Module Voltage | Float |  |  | 0 | 1
test | 515 | 1 | 1694 | 2 | 0 | BMS Comm Parameters 1 | Voltage at Module Undervoltage Shutdown | Float | V |  | 0 | 1
test | 515 | 1 | 1696 | 2 | 0 | BMS Comm Parameters 1 | Start Insulation Sampling | Float |  | 0, Reset; 1, No Reset | 0 | 1
test | 515 | 1 | 1698 | 2 | 0 | BMS Comm Parameters 1 | Precharge Control | Float |  | 1, Start; 2, Stop | 0 | 1
test | 515 | 1 | 1700 | 2 | 0 | BMS Comm Parameters 1 | Main Controller Reset | Float |  | 1, Reset | 0 | 1
test | 515 | 1 | 1702 | 2 | 0 | BMS Comm Parameters 1 | Reset Slave ID Enable | Float |  | 1, Enable; 2, Disable | 0 | 1
test | 515 | 1 | 1704 | 2 | 0 | BMS Comm Parameters 1 | Set Master Address | Float |  |  | 0 | 1
test | 515 | 1 | 1706 | 2 | 0 | BMS Comm Parameters 1 | Fan Forced Control Switch | Float |  | 0, No Forced Control; 1, Forced On; 2, Forced Off | 0 | 1
test | 515 | 1 | 1708 | 2 | 0 | I/O | Comm Status | Float |  | 0, Offline; 1, Online | 1 | 1
test | 515 | 1 | 1710 | 2 | 0 | I/O | Emergency Stop Signal | Float |  | 0, Normal; 1, Alarm | 1 | 1
test | 515 | 1 | 1712 | 2 | 0 | I/O | Water Ingress Alarm | Float |  | 0, Normal; 1, Alarm | 1 | 1
test | 515 | 1 | 1714 | 2 | 0 | I/O | Breaker Feedback | Float |  | 0, Open; 1, Closed | 1 | 1
test | 515 | 1 | 1716 | 2 | 0 | I/O | DI4 | Float |  | 0, Open; 1, Closed | 1 | 1
test | 515 | 1 | 1718 | 2 | 0 | I/O | Door Access | Float |  | 0, Open; 1, Closed | 1 | 1
test | 515 | 1 | 1720 | 2 | 0 | I/O | Fire Protection Sprinkler | Float |  | 0, Normal; 1, Alarm | 1 | 1
test | 515 | 1 | 1722 | 2 | 0 | I/O | PCS Fault | Float |  | 0, Normal; 1, Alarm | 1 | 1
test | 515 | 1 | 1724 | 2 | 0 | I/O | DI8 | Float |  | 0, Open; 1, Closed | 1 | 1
test | 515 | 1 | 1726 | 2 | 0 | I/O | DI9 | Float |  | 0, Open; 1, Closed | 1 | 1
test | 515 | 1 | 1728 | 2 | 0 | I/O | DI10 | Float |  | 0, Open; 1, Closed | 1 | 1
test | 515 | 1 | 1730 | 2 | 0 | I/O | DI11 | Float |  | 0, Open; 1, Closed | 1 | 1
test | 515 | 1 | 1732 | 2 | 0 | I/O | DI12 | Float |  | 0, Open; 1, Closed | 1 | 1
test | 515 | 1 | 1734 | 2 | 0 | I/O | Breaker Control | Float |  | 0, Normal; 1, Tripped | 1 | 1
test | 515 | 1 | 1736 | 2 | 0 | I/O | Running Indicator | Float |  | 0, Open; 1, Closed | 1 | 1
test | 515 | 1 | 1738 | 2 | 0 | I/O | Fault Indicator | Float |  | 0, Open; 1, Closed | 1 | 1
test | 515 | 1 | 1740 | 2 | 0 | I/O | DO4 | Float |  | 0, Open; 1, Closed | 1 | 1
test | 515 | 1 | 1742 | 2 | 0 | I/O | DO5 | Float |  | 0, Open; 1, Closed | 1 | 1
test | 515 | 1 | 1744 | 2 | 0 | I/O | DO6 | Float |  | 0, Open; 1, Closed | 1 | 1
test | 515 | 1 | 1746 | 2 | 0 | I/O | DO7 | Float |  | 0, Open; 1, Closed | 1 | 1
test | 515 | 1 | 1748 | 2 | 0 | I/O | DO8 | Float |  | 0, Open; 1, Closed | 1 | 1
test | 515 | 1 | 1750 | 2 | 0 | PCS1 | Rated Power | Float | kW |  | 1 | 1
test | 515 | 1 | 1752 | 2 | 0 | PCS1 | Charge Power | Float | kW |  | 1 | 1
test | 515 | 1 | 1754 | 2 | 0 | PCS1 | Discharge Power | Float | kW |  | 1 | 1
test | 515 | 1 | 1756 | 2 | 0 | PCS1 | Charge/Discharge Power | Float | kW |  | 1 | 1
test | 515 | 1 | 1758 | 2 | 0 | PCS1 | DC Power | Float | kW |  | 1 | 1
test | 515 | 1 | 1760 | 2 | 0 | PCS1 | Available Charge Power | Float | kW |  | 1 | 1
test | 515 | 1 | 1762 | 2 | 0 | PCS1 | Available Discharge Power | Float | kW |  | 1 | 1
test | 515 | 1 | 1764 | 2 | 0 | PCS1 | Rate Limit Enable | Float |  | 0, Disabled; 1, Enabled | 1 | 1
test | 515 | 1 | 1766 | 2 | 0 | PCS1 | Device Available Charge Rate | Float |  |  | 1 | 1
test | 515 | 1 | 1768 | 2 | 0 | PCS1 | Device Available Discharge Rate | Float |  |  | 1 | 1
test | 515 | 1 | 1770 | 2 | 0 | PCS1 | BMS Available Charge Power | Float | kW |  | 1 | 1
test | 515 | 1 | 1772 | 2 | 0 | PCS1 | BMS Available Discharge Power | Float | kW |  | 1 | 1
test | 515 | 1 | 1774 | 2 | 0 | PCS1 | BMS Max Available Charge Current | Float | A |  | 1 | 1
test | 515 | 1 | 1776 | 2 | 0 | PCS1 | BMS Max Available Discharge Current | Float | A |  | 1 | 1
test | 515 | 1 | 1778 | 2 | 0 | PCS1 | BMS Total Voltage | Float | V |  | 1 | 1
test | 515 | 1 | 1780 | 2 | 0 | PCS1 | Charge SOC Setpoint (%) | Float | ％ |  | 1 | 1
test | 515 | 1 | 1782 | 2 | 0 | PCS1 | Discharge SOC Setpoint (%) | Float | ％ |  | 1 | 1
test | 515 | 1 | 1784 | 2 | 0 | PCS1 | Charge/Discharge Control Mode | Float |  | 0, Not Configured; 1, Shutdown; 2, Standby; 3, Charge; 4, Discharge | 1 | 1
test | 515 | 1 | 1786 | 2 | 0 | PCS1 | SOC | Float | % |  | 1 | 1
test | 515 | 1 | 1788 | 2 | 0 | PCS1 | SOC Limit Enable | Float |  |  | 1 | 1
test | 515 | 1 | 1790 | 2 | 0 | PCS1 | Charge Cutoff SOC Setting | Float | kW |  | 1 | 1
test | 515 | 1 | 1792 | 2 | 0 | PCS1 | Discharge Cutoff SOC Setting | Float | kW |  | 1 | 1
test | 515 | 1 | 1794 | 2 | 0 | PCS1 | Running Status | Float |  | 0, Stopped; 1, Self-Check; 2, Running; 4, Fault; 7, Standby | 1 | 1
test | 515 | 1 | 1796 | 2 | 0 | PCS1 | Fault Status | Float |  | 0, Normal; 1, Fault | 1 | 1
test | 515 | 1 | 1798 | 2 | 0 | PCS1 | Grid-Connected Status | Float |  | 0, Invalid; 1, Grid-Connected | 1 | 1
test | 515 | 1 | 1800 | 2 | 0 | PCS1 | Off-Grid Status | Float |  | 0, Invalid; 1, Off-Grid | 1 | 1
test | 515 | 1 | 1802 | 2 | 0 | PCS1 | Locked | Float |  | 0, Unlocked; 1, Locked | 1 | 1
test | 515 | 1 | 1804 | 2 | 0 | PCS1 | Fault Reset | Float |  | 0, Normal; 1, Reset | 1 | 1
test | 515 | 1 | 1806 | 2 | 0 | PCS1 | Emergency Stop | Float |  | 0, Normal; 1, Emergency Stop | 1 | 1
test | 515 | 1 | 1808 | 2 | 0 | PCS1 | Start/Stop Control | Float |  | 0, Stop; 1, Start | 1 | 1
test | 515 | 1 | 1810 | 2 | 0 | PCS1 | Start Control | Float |  | 0, Invalid; 1, Start | 1 | 1
test | 515 | 1 | 1812 | 2 | 0 | PCS1 | Stop Control | Float |  | 0, Invalid; 1, Shutdown | 1 | 1
test | 515 | 1 | 1814 | 2 | 0 | PCS1 | Auto Start/Stop Command | Float |  | 0, Stop; 1, Start | 1 | 1
test | 515 | 1 | 1816 | 2 | 0 | PCS1 | Start Failure | Float |  | 0, Normal; 1, Start Failed | 1 | 1
test | 515 | 1 | 1818 | 2 | 0 | PCS1 | Action Timeout Setting | Float | s |  | 1 | 1
test | 515 | 1 | 1820 | 2 | 0 | PCS1 | Action Time | Float | s |  | 1 | 1
test | 515 | 1 | 1822 | 2 | 0 | PCS1 | Offline Timeout Setting | Float | s |  | 1 | 1
test | 515 | 1 | 1824 | 2 | 0 | PCS1 | Offline Time | Float | s |  | 1 | 1
test | 515 | 1 | 1826 | 2 | 0 | PCS1 | Offline Status | Float |  |  | 1 | 1
test | 515 | 1 | 1828 | 2 | 0 | PCS1 | Total Fault Status | Float |  | 0, Normal; 1, Fault | 1 | 1
test | 515 | 1 | 1830 | 2 | 0 | PCS1 | Time Reset | Float |  | 0, Normal; 1, Reset | 1 | 1
test | 515 | 1 | 1832 | 2 | 0 | PCS1 | Auto Available Status | Float |  | 0, Disabled; 1, Available | 1 | 1
test | 515 | 1 | 1834 | 2 | 0 | PCS1 | BMS Online Status | Float |  | 0, Offline; 1, Online | 1 | 1
test | 515 | 1 | 1836 | 2 | 0 | PCS1 | PCS Online Status | Float |  | 0, Offline; 1, Online | 1 | 1
test | 515 | 1 | 1838 | 2 | 0 | PCS1 | Liquid Cooling Online Status | Float |  | 0, Offline; 1, Online | 1 | 1
test | 515 | 1 | 1840 | 2 | 0 | PCS1 | Liquid Cooling Device Status | Float |  | 0, Shutdown; 1, Self-Circulation; 2, Standby; 3, Cooling; 4, Heating; 5, Manual; 6, Vacuum Pumping; 7, Fault Shutdown; 8, Group Control Standby; 9, Remote Shutdown; 10, Auto Exhaust | 1 | 1
test | 515 | 1 | 1842 | 2 | 0 | PCS1 | Fire Protection Status | Float |  | 0, Normal; 1, Fire Protection Offline; 2, Fire Protection Alarm | 1 | 1
test | 515 | 1 | 1844 | 2 | 0 | PCS1 | Water Ingress Alarm | Float |  | 0, Normal; 1, Alarm | 1 | 1
test | 515 | 1 | 1846 | 2 | 0 | PCS1 | PPS Pulse | Float |  |  | 1 | 1
test | 515 | 1 | 1848 | 2 | 0 | PCS1 | Grid On/Off Switch | Float |  | 0, Grid-Connected; 1, Off-Grid | 1 | 1
test | 515 | 1 | 1850 | 2 | 0 | PCS1 | Grid On/Off Switch Flag | Float |  | 0, Complete; 1, Grid-Connected; 2, Off-Grid | 1 | 1
test | 515 | 1 | 1852 | 2 | 0 | PCS1 | Battery Precharge Control | Float |  | 0, Power-Off; 1, Power-On | 1 | 1
test | 515 | 1 | 1854 | 2 | 0 | PCS1 | Battery Precharge Control Flag | Float |  | 0, Complete; 1, Power-Off; 2, Power-On | 1 | 1
test | 515 | 1 | 1856 | 2 | 0 | PCS1 | Battery System Status | Float |  | 0, Normal; 1, Charge Disabled; 2, Discharge Disabled; 3, Standby; 4, Stopped | 1 | 1
test | 515 | 1 | 1858 | 2 | 0 | PCS1 | PCS Reset | Float |  | 0, Normal; 1, Reset | 1 | 1
test | 515 | 1 | 1860 | 2 | 0 | PCS1 | Off-Grid Shutdown SOC | Float |  |  | 1 | 1
test | 515 | 1 | 1862 | 2 | 0 | PCS1 | System Abnormal | Float |  |  | 1 | 1
test | 515 | 1 | 1864 | 2 | 0 | PCS1 | Off-Grid Start Timer | Float |  |  | 1 | 1
test | 515 | 1 | 1866 | 2 | 0 | PCS1 | Off-Grid Start Timer Setting | Float |  |  | 1 | 1
test | 515 | 1 | 1868 | 2 | 0 | PCS Comm Parameters 1 | Online Points | Float |  | 0, Offline; 1, Online | 1 | 1
test | 515 | 1 | 1870 | 2 | 0 | PCS Comm Parameters 1 | Fault Reset | Float |  | 0, Invalid; 1, Reset | 1 | 1
test | 515 | 1 | 1872 | 2 | 0 | PCS Comm Parameters 1 | Device Start | Float |  | 0, Invalid; 1, Start | 1 | 1
test | 515 | 1 | 1874 | 2 | 0 | PCS Comm Parameters 1 | Device Stop | Float |  | 0, Invalid; 1, Shutdown | 1 | 1
test | 515 | 1 | 1876 | 2 | 0 | PCS Comm Parameters 1 | Remote Emergency Stop | Float |  | 0, Invalid; 1, Emergency Stop | 1 | 1
test | 515 | 1 | 1878 | 2 | 0 | PCS Comm Parameters 1 | Cumulative Charge Energy Clear | Float |  | 0, Invalid; 1, Clear | 1 | 1
test | 515 | 1 | 1880 | 2 | 0 | PCS Comm Parameters 1 | Cumulative Discharge Energy Clear | Float |  | 0, Invalid; 1, Clear | 1 | 1
test | 515 | 1 | 1882 | 2 | 0 | PCS Comm Parameters 1 | Remote/Local Setting | Float |  | 0, Local; 1, Remote | 1 | 1
test | 515 | 1 | 1884 | 2 | 0 | PCS Comm Parameters 1 | Device Standby | Float |  | 0, Invalid; 1, Standby | 1 | 1
test | 515 | 1 | 1886 | 2 | 0 | PCS Comm Parameters 1 | Shutdown Status | Float |  | 0, Invalid; 1, Shutdown | 1 | 1
test | 515 | 1 | 1888 | 2 | 0 | PCS Comm Parameters 1 | Standby Status | Float |  | 0, Invalid; 1, Standby | 1 | 1
test | 515 | 1 | 1890 | 2 | 0 | PCS Comm Parameters 1 | Running Status | Float |  | 0, Invalid; 1, Running | 1 | 1
test | 515 | 1 | 1892 | 2 | 0 | PCS Comm Parameters 1 | Total Fault Status | Float |  | 0, Invalid; 1, Fault | 1 | 1
test | 515 | 1 | 1894 | 2 | 0 | PCS Comm Parameters 1 | Total Alarm Status | Float |  | 0, Invalid; 1, Alarm | 1 | 1
test | 515 | 1 | 1896 | 2 | 0 | PCS Comm Parameters 1 | Remote/Local Status | Float |  | 0, Local; 1, Remote | 1 | 1
test | 515 | 1 | 1898 | 2 | 0 | PCS Comm Parameters 1 | Emergency Stop Input Status | Float |  | 0, Invalid; 1, Emergency Stop | 1 | 1
test | 515 | 1 | 1900 | 2 | 0 | PCS Comm Parameters 1 | Grid-Connected Status | Float |  | 0, Invalid; 1, Grid-Connected | 1 | 1
test | 515 | 1 | 1902 | 2 | 0 | PCS Comm Parameters 1 | VF Off-Grid Status | Float |  | 0, Invalid; 1, VF Off-Grid | 1 | 1
test | 515 | 1 | 1904 | 2 | 0 | PCS Comm Parameters 1 | Overload Derating | Float |  | 0, Invalid; 1, Overload Occurred | 1 | 1
test | 515 | 1 | 1906 | 2 | 0 | PCS Comm Parameters 1 | BMS Dry Contact Input | Float |  | 0, Invalid; 1, Fault Active | 1 | 1
test | 515 | 1 | 1908 | 2 | 0 | PCS Comm Parameters 1 | A-Phase Voltage | Float | V |  | 1 | 1
test | 515 | 1 | 1910 | 2 | 0 | PCS Comm Parameters 1 | B-Phase Voltage | Float | V |  | 1 | 1
test | 515 | 1 | 1912 | 2 | 0 | PCS Comm Parameters 1 | C-Phase Voltage | Float | V |  | 1 | 1
test | 515 | 1 | 1914 | 2 | 0 | PCS Comm Parameters 1 | A-Phase Current | Float | A |  | 1 | 1
test | 515 | 1 | 1916 | 2 | 0 | PCS Comm Parameters 1 | B-Phase Current | Float | A |  | 1 | 1
test | 515 | 1 | 1918 | 2 | 0 | PCS Comm Parameters 1 | C-Phase Current | Float | A |  | 1 | 1
test | 515 | 1 | 1920 | 2 | 0 | PCS Comm Parameters 1 | Grid Frequency | Float | Hz |  | 1 | 1
test | 515 | 1 | 1922 | 2 | 0 | PCS Comm Parameters 1 | A-Phase Active Power | Float | kW |  | 1 | 1
test | 515 | 1 | 1924 | 2 | 0 | PCS Comm Parameters 1 | B-Phase Active Power | Float | kW |  | 1 | 1
test | 515 | 1 | 1926 | 2 | 0 | PCS Comm Parameters 1 | C-Phase Active Power | Float | kW |  | 1 | 1
test | 515 | 1 | 1928 | 2 | 0 | PCS Comm Parameters 1 | Total Active Power | Float | kW |  | 1 | 1
test | 515 | 1 | 1930 | 2 | 0 | PCS Comm Parameters 1 | A-Phase Reactive Power | Float | kVar |  | 1 | 1
test | 515 | 1 | 1932 | 2 | 0 | PCS Comm Parameters 1 | B-Phase Reactive Power | Float | kVar |  | 1 | 1
test | 515 | 1 | 1934 | 2 | 0 | PCS Comm Parameters 1 | C-Phase Reactive Power | Float | kVar |  | 1 | 1
test | 515 | 1 | 1936 | 2 | 0 | PCS Comm Parameters 1 | Total Reactive Power | Float | kVar |  | 1 | 1
test | 515 | 1 | 1938 | 2 | 0 | PCS Comm Parameters 1 | A-Phase Apparent Power | Float | kVA |  | 1 | 1
test | 515 | 1 | 1940 | 2 | 0 | PCS Comm Parameters 1 | B-Phase Apparent Power | Float | kVA |  | 1 | 1
test | 515 | 1 | 1942 | 2 | 0 | PCS Comm Parameters 1 | C-Phase Apparent Power | Float | kVA |  | 1 | 1
test | 515 | 1 | 1944 | 2 | 0 | PCS Comm Parameters 1 | Total Apparent Power | Float | kVA |  | 1 | 1
test | 515 | 1 | 1946 | 2 | 0 | PCS Comm Parameters 1 | A-Phase Power Factor | Float |  |  | 1 | 1
test | 515 | 1 | 1948 | 2 | 0 | PCS Comm Parameters 1 | B-Phase Power Factor | Float |  |  | 1 | 1
test | 515 | 1 | 1950 | 2 | 0 | PCS Comm Parameters 1 | C-Phase Power Factor | Float |  |  | 1 | 1
test | 515 | 1 | 1952 | 2 | 0 | PCS Comm Parameters 1 | Total Power Factor | Float |  |  | 1 | 1
test | 515 | 1 | 1954 | 2 | 0 | PCS Comm Parameters 1 | DC Power | Float | kW |  | 1 | 1
test | 515 | 1 | 1956 | 2 | 0 | PCS Comm Parameters 1 | DC Voltage | Float | V |  | 1 | 1
test | 515 | 1 | 1958 | 2 | 0 | PCS Comm Parameters 1 | DC Current | Float | A |  | 1 | 1
test | 515 | 1 | 1960 | 2 | 0 | PCS Comm Parameters 1 | Heatsink Temperature | Float | ℃ |  | 1 | 1
test | 515 | 1 | 1962 | 2 | 0 | PCS Comm Parameters 1 | BMS Working Status | Float |  |  | 1 | 1
test | 515 | 1 | 1964 | 2 | 0 | PCS Comm Parameters 1 | PCS Running Status | Float |  | 0, Stopped; 1, Self-Check; 2, Running; 4, Fault; 7, Standby | 1 | 1
test | 515 | 1 | 1966 | 2 | 0 | PCS Comm Parameters 1 | AC Cumulative Charge Energy | Float | kWh |  | 1 | 1
test | 515 | 1 | 1968 | 2 | 0 | PCS Comm Parameters 1 | AC Cumulative Discharge Energy | Float | kWh |  | 1 | 1
test | 515 | 1 | 1970 | 2 | 0 | PCS Comm Parameters 1 | DC Cumulative Charge Energy | Float | kWh |  | 1 | 1
test | 515 | 1 | 1972 | 2 | 0 | PCS Comm Parameters 1 | DC Cumulative Discharge Energy | Float | kWh |  | 1 | 1
test | 515 | 1 | 1974 | 2 | 0 | PCS Comm Parameters 1 | PCS Comm Status Word | Float |  |  | 1 | 1
test | 515 | 1 | 1976 | 2 | 0 | PCS Comm Parameters 1 | Second | Float |  |  | 1 | 1
test | 515 | 1 | 1978 | 2 | 0 | PCS Comm Parameters 1 | Minute | Float |  |  | 1 | 1
test | 515 | 1 | 1980 | 2 | 0 | PCS Comm Parameters 1 | Hour | Float |  |  | 1 | 1
test | 515 | 1 | 1982 | 2 | 0 | PCS Comm Parameters 1 | Day | Float |  |  | 1 | 1
test | 515 | 1 | 1984 | 2 | 0 | PCS Comm Parameters 1 | Month | Float |  |  | 1 | 1
test | 515 | 1 | 1986 | 2 | 0 | PCS Comm Parameters 1 | Year | Float |  |  | 1 | 1
test | 515 | 1 | 1988 | 2 | 0 | PCS Comm Parameters 1 | N-Phase Current RMS | Float | A |  | 1 | 1
test | 515 | 1 | 1990 | 2 | 0 | PCS Comm Parameters 1 | Derating Factor | Float |  |  | 1 | 1
test | 515 | 1 | 1992 | 2 | 0 | PCS Comm Parameters 1 | Derating Flag | Float |  | 0, No Derating; 1, Host/EMS Command Derating; 2, BMS Derating; 3, DC Over/Under Voltage Derating; 4, Over-Temperature Derating; 5, AC Under-Voltage Derating | 1 | 1
test | 515 | 1 | 1994 | 2 | 0 | PCS Comm Parameters 1 | PCS DC Link Upper Voltage | Float | V |  | 1 | 1
test | 515 | 1 | 1996 | 2 | 0 | PCS Comm Parameters 1 | PCS DC Link Lower Voltage | Float | V |  | 1 | 1
test | 515 | 1 | 1998 | 2 | 0 | PCS Comm Parameters 1 | PCS Total DC Voltage | Float | V |  | 1 | 1
test | 515 | 1 | 2000 | 2 | 0 | PCS Comm Parameters 1 | Leakage Current Value | Float | A |  | 1 | 1
test | 515 | 1 | 2002 | 2 | 0 | PCS Comm Parameters 1 | Insulation Resistance Value | Float | KΩ |  | 1 | 1
test | 515 | 1 | 2004 | 2 | 0 | PCS Comm Parameters 1 | A-Phase Branch 1 Current | Float | A |  | 1 | 1
test | 515 | 1 | 2006 | 2 | 0 | PCS Comm Parameters 1 | B-Phase Branch 1 Current | Float | A |  | 1 | 1
test | 515 | 1 | 2008 | 2 | 0 | PCS Comm Parameters 1 | C-Phase Branch 1 Current | Float | A |  | 1 | 1
test | 515 | 1 | 2010 | 2 | 0 | PCS Comm Parameters 1 | N-Phase Branch 1 Current | Float | A |  | 1 | 1
test | 515 | 1 | 2012 | 2 | 0 | PCS Comm Parameters 1 | A-Phase Branch 2 Current | Float | A |  | 1 | 1
test | 515 | 1 | 2014 | 2 | 0 | PCS Comm Parameters 1 | B-Phase Branch 2 Current | Float | A |  | 1 | 1
test | 515 | 1 | 2016 | 2 | 0 | PCS Comm Parameters 1 | C-Phase Branch 2 Current | Float | A |  | 1 | 1
test | 515 | 1 | 2018 | 2 | 0 | PCS Comm Parameters 1 | N-Phase Branch 2 Current | Float | A |  | 1 | 1
test | 515 | 1 | 2020 | 2 | 0 | PCS Comm Parameters 1 | A-Phase Temperature | Float | ℃ |  | 1 | 1
test | 515 | 1 | 2022 | 2 | 0 | PCS Comm Parameters 1 | B-Phase Temperature | Float | ℃ |  | 1 | 1
test | 515 | 1 | 2024 | 2 | 0 | PCS Comm Parameters 1 | C-Phase Temperature | Float | ℃ |  | 1 | 1
test | 515 | 1 | 2026 | 2 | 0 | PCS Comm Parameters 1 | N-Phase Temperature | Float | ℃ |  | 1 | 1
test | 515 | 1 | 2028 | 2 | 0 | PCS Comm Parameters 1 | Air Inlet Temperature | Float | ℃ |  | 1 | 1
test | 515 | 1 | 2030 | 2 | 0 | PCS Comm Parameters 1 | Cabinet Internal Temperature | Float | ℃ |  | 1 | 1
test | 515 | 1 | 2032 | 2 | 0 | PCS Comm Parameters 1 | Air Outlet Temperature | Float | ℃ |  | 1 | 1
test | 515 | 1 | 2034 | 2 | 0 | PCS Comm Parameters 1 | Control Chip Junction Temp | Float | ℃ |  | 1 | 1
test | 515 | 1 | 2036 | 2 | 0 | PCS Comm Parameters 1 | Comm Chip Junction Temp | Float | ℃ |  | 1 | 1
test | 515 | 1 | 2038 | 2 | 0 | PCS Comm Parameters 1 | Running Mode Selection | Float |  | 0, Reserved; 1, CC Charging; 2, CV Charging; 3, CP Charging; 4, DC CV Mode | 1 | 1
test | 515 | 1 | 2040 | 2 | 0 | PCS Comm Parameters 1 | Constant Voltage Charge Voltage Setpoint | Float | V |  | 1 | 1
test | 515 | 1 | 2042 | 2 | 0 | PCS Comm Parameters 1 | Constant Current Charge Current Setpoint | Float | A |  | 1 | 1
test | 515 | 1 | 2044 | 2 | 0 | PCS Comm Parameters 1 | Active Power Setpoint | Float | kW |  | 1 | 1
test | 515 | 1 | 2046 | 2 | 0 | PCS Comm Parameters 1 | Reactive Power Setpoint | Float | kVar |  | 1 | 1
test | 515 | 1 | 2048 | 2 | 0 | PCS Comm Parameters 1 | Grid On/Off Setting | Float |  | 0, Grid-Tied Mode; 1, Off-Grid Mode; 2, VSG Mode | 1 | 1
test | 515 | 1 | 2050 | 2 | 0 | PCS Comm Parameters 1 | Off-Grid Output Voltage Setpoint | Float | V |  | 1 | 1
test | 515 | 1 | 2052 | 2 | 0 | PCS Comm Parameters 1 | Off-Grid Output Frequency Setpoint | Float | Hz |  | 1 | 1
test | 515 | 1 | 2054 | 2 | 0 | PCS Comm Parameters 1 | A-Phase Active Power Setpoint | Float | kW |  | 1 | 1
test | 515 | 1 | 2056 | 2 | 0 | PCS Comm Parameters 1 | B-Phase Active Power Setpoint | Float | kW |  | 1 | 1
test | 515 | 1 | 2058 | 2 | 0 | PCS Comm Parameters 1 | C-Phase Active Power Setpoint | Float | kW |  | 1 | 1
test | 515 | 1 | 2060 | 2 | 0 | PCS Comm Parameters 1 | A-Phase Reactive Power Setpoint | Float | kVar |  | 1 | 1
test | 515 | 1 | 2062 | 2 | 0 | PCS Comm Parameters 1 | B-Phase Reactive Power Setpoint | Float | kVar |  | 1 | 1
test | 515 | 1 | 2064 | 2 | 0 | PCS Comm Parameters 1 | C-Phase Reactive Power Setpoint | Float | kVar |  | 1 | 1
test | 515 | 1 | 2066 | 2 | 0 | PCS Comm Parameters 1 | Off-Grid A-Phase Voltage Setpoint | Float | V |  | 1 | 1
test | 515 | 1 | 2068 | 2 | 0 | PCS Comm Parameters 1 | Off-Grid B-Phase Voltage Setpoint | Float | V |  | 1 | 1
test | 515 | 1 | 2070 | 2 | 0 | PCS Comm Parameters 1 | Off-Grid C-Phase Voltage Setpoint | Float | V |  | 1 | 1
test | 515 | 1 | 2072 | 2 | 0 | PCS Comm Parameters 1 | Primary Frequency Regulation Dead Band | Float | Hz |  | 1 | 1
test | 515 | 1 | 2074 | 2 | 0 | PCS Comm Parameters 1 | Primary Frequency Regulation K Value | Float |  |  | 1 | 1
test | 515 | 1 | 2076 | 2 | 0 | PCS Comm Parameters 1 | VSG Frequency Droop Coefficient | Float |  |  | 1 | 1
test | 515 | 1 | 2078 | 2 | 0 | PCS Comm Parameters 1 | VSG Voltage Droop Coefficient | Float |  |  | 1 | 1
test | 515 | 1 | 2080 | 2 | 0 | PCS Comm Parameters 1 | Grid On/Off Switch Running Mode | Float |  | 0, None; 1, Manual; 2, Auto; 3, Hybrid; 4, Silent | 1 | 1
test | 515 | 1 | 2082 | 2 | 0 | PCS Comm Parameters 1 | Active Power Control Mode | Float |  | 0, Phase Power Control Mode; 1, Total Power Control Mode | 1 | 1
test | 515 | 1 | 2084 | 2 | 0 | PCS Comm Parameters 1 | Time Sync - Second | Float |  |  | 1 | 1
test | 515 | 1 | 2086 | 2 | 0 | PCS Comm Parameters 1 | Time Sync - Minute | Float |  |  | 1 | 1
test | 515 | 1 | 2088 | 2 | 0 | PCS Comm Parameters 1 | Time Sync - Hour | Float |  |  | 1 | 1
test | 515 | 1 | 2090 | 2 | 0 | PCS Comm Parameters 1 | Time Sync - Day | Float |  |  | 1 | 1
test | 515 | 1 | 2092 | 2 | 0 | PCS Comm Parameters 1 | Time Sync - Month | Float |  |  | 1 | 1
test | 515 | 1 | 2094 | 2 | 0 | PCS Comm Parameters 1 | Time Sync - Year | Float |  |  | 1 | 1
test | 515 | 1 | 2096 | 2 | 0 | PCS Comm Parameters 1 | Reactive Power Mode | Float |  | 0, Constant Power Mode; 1, Constant Power Factor Mode | 1 | 1
test | 515 | 1 | 2098 | 2 | 0 | PCS Comm Parameters 1 | Power Factor Setting | Float |  |  | 1 | 1
test | 515 | 1 | 2100 | 2 | 0 | PCS Comm Parameters 1 | Insulation Detection Enable | Float |  | 0, Disable; 1, Enable | 1 | 1
test | 515 | 1 | 2102 | 2 | 0 | PCS Comm Parameters 1 | Leakage Current Threshold Setting | Float | A |  | 1 | 1
test | 515 | 1 | 2104 | 2 | 0 | PCS Comm Parameters 1 | Insulation Resistance Threshold Setting | Float | KΩ |  | 1 | 1
test | 515 | 1 | 2106 | 2 | 0 | PCS Comm Parameters 1 | Primary Frequency Regulation Enable | Float |  | 0, Disabled; 1, Enabled | 1 | 1
test | 515 | 1 | 2108 | 2 | 0 | PCS Comm Parameters 1 | Hardware Fault - A-Phase HW Overcurrent | Float |  | 0, Normal; 1, Fault | 1 | 1
test | 515 | 1 | 2110 | 2 | 0 | PCS Comm Parameters 1 | Hardware Fault - B-Phase HW Overcurrent | Float |  | 0, Normal; 1, Fault | 1 | 1
test | 515 | 1 | 2112 | 2 | 0 | PCS Comm Parameters 1 | Hardware Fault - C-Phase HW Overcurrent | Float |  | 0, Normal; 1, Fault | 1 | 1
test | 515 | 1 | 2114 | 2 | 0 | PCS Comm Parameters 1 | Hardware Fault - N-Phase HW Overcurrent | Float |  | 0, Normal; 1, Fault | 1 | 1
test | 515 | 1 | 2116 | 2 | 0 | PCS Comm Parameters 1 | Hardware Fault - AC/DC Power Mismatch | Float |  | 0, Normal; 1, Fault | 1 | 1
test | 515 | 1 | 2118 | 2 | 0 | PCS Comm Parameters 1 | Hardware Fault - Auxiliary Power Loss | Float |  | 0, Normal; 1, Fault | 1 | 1
test | 515 | 1 | 2120 | 2 | 0 | PCS Comm Parameters 1 | Hardware Fault - Temp Too Low or Sensor Fault | Float |  | 0, Normal; 1, Fault | 1 | 1
test | 515 | 1 | 2122 | 2 | 0 | PCS Comm Parameters 1 | Hardware Fault - Insulation Fault | Float |  | 0, Normal; 1, Fault | 1 | 1
test | 515 | 1 | 2124 | 2 | 0 | PCS Comm Parameters 1 | Hardware Fault - Total Drive Fault | Float |  | 0, Normal; 1, Fault | 1 | 1
test | 515 | 1 | 2126 | 2 | 0 | PCS Comm Parameters 1 | Software Fault - A-Phase Drive Fault | Float |  | 0, Normal; 1, Fault | 1 | 1
test | 515 | 1 | 2128 | 2 | 0 | PCS Comm Parameters 1 | Hardware Fault - B-Phase Drive Fault | Float |  | 0, Normal; 1, Fault | 1 | 1
test | 515 | 1 | 2130 | 2 | 0 | PCS Comm Parameters 1 | Hardware Fault - C-Phase Drive Fault | Float |  | 0, Normal; 1, Fault | 1 | 1
test | 515 | 1 | 2132 | 2 | 0 | PCS Comm Parameters 1 | Hardware Fault - N-Phase Drive Fault | Float |  | 0, Normal; 1, Fault | 1 | 1
test | 515 | 1 | 2134 | 2 | 0 | PCS Comm Parameters 1 | Hardware Fault - Heatsink Over-Temp Fault | Float |  | 0, Normal; 1, Fault | 1 | 1
test | 515 | 1 | 2136 | 2 | 0 | PCS Comm Parameters 1 | Hardware Fault - Ambient Over-Temp Fault | Float |  | 0, Normal; 1, Fault | 1 | 1
test | 515 | 1 | 2138 | 2 | 0 | PCS Comm Parameters 1 | Software Fault - A-Phase Output Overload | Float |  | 0, Normal; 1, Fault | 1 | 1
test | 515 | 1 | 2140 | 2 | 0 | PCS Comm Parameters 1 | Software Fault - A-Phase Output Overcurrent | Float |  | 0, Normal; 1, Fault | 1 | 1
test | 515 | 1 | 2142 | 2 | 0 | PCS Comm Parameters 1 | Software Fault - B-Phase Output Overload | Float |  | 0, Normal; 1, Fault | 1 | 1
test | 515 | 1 | 2144 | 2 | 0 | PCS Comm Parameters 1 | Software Fault - B-Phase Output Overcurrent | Float |  | 0, Normal; 1, Fault | 1 | 1
test | 515 | 1 | 2146 | 2 | 0 | PCS Comm Parameters 1 | Software Fault - C-Phase Output Overload | Float |  | 0, Normal; 1, Fault | 1 | 1
test | 515 | 1 | 2148 | 2 | 0 | PCS Comm Parameters 1 | Software Fault - C-Phase Output Overcurrent | Float |  | 0, Normal; 1, Fault | 1 | 1
test | 515 | 1 | 2150 | 2 | 0 | PCS Comm Parameters 1 | Software Fault - N-Phase Output Overload | Float |  | 0, Normal; 1, Fault | 1 | 1
test | 515 | 1 | 2152 | 2 | 0 | PCS Comm Parameters 1 | Software Fault - N-Phase Output Overcurrent | Float |  | 0, Normal; 1, Fault | 1 | 1
test | 515 | 1 | 2154 | 2 | 0 | PCS Comm Parameters 1 | Software Fault - AC Overvoltage | Float |  | 0, Normal; 1, Fault | 1 | 1
test | 515 | 1 | 2156 | 2 | 0 | PCS Comm Parameters 1 | Software Fault - AC Undervoltage | Float |  | 0, Normal; 1, Fault | 1 | 1
test | 515 | 1 | 2158 | 2 | 0 | PCS Comm Parameters 1 | Software Fault - AC Output Overvoltage | Float |  | 0, Normal; 1, Fault | 1 | 1
test | 515 | 1 | 2160 | 2 | 0 | PCS Comm Parameters 1 | Software Fault - AC Output Undervoltage | Float |  | 0, Normal; 1, Fault | 1 | 1
test | 515 | 1 | 2162 | 2 | 0 | PCS Comm Parameters 1 | Software Fault - THDU Exceeded | Float |  | 0, Normal; 1, Fault | 1 | 1
test | 515 | 1 | 2164 | 2 | 0 | PCS Comm Parameters 1 | Software Fault - AC Phase Loss | Float |  | 0, Normal; 1, Fault | 1 | 1
test | 515 | 1 | 2166 | 2 | 0 | PCS Comm Parameters 1 | Software Fault - AC Phase Sequence Error | Float |  | 0, Normal; 1, Fault | 1 | 1
test | 515 | 1 | 2168 | 2 | 0 | PCS Comm Parameters 1 | Software Fault - DC Reverse Polarity Fault | Float |  | 0, Normal; 1, Fault | 1 | 1
test | 515 | 1 | 2170 | 2 | 0 | PCS Comm Parameters 1 | Software Fault - DC Bus Software Overvoltage | Float |  | 0, Normal; 1, Fault | 1 | 1
test | 515 | 1 | 2172 | 2 | 0 | PCS Comm Parameters 1 | Software Fault - DC Bus Software Undervoltage | Float |  | 0, Normal; 1, Fault | 1 | 1
test | 515 | 1 | 2174 | 2 | 0 | PCS Comm Parameters 1 | Software Fault - AC Over-Frequency | Float |  | 0, Normal; 1, Fault | 1 | 1
test | 515 | 1 | 2176 | 2 | 0 | PCS Comm Parameters 1 | Software Fault - AC Under-Frequency | Float |  | 0, Normal; 1, Fault | 1 | 1
test | 515 | 1 | 2178 | 2 | 0 | PCS Comm Parameters 1 | Software Fault - DC Charge Overcurrent | Float |  | 0, Normal; 1, Fault | 1 | 1
test | 515 | 1 | 2180 | 2 | 0 | PCS Comm Parameters 1 | Software Fault - DC Discharge Overcurrent | Float |  | 0, Normal; 1, Fault | 1 | 1
test | 515 | 1 | 2182 | 2 | 0 | PCS Comm Parameters 1 | Software Fault - SPI Comm Fault | Float |  | 0, Normal; 1, Fault | 1 | 1
test | 515 | 1 | 2184 | 2 | 0 | PCS Comm Parameters 1 | Software Fault - DC Component Exceeded | Float |  | 0, Normal; 1, Fault | 1 | 1
test | 515 | 1 | 2186 | 2 | 0 | PCS Comm Parameters 1 | Software Fault - AC Relay Closing Fault | Float |  | 0, Normal; 1, Fault | 1 | 1
test | 515 | 1 | 2188 | 2 | 0 | PCS Comm Parameters 1 | Software Fault - AC Relay Opening Fault | Float |  | 0, Normal; 1, Fault | 1 | 1
test | 515 | 1 | 2190 | 2 | 0 | PCS Comm Parameters 1 | Software Fault - AC Soft-Start Relay Closing Fault | Float |  | 0, Normal; 1, Fault | 1 | 1
test | 515 | 1 | 2192 | 2 | 0 | PCS Comm Parameters 1 | Software Fault - AC Soft-Start Relay Opening Fault | Float |  | 0, Normal; 1, Fault | 1 | 1
test | 515 | 1 | 2194 | 2 | 0 | PCS Comm Parameters 1 | Software Fault - DC Main Positive Closing Fault | Float |  | 0, Normal; 1, Fault | 1 | 1
test | 515 | 1 | 2196 | 2 | 0 | PCS Comm Parameters 1 | Software Fault - DC Main Positive Opening Fault | Float |  | 0, Normal; 1, Fault | 1 | 1
test | 515 | 1 | 2198 | 2 | 0 | PCS Comm Parameters 1 | Software Fault - DC Main Negative Closing Fault | Float |  | 0, Normal; 1, Fault | 1 | 1
test | 515 | 1 | 2200 | 2 | 0 | PCS Comm Parameters 1 | Software Fault - DC Main Negative Closing Fault 2 | Float |  | 0, Normal; 1, Fault | 1 | 1
test | 515 | 1 | 2202 | 2 | 0 | PCS Comm Parameters 1 | Software Fault - F-RAM Parameter Save Error | Float |  | 0, Normal; 1, Fault | 1 | 1
test | 515 | 1 | 2204 | 2 | 0 | PCS Comm Parameters 1 | Software Fault - DC Soft Start Failure | Float |  | 0, Normal; 1, Fault | 1 | 1
test | 515 | 1 | 2206 | 2 | 0 | PCS Comm Parameters 1 | Software Fault - AC/DC Voltage Mismatch | Float |  | 0, Normal; 1, Fault | 1 | 1
test | 515 | 1 | 2208 | 2 | 0 | PCS Comm Parameters 1 | Software Fault - Grid Islanding Fault | Float |  | 0, Normal; 1, Fault | 1 | 1
test | 515 | 1 | 2210 | 2 | 0 | PCS Comm Parameters 1 | Software Fault - Start Condition Not Met | Float |  | 0, Normal; 1, Fault | 1 | 1
test | 515 | 1 | 2212 | 2 | 0 | PCS Comm Parameters 1 | Software Fault - Switch Fault During Operation | Float |  | 0, Normal; 1, Fault | 1 | 1
test | 515 | 1 | 2214 | 2 | 0 | PCS Comm Parameters 1 | Software Fault - Start Timeout Fault | Float |  | 0, Normal; 1, Fault | 1 | 1
test | 515 | 1 | 2216 | 2 | 0 | PCS Comm Parameters 1 | Software Fault - Parameter Configuration Error | Float |  | 0, Normal; 1, Fault | 1 | 1
test | 515 | 1 | 2218 | 2 | 0 | PCS Comm Parameters 1 | Software Fault - Branch Instantaneous Value Imbalance | Float |  | 0, Normal; 1, Fault | 1 | 1
test | 515 | 1 | 2220 | 2 | 0 | PCS Comm Parameters 1 | Software Fault - DC Path RMS Imbalance | Float |  | 0, Normal; 1, Fault | 1 | 1
test | 515 | 1 | 2222 | 2 | 0 | PCS Comm Parameters 1 | Software Fault - AC Voltage Imbalance Fault | Float |  | 0, Normal; 1, Fault | 1 | 1
test | 515 | 1 | 2224 | 2 | 0 | PCS Comm Parameters 1 | Software Alarm - Parameter Upgrade Fault | Float |  | 0, Normal; 1, Fault | 1 | 1
test | 515 | 1 | 2226 | 2 | 0 | PCS Comm Parameters 1 | Software Fault - F-RAM Chip Fault | Float |  | 0, Normal; 1, Fault | 1 | 1
test | 515 | 1 | 2228 | 2 | 0 | PCS Comm Parameters 1 | Hardware Fault - Fuse Blown | Float |  | 0, Normal; 1, Fault | 1 | 1
test | 515 | 1 | 2230 | 2 | 0 | PCS Comm Parameters 1 | Software Fault - Fiber Optic Comm Fault | Float |  | 0, Normal; 1, Fault | 1 | 1
test | 515 | 1 | 2232 | 2 | 0 | PCS Comm Parameters 1 | Software Fault - Battery Software Overvoltage | Float |  | 0, Normal; 1, Fault | 1 | 1
test | 515 | 1 | 2234 | 2 | 0 | PCS Comm Parameters 1 | Software Fault - Battery Software Undervoltage | Float |  | 0, Normal; 1, Fault | 1 | 1
test | 515 | 1 | 2236 | 2 | 0 | PCS Comm Parameters 1 | Software Fault - Bus Voltage Imbalance | Float |  | 0, Normal; 1, Fault | 1 | 1
test | 515 | 1 | 2238 | 2 | 0 | PCS Comm Parameters 1 | Software Fault - Half Bus Overvoltage | Float |  | 0, Normal; 1, Fault | 1 | 1
test | 515 | 1 | 2240 | 2 | 0 | PCS Comm Parameters 1 | Software Fault - Internal Comm Offline | Float |  | 0, Normal; 1, Fault | 1 | 1
test | 515 | 1 | 2242 | 2 | 0 | PCS Comm Parameters 1 | Leakage Current Over-Limit Protection | Float |  | 0, Normal; 1, Fault | 1 | 1
test | 515 | 1 | 2244 | 2 | 0 | PCS Comm Parameters 1 | Hardware Fault - Zero Drift | Float |  | 0, Normal; 1, Fault | 1 | 1
test | 515 | 1 | 2246 | 2 | 0 | PCS Comm Parameters 1 | Hardware Fault - DC Soft Start Fault | Float |  | 0, Normal; 1, Fault | 1 | 1
test | 515 | 1 | 2248 | 2 | 0 | PCS Comm Parameters 1 | Hardware Fault - AC Overcurrent | Float |  | 0, Normal; 1, Fault | 1 | 1
test | 515 | 1 | 2250 | 2 | 0 | PCS Comm Parameters 1 | Software Fault - AC Overcurrent | Float |  | 0, Normal; 1, Fault | 1 | 1
test | 515 | 1 | 2252 | 2 | 0 | PCS Comm Parameters 1 | Hardware Fault - Half Bus Overvoltage | Float |  | 0, Normal; 1, Fault | 1 | 1
test | 515 | 1 | 2254 | 2 | 0 | PCS Comm Parameters 1 | Hardware Fault - DC Overvoltage | Float |  | 0, Normal; 1, Fault | 1 | 1
test | 515 | 1 | 2256 | 2 | 0 | PCS Comm Parameters 1 | Hardware Fault - AC Soft Start Fault | Float |  | 0, Normal; 1, Fault | 1 | 1
test | 515 | 1 | 2258 | 2 | 0 | PCS Comm Parameters 1 | Software Fault - ARM Internal Comm Fault | Float |  | 0, Normal; 1, Fault | 1 | 1
test | 515 | 1 | 2260 | 2 | 0 | PCS Comm Parameters 1 | Software Fault - ARM EMS Comm Fault | Float |  | 0, Normal; 1, Fault | 1 | 1
test | 515 | 1 | 2262 | 2 | 0 | PCS Comm Parameters 1 | Software Fault - ARM SPI Fault Recorder Comm Fault | Float |  | 0, Normal; 1, Fault | 1 | 1
test | 515 | 1 | 2264 | 2 | 0 | PCS Comm Parameters 1 | Software Fault - ARM SD Card Fault | Float |  | 0, Normal; 1, Fault | 1 | 1
test | 515 | 1 | 2266 | 2 | 0 | PCS Comm Parameters 1 | Software Fault - ARM RTC Fault | Float |  | 0, Normal; 1, Fault | 1 | 1
test | 515 | 1 | 2268 | 2 | 0 | PCS Comm Parameters 1 | Software Fault - ARM Internal Comm Protocol Version Mismatch | Float |  | 0, Normal; 1, Fault | 1 | 1
test | 515 | 1 | 2270 | 2 | 0 | PCS Comm Parameters 1 | Software Fault - ARM COM1 Ethernet Comm Fault | Float |  | 0, Normal; 1, Fault | 1 | 1
test | 515 | 1 | 2272 | 2 | 0 | PCS Comm Parameters 1 | Software Fault - ARM Emergency Stop Input Feedback | Float |  | 0, Normal; 1, Fault | 1 | 1
test | 515 | 1 | 2274 | 2 | 0 | PCS Comm Parameters 1 | Software Fault - ARM BMS Dry Contact Signal Feedback | Float |  | 0, Normal; 1, Fault | 1 | 1
test | 515 | 1 | 2276 | 2 | 0 | PCS Comm Parameters 1 | Software Fault - ARM Yingbo STS Switch Thyristor Over-Temp | Float |  | 0, Normal; 1, Fault | 1 | 1
test | 515 | 1 | 2278 | 2 | 0 | PCS Comm Parameters 1 | BMS Comm Fault | Float |  | 0, Normal; 1, Fault | 1 | 1
test | 515 | 1 | 2280 | 2 | 0 | PCS Comm Parameters 1 | BMS Temperature Abnormal | Float |  | 0, Normal; 1, Fault | 1 | 1
test | 515 | 1 | 2282 | 2 | 0 | PCS Comm Parameters 1 | BMS Trip | Float |  | 0, Normal; 1, Fault | 1 | 1
test | 515 | 1 | 2284 | 2 | 0 | PCS Comm Parameters 1 | BMS Battery Alarm | Float |  | 0, Normal; 1, Fault | 1 | 1
test | 515 | 1 | 2286 | 2 | 0 | PCS Comm Parameters 1 | Software Emergency Stop Fault Feedback | Float |  | 0, Normal; 1, Fault | 1 | 1
test | 515 | 1 | 2288 | 2 | 0 | Utility Meter Comm Parameters | Comm Status | Float |  | 0, Offline; 1, Online | 0 | 1
test | 515 | 1 | 2290 | 2 | 0 | Utility Meter Comm Parameters | A-Phase Voltage | Float | V |  | 0 | 1
test | 515 | 1 | 2292 | 2 | 0 | Utility Meter Comm Parameters | B-Phase Voltage | Float | V |  | 0 | 1
test | 515 | 1 | 2294 | 2 | 0 | Utility Meter Comm Parameters | C-Phase Voltage | Float | V |  | 0 | 1
test | 515 | 1 | 2296 | 2 | 0 | Utility Meter Comm Parameters | AB Line Voltage | Float | V |  | 0 | 1
test | 515 | 1 | 2298 | 2 | 0 | Utility Meter Comm Parameters | BC Line Voltage | Float | V |  | 0 | 1
test | 515 | 1 | 2300 | 2 | 0 | Utility Meter Comm Parameters | CA Line Voltage | Float | V |  | 0 | 1
test | 515 | 1 | 2302 | 2 | 0 | Utility Meter Comm Parameters | A-Phase Current | Float | A |  | 0 | 1
test | 515 | 1 | 2304 | 2 | 0 | Utility Meter Comm Parameters | B-Phase Current | Float | A |  | 0 | 1
test | 515 | 1 | 2306 | 2 | 0 | Utility Meter Comm Parameters | C-Phase Current | Float | A |  | 0 | 1
test | 515 | 1 | 2308 | 2 | 0 | Utility Meter Comm Parameters | N-Line Current | Float | A |  | 0 | 1
test | 515 | 1 | 2310 | 2 | 0 | Utility Meter Comm Parameters | A-Phase Active Power | Float | kW |  | 0 | 1
test | 515 | 1 | 2312 | 2 | 0 | Utility Meter Comm Parameters | B-Phase Active Power | Float | kW |  | 0 | 1
test | 515 | 1 | 2314 | 2 | 0 | Utility Meter Comm Parameters | C-Phase Active Power | Float | kW |  | 0 | 1
test | 515 | 1 | 2316 | 2 | 0 | Utility Meter Comm Parameters | Total Active Power | Float | kW |  | 0 | 1
test | 515 | 1 | 2318 | 2 | 0 | Utility Meter Comm Parameters | A-Phase Reactive Power | Float | kvar |  | 0 | 1
test | 515 | 1 | 2320 | 2 | 0 | Utility Meter Comm Parameters | B-Phase Reactive Power | Float | kvar |  | 0 | 1
test | 515 | 1 | 2322 | 2 | 0 | Utility Meter Comm Parameters | C-Phase Reactive Power | Float | kvar |  | 0 | 1
test | 515 | 1 | 2324 | 2 | 0 | Utility Meter Comm Parameters | Total Reactive Power | Float | kvar |  | 0 | 1
test | 515 | 1 | 2326 | 2 | 0 | Utility Meter Comm Parameters | A-Phase Apparent Power | Float | kVA |  | 0 | 1
test | 515 | 1 | 2328 | 2 | 0 | Utility Meter Comm Parameters | B-Phase Apparent Power | Float | kVA |  | 0 | 1
test | 515 | 1 | 2330 | 2 | 0 | Utility Meter Comm Parameters | C-Phase Apparent Power | Float | kVA |  | 0 | 1
test | 515 | 1 | 2332 | 2 | 0 | Utility Meter Comm Parameters | Total Apparent Power | Float | kVA |  | 0 | 1
test | 515 | 1 | 2334 | 2 | 0 | Utility Meter Comm Parameters | A-Phase Power Factor | Float |  |  | 0 | 1
test | 515 | 1 | 2336 | 2 | 0 | Utility Meter Comm Parameters | B-Phase Power Factor | Float |  |  | 0 | 1
test | 515 | 1 | 2338 | 2 | 0 | Utility Meter Comm Parameters | C-Phase Power Factor | Float |  |  | 0 | 1
test | 515 | 1 | 2340 | 2 | 0 | Utility Meter Comm Parameters | Total Power Factor | Float |  |  | 0 | 1
test | 515 | 1 | 2342 | 2 | 0 | Utility Meter Comm Parameters | Frequency | Float | Hz |  | 0 | 1
test | 515 | 1 | 2344 | 2 | 0 | Utility Meter Comm Parameters | Reserved Phase Voltage Average | Float | V |  | 0 | 1
test | 515 | 1 | 2346 | 2 | 0 | Utility Meter Comm Parameters | Reserved Line Voltage Average | Float | V |  | 0 | 1
test | 515 | 1 | 2348 | 2 | 0 | Utility Meter Comm Parameters | Reserved Current Average | Float | V |  | 0 | 1
test | 515 | 1 | 2350 | 2 | 0 | Utility Meter Comm Parameters | Voltage Unbalance | Float | ％ |  | 0 | 1
test | 515 | 1 | 2352 | 2 | 0 | Utility Meter Comm Parameters | Current Unbalance | Float | ％ |  | 0 | 1
test | 515 | 1 | 2354 | 2 | 0 | Utility Meter Comm Parameters | Reserved Zero-Sequence Voltage | Float | V |  | 0 | 1
test | 515 | 1 | 2356 | 2 | 0 | Utility Meter Comm Parameters | Reserved Zero-Sequence Current | Float | A |  | 0 | 1
test | 515 | 1 | 2358 | 2 | 0 | Utility Meter Comm Parameters | Reserved A Power Angle | Float | ° |  | 0 | 1
test | 515 | 1 | 2360 | 2 | 0 | Utility Meter Comm Parameters | Reserved B Power Angle | Float | ° |  | 0 | 1
test | 515 | 1 | 2362 | 2 | 0 | Utility Meter Comm Parameters | Reserved C Power Angle | Float | ° |  | 0 | 1
test | 515 | 1 | 2364 | 2 | 0 | Utility Meter Comm Parameters | A Voltage Angle | Float | ° |  | 0 | 1
test | 515 | 1 | 2366 | 2 | 0 | Utility Meter Comm Parameters | B Voltage Angle | Float | ° |  | 0 | 1
test | 515 | 1 | 2368 | 2 | 0 | Utility Meter Comm Parameters | C Voltage Angle | Float | ° |  | 0 | 1
test | 515 | 1 | 2370 | 2 | 0 | Utility Meter Comm Parameters | A Current Angle | Float | ° |  | 0 | 1
test | 515 | 1 | 2372 | 2 | 0 | Utility Meter Comm Parameters | B Current Angle | Float | ° |  | 0 | 1
test | 515 | 1 | 2374 | 2 | 0 | Utility Meter Comm Parameters | C Current Angle | Float | ° |  | 0 | 1
test | 515 | 1 | 2376 | 2 | 0 | Utility Meter Comm Parameters | Reserved Internal Temperature | Float | ℃ |  | 0 | 1
test | 515 | 1 | 2378 | 2 | 0 | Utility Meter Comm Parameters | Temperature 1 | Float | ℃ |  | 0 | 1
test | 515 | 1 | 2380 | 2 | 0 | Utility Meter Comm Parameters | Temperature 2 | Float | ℃ |  | 0 | 1
test | 515 | 1 | 2382 | 2 | 0 | Utility Meter Comm Parameters | Temperature 3 | Float | ℃ |  | 0 | 1
test | 515 | 1 | 2384 | 2 | 0 | Utility Meter Comm Parameters | Temperature 4 | Float | ℃ |  | 0 | 1
test | 515 | 1 | 2386 | 2 | 0 | Utility Meter Comm Parameters | Leakage Current 1 | Float | A |  | 0 | 1
test | 515 | 1 | 2388 | 2 | 0 | Utility Meter Comm Parameters | Total Active Energy | Float | kWh |  | 0 | 1
test | 515 | 1 | 2390 | 2 | 0 | Utility Meter Comm Parameters | Forward Total Active Energy | Float | kWh |  | 0 | 1
test | 515 | 1 | 2392 | 2 | 0 | Utility Meter Comm Parameters | Reverse Total Active Energy | Float | kWh |  | 0 | 1
test | 515 | 1 | 2394 | 2 | 0 | Utility Meter Comm Parameters | Overvoltage Alarm | Float |  | 0, Normal; 1, Alarm | 0 | 1
test | 515 | 1 | 2396 | 2 | 0 | Utility Meter Comm Parameters | Undervoltage Alarm | Float |  | 0, Normal; 1, Alarm | 0 | 1
test | 515 | 1 | 2398 | 2 | 0 | Utility Meter Comm Parameters | Overcurrent Alarm | Float |  | 0, Normal; 1, Alarm | 0 | 1
test | 515 | 1 | 2400 | 2 | 0 | Utility Meter Comm Parameters | Undercurrent Alarm | Float |  | 0, Normal; 1, Alarm | 0 | 1
test | 515 | 1 | 2402 | 2 | 0 | Utility Meter Comm Parameters | Overpower Alarm | Float |  | 0, Normal; 1, Alarm | 0 | 1
test | 515 | 1 | 2404 | 2 | 0 | Utility Meter Comm Parameters | Underpower Alarm | Float |  | 0, Normal; 1, Alarm | 0 | 1
test | 515 | 1 | 2406 | 2 | 0 | Utility Meter Comm Parameters | DO1 Alarm Output | Float |  | 0, Normal; 1, Alarm | 0 | 1
test | 515 | 1 | 2408 | 2 | 0 | Utility Meter Comm Parameters | DO2 Alarm Output | Float |  | 0, Normal; 1, Alarm | 0 | 1
test | 515 | 1 | 2410 | 2 | 0 | Utility Meter Comm Parameters | A-Phase Current Loss Alarm | Float |  | 0, Normal; 1, Alarm | 0 | 1
test | 515 | 1 | 2412 | 2 | 0 | Utility Meter Comm Parameters | B-Phase Current Loss Alarm | Float |  | 0, Normal; 1, Alarm | 0 | 1
test | 515 | 1 | 2414 | 2 | 0 | Utility Meter Comm Parameters | C-Phase Current Loss Alarm | Float |  | 0, Normal; 1, Alarm | 0 | 1
test | 515 | 1 | 2416 | 2 | 0 | Utility Meter Comm Parameters | A-Phase Voltage Loss Alarm | Float |  | 0, Normal; 1, Alarm | 0 | 1
test | 515 | 1 | 2418 | 2 | 0 | Utility Meter Comm Parameters | B-Phase Voltage Loss Alarm | Float |  | 0, Normal; 1, Alarm | 0 | 1
test | 515 | 1 | 2420 | 2 | 0 | Utility Meter Comm Parameters | C-Phase Voltage Loss Alarm | Float |  | 0, Normal; 1, Alarm | 0 | 1
test | 515 | 1 | 2422 | 2 | 0 | Utility Meter Comm Parameters | Phase Sequence Error Alarm | Float |  | 0, Normal; 1, Alarm | 0 | 1
test | 515 | 1 | 2424 | 2 | 0 | Utility Meter Comm Parameters | Power Loss Report | Float |  | 0: Invalid; 1: Valid | 0 | 1
test | 515 | 1 | 2426 | 2 | 0 | Fire Protection Comm Parameters | Comm Status | Float |  | 0, Offline; 1, Online | 0 | 1
test | 515 | 1 | 2428 | 2 | 0 | Fire Protection Comm Parameters | Fault - CO | Float |  | 0, Normal; 1, Alarm | 0 | 1
test | 515 | 1 | 2430 | 2 | 0 | Fire Protection Comm Parameters | Fault - Temperature | Float |  | 0, Normal; 1, Alarm | 0 | 1
test | 515 | 1 | 2432 | 2 | 0 | Fire Protection Comm Parameters | Fault - Start | Float |  | 0, Normal; 1, Alarm | 0 | 1
test | 515 | 1 | 2434 | 2 | 0 | Fire Protection Comm Parameters | Fault - Feedback | Float |  | 0, Normal; 1, Alarm | 0 | 1
test | 515 | 1 | 2436 | 2 | 0 | Fire Protection Comm Parameters | Fault - Infrared | Float |  | 0, Normal; 1, Alarm | 0 | 1
test | 515 | 1 | 2438 | 2 | 0 | Fire Protection Comm Parameters | Fire Alarm - CO | Float |  | 0, Normal; 1, Alarm | 0 | 1
test | 515 | 1 | 2440 | 2 | 0 | Fire Protection Comm Parameters | Fire Alarm - Temperature | Float |  | 0, Normal; 1, Alarm | 0 | 1
test | 515 | 1 | 2442 | 2 | 0 | Fire Protection Comm Parameters | Fire Alarm - Start | Float |  | 0, Normal; 1, Alarm | 0 | 1
test | 515 | 1 | 2444 | 2 | 0 | Fire Protection Comm Parameters | Fire Alarm - Feedback | Float |  | 0: Normal; 1: Feedback | 0 | 1
test | 515 | 1 | 2446 | 2 | 0 | Fire Protection Comm Parameters | Fire Alarm - Infrared | Float |  | 0, Normal; 1, Alarm | 0 | 1
test | 515 | 1 | 2448 | 2 | 0 | Fire Protection Comm Parameters | Temperature Value | Float | ℃ |  | 0 | 1
test | 515 | 1 | 2450 | 2 | 0 | Fire Protection Comm Parameters | CO1 | Float |  |  | 0 | 1
test | 515 | 1 | 2452 | 2 | 0 | Fire Protection Comm Parameters | CO2 | Float |  |  | 0 | 1
test | 515 | 1 | 2454 | 2 | 0 | Fire Protection Comm Parameters | CO3 | Float |  |  | 0 | 1
test | 515 | 1 | 2456 | 2 | 0 | Fire Protection Comm Parameters | Infrared High | Float |  |  | 0 | 1
test | 515 | 1 | 2458 | 2 | 0 | Fire Protection Comm Parameters | Infrared Low | Float |  |  | 0 | 1
test | 515 | 1 | 2460 | 2 | 0 | Fire Protection Comm Parameters | Fault | Float |  | 0, No Fault; 1, Extinguisher Activated; 2, Sensor Fault; 3, Two or More Alarms | 0 | 1
test | 515 | 1 | 2462 | 2 | 0 | Fire Protection Comm Parameters | Fire Alarm | Float |  | 0, No Fire Alarm; 1, CO Fire Alarm; 2, Temperature Fire Alarm; 3, Two or More Fire Alarms; 4, Extinguisher Activated | 0 | 1
test | 515 | 1 | 2464 | 2 | 0 | Fire Protection Comm Parameters | Fan Damper Control Module - Fire Alarm | Float |  | 0, Normal; 1, Alarm | 0 | 1
test | 515 | 1 | 2466 | 2 | 0 | Fire Protection Comm Parameters | Fan Damper Control Module - Status | Float |  | 0, Stop; 8, Start | 0 | 1
test | 515 | 1 | 2468 | 2 | 0 | Fire Protection Comm Parameters | Audible/Visual Alarm Module - Fire Alarm | Float |  | 0, Normal; 1, Alarm | 0 | 1
test | 515 | 1 | 2470 | 2 | 0 | Fire Protection Comm Parameters | Audible/Visual Alarm Module - Status | Float |  | 0, Stop; 8, Start | 0 | 1
test | 515 | 1 | 2472 | 2 | 0 | Liquid Cooling Comm Parameters | Online Points | Float |  | 0, Offline; 1, Online | 0 | 1
test | 515 | 1 | 2474 | 2 | 0 | Liquid Cooling Comm Parameters | Start/Stop | Float |  | 0, Shutdown; 1, Start | 0 | 1
test | 515 | 1 | 2476 | 2 | 0 | Liquid Cooling Comm Parameters | Water Temp Control Target | Float |  | 0, Outlet Water Temp; 1, Inlet Water Temp | 0 | 1
test | 515 | 1 | 2478 | 2 | 0 | Liquid Cooling Comm Parameters | Outlet High-Pressure Alarm Value | Float | Bar |  | 0 | 1
test | 515 | 1 | 2480 | 2 | 0 | Liquid Cooling Comm Parameters | Inlet Low-Pressure Alarm Value | Float | Bar |  | 0 | 1
test | 515 | 1 | 2482 | 2 | 0 | Liquid Cooling Comm Parameters | Outlet High-Temp Alarm Value | Float | ℃ |  | 0 | 1
test | 515 | 1 | 2484 | 2 | 0 | Liquid Cooling Comm Parameters | Outlet Low-Temp Alarm Value | Float | ℃ |  | 0 | 1
test | 515 | 1 | 2486 | 2 | 0 | Liquid Cooling Comm Parameters | Working Mode | Float |  | 0, Chiller Control; 1, Temp Monitoring; 2, Monitoring Mode; 3, Full-Speed Cooling | 0 | 1
test | 515 | 1 | 2488 | 2 | 0 | Liquid Cooling Comm Parameters | Cooling Setpoint Temperature | Float | ℃ |  | 0 | 1
test | 515 | 1 | 2490 | 2 | 0 | Liquid Cooling Comm Parameters | Heating Setpoint Temperature | Float | ℃ |  | 0 | 1
test | 515 | 1 | 2492 | 2 | 0 | Liquid Cooling Comm Parameters | Cooling Battery Max Temperature | Float | ℃ |  | 0 | 1
test | 515 | 1 | 2494 | 2 | 0 | Liquid Cooling Comm Parameters | Cooling Battery Avg Temperature | Float | ℃ |  | 0 | 1
test | 515 | 1 | 2496 | 2 | 0 | Liquid Cooling Comm Parameters | Cooling Battery Temp Differential | Float | ℃ |  | 0 | 1
test | 515 | 1 | 2498 | 2 | 0 | Liquid Cooling Comm Parameters | Heating Battery Min Temperature | Float | ℃ |  | 0 | 1
test | 515 | 1 | 2500 | 2 | 0 | Liquid Cooling Comm Parameters | Heating Battery Avg Temperature | Float | ℃ |  | 0 | 1
test | 515 | 1 | 2502 | 2 | 0 | Liquid Cooling Comm Parameters | Heating Battery Temp Differential | Float | ℃ |  | 0 | 1
test | 515 | 1 | 2504 | 2 | 0 | Liquid Cooling Comm Parameters | Monitoring Mode | Float |  | 0, Shutdown; 1, Cooling; 2, Heating; 3, Self-Circulation; 4, Standby | 0 | 1
test | 515 | 1 | 2506 | 2 | 0 | Liquid Cooling Comm Parameters | Inlet Water Temperature | Float | ℃ |  | 0 | 1
test | 515 | 1 | 2508 | 2 | 0 | Liquid Cooling Comm Parameters | Outlet Water Temperature | Float | ℃ |  | 0 | 1
test | 515 | 1 | 2510 | 2 | 0 | Liquid Cooling Comm Parameters | Inlet/Outlet Water Pressure Diff | Float | ℃ |  | 0 | 1
test | 515 | 1 | 2512 | 2 | 0 | Liquid Cooling Comm Parameters | Inlet/Outlet Water Temperature Diff | Float | ℃ |  | 0 | 1
test | 515 | 1 | 2514 | 2 | 0 | Liquid Cooling Comm Parameters | Inlet Water Pressure | Float | Bar |  | 0 | 1
test | 515 | 1 | 2516 | 2 | 0 | Liquid Cooling Comm Parameters | Outlet Water Pressure | Float | Bar |  | 0 | 1
test | 515 | 1 | 2518 | 2 | 0 | Liquid Cooling Comm Parameters | Outdoor Temperature | Float | ℃ |  | 0 | 1
test | 515 | 1 | 2520 | 2 | 0 | Liquid Cooling Comm Parameters | System Cooling Demand | Float | ℃ |  | 0 | 1
test | 515 | 1 | 2522 | 2 | 0 | Liquid Cooling Comm Parameters | System Heating Demand | Float | ℃ |  | 0 | 1
test | 515 | 1 | 2524 | 2 | 0 | Liquid Cooling Comm Parameters | Unit Working Mode | Float |  | 0, Self-Circulation; 1, Cooling; 2, Heating; 3, Standby | 0 | 1
test | 515 | 1 | 2526 | 2 | 0 | Liquid Cooling Comm Parameters | Unit Control Mode | Float |  | 0, Shutdown; 1, Self-Circulation; 2, Standby; 3, Cooling; 4, Heating; 5, Manual; 6, Vacuum Pumping; 7, Fault Shutdown; 8, Group Control Standby; 9, Remote Shutdown; 10, Auto Exhaust | 0 | 1
test | 515 | 1 | 2528 | 2 | 0 | Liquid Cooling Comm Parameters | Power Supply Overvoltage Alarm | Float |  | 0, Normal; 1, Alarm | 0 | 1
test | 515 | 1 | 2530 | 2 | 0 | Liquid Cooling Comm Parameters | Power Supply Undervoltage Alarm | Float |  | 0, Normal; 1, Alarm | 0 | 1
test | 515 | 1 | 2532 | 2 | 0 | Liquid Cooling Comm Parameters | Power Supply Phase Loss Alarm | Float |  | 0, Normal; 1, Alarm | 0 | 1
test | 515 | 1 | 2534 | 2 | 0 | Liquid Cooling Comm Parameters | Power Supply Phase Error Alarm | Float |  | 0, Normal; 1, Alarm | 0 | 1
test | 515 | 1 | 2536 | 2 | 0 | Liquid Cooling Comm Parameters | Switching Power Supply Fault | Float |  | 0, Normal; 1, Alarm | 0 | 1
test | 515 | 1 | 2538 | 2 | 0 | Liquid Cooling Comm Parameters | Electric Heater Protection Alarm | Float |  | 0, Normal; 1, Alarm | 0 | 1
test | 515 | 1 | 2540 | 2 | 0 | Liquid Cooling Comm Parameters | Smoke Alarm | Float |  | 0, Normal; 1, Alarm | 0 | 1
test | 515 | 1 | 2542 | 2 | 0 | Liquid Cooling Comm Parameters | Water Ingress Alarm | Float |  | 0, Normal; 1, Alarm | 0 | 1
test | 515 | 1 | 2544 | 2 | 0 | Liquid Cooling Comm Parameters | Low Water Flow Alarm | Float |  | 0, Normal; 1, Alarm | 0 | 1
test | 515 | 1 | 2546 | 2 | 0 | Liquid Cooling Comm Parameters | Water Tank Low Water Level Alarm | Float |  | 0, Normal; 1, Alarm | 0 | 1
test | 515 | 1 | 2548 | 2 | 0 | Liquid Cooling Comm Parameters | Water Flow Meter Comm Fault | Float |  | 0, Normal; 1, Alarm | 0 | 1
test | 515 | 1 | 2550 | 2 | 0 | Liquid Cooling Comm Parameters | Electric Heater Overload Alarm Latch | Float |  | 0, Normal; 1, Alarm | 0 | 1
test | 515 | 1 | 2552 | 2 | 0 | Liquid Cooling Comm Parameters | Meter Comm Fault | Float |  | 0, Normal; 1, Alarm | 0 | 1
test | 515 | 1 | 2554 | 2 | 0 | Liquid Cooling Comm Parameters | Group Control Comm Address Conflict | Float |  | 0, Normal; 1, Alarm | 0 | 1
test | 515 | 1 | 2556 | 2 | 0 | Liquid Cooling Comm Parameters | Group Control Network Comm Fault | Float |  | 0, Normal; 1, Alarm | 0 | 1
test | 515 | 1 | 2558 | 2 | 0 | Liquid Cooling Comm Parameters | Indoor Temp Probe Fault | Float |  | 0, Normal; 1, Alarm | 0 | 1
test | 515 | 1 | 2560 | 2 | 0 | Liquid Cooling Comm Parameters | Indoor Humidity Probe Fault | Float |  | 0, Normal; 1, Alarm | 0 | 1
test | 515 | 1 | 2562 | 2 | 0 | Liquid Cooling Comm Parameters | Inlet Water Temp Probe Fault | Float |  | 0, Normal; 1, Alarm | 0 | 1
test | 515 | 1 | 2564 | 2 | 0 | Liquid Cooling Comm Parameters | Outlet Water Temp Probe Fault | Float |  | 0, Normal; 1, Alarm | 0 | 1
test | 515 | 1 | 2566 | 2 | 0 | Liquid Cooling Comm Parameters | Inlet Water Pressure Probe Fault | Float |  | 0, Normal; 1, Alarm | 0 | 1
test | 515 | 1 | 2568 | 2 | 0 | Liquid Cooling Comm Parameters | Outlet Water Pressure Probe Fault | Float |  | 0, Normal; 1, Alarm | 0 | 1
test | 515 | 1 | 2570 | 2 | 0 | Liquid Cooling Comm Parameters | Inlet Water High-Temp Alarm | Float |  | 0, Normal; 1, Alarm | 0 | 1
test | 515 | 1 | 2572 | 2 | 0 | Liquid Cooling Comm Parameters | Inlet Water Low-Temp Alarm | Float |  | 0, Normal; 1, Alarm | 0 | 1
test | 515 | 1 | 2574 | 2 | 0 | Liquid Cooling Comm Parameters | Outlet Water High-Temp Alarm | Float |  | 0, Normal; 1, Alarm | 0 | 1
test | 515 | 1 | 2576 | 2 | 0 | Liquid Cooling Comm Parameters | Outlet Water Low-Temp Alarm | Float |  | 0, Normal; 1, Alarm | 0 | 1
test | 515 | 1 | 2578 | 2 | 0 | Liquid Cooling Comm Parameters | SPI Comm Fault | Float |  | 0, Normal; 1, Alarm | 0 | 1
test | 515 | 1 | 2580 | 2 | 0 | Liquid Cooling Comm Parameters | Outdoor Temp Probe Fault | Float |  | 0, Normal; 1, Alarm | 0 | 1
test | 515 | 1 | 2582 | 2 | 0 | Liquid Cooling Comm Parameters | Inlet/Outlet Temp Probe Reversed | Float |  | 0, Normal; 1, Alarm | 0 | 1
test | 515 | 1 | 2584 | 2 | 0 | Liquid Cooling Comm Parameters | Inlet/Outlet Pressure Probe Reversed | Float |  | 0, Normal; 1, Alarm | 0 | 1
test | 515 | 1 | 2586 | 2 | 0 | Liquid Cooling Comm Parameters | A/B System Suction/Discharge Temp Probe Wiring Abnormal | Float |  | 0, Normal; 1, Alarm | 0 | 1
test | 515 | 1 | 2588 | 2 | 0 | Liquid Cooling Comm Parameters | CAN Comm Fault | Float |  | 0, Normal; 1, Alarm | 0 | 1
test | 515 | 1 | 2590 | 2 | 0 | Liquid Cooling Comm Parameters | External Fan 1 Fault Latch | Float |  | 0, Normal; 1, Alarm | 0 | 1
test | 515 | 1 | 2592 | 2 | 0 | Liquid Cooling Comm Parameters | External Fan 2 Fault Latch | Float |  | 0, Normal; 1, Alarm | 0 | 1
test | 515 | 1 | 2594 | 2 | 0 | Liquid Cooling Comm Parameters | External Fan 3 Fault Latch | Float |  | 0, Normal; 1, Alarm | 0 | 1
test | 515 | 1 | 2596 | 2 | 0 | Liquid Cooling Comm Parameters | External Fan 4 Fault Latch | Float |  | 0, Normal; 1, Alarm | 0 | 1
test | 515 | 1 | 2598 | 2 | 0 | Liquid Cooling Comm Parameters | External Fan 5 Fault Latch | Float |  | 0, Normal; 1, Alarm | 0 | 1
test | 515 | 1 | 2600 | 2 | 0 | Liquid Cooling Comm Parameters | External Fan 6 Fault Latch | Float |  | 0, Normal; 1, Alarm | 0 | 1
test | 515 | 1 | 2602 | 2 | 0 | Liquid Cooling Comm Parameters | Inlet Low-Pressure Alarm | Float |  | 0, Normal; 1, Alarm | 0 | 1
test | 515 | 1 | 2604 | 2 | 0 | Liquid Cooling Comm Parameters | Outlet High-Pressure Alarm Latch | Float |  | 0, Normal; 1, Alarm | 0 | 1
test | 515 | 1 | 2606 | 2 | 0 | Liquid Cooling Comm Parameters | Remote RS485 Comm Fault | Float |  | 0, Normal; 1, Alarm | 0 | 1
test | 515 | 1 | 2608 | 2 | 0 | Liquid Cooling Comm Parameters | System A High-Pressure Alarm Latch | Float |  | 0, Normal; 1, Alarm | 0 | 1
test | 515 | 1 | 2610 | 2 | 0 | Liquid Cooling Comm Parameters | System A Low-Pressure Alarm Latch | Float |  | 0, Normal; 1, Alarm | 0 | 1
test | 515 | 1 | 2612 | 2 | 0 | Liquid Cooling Comm Parameters | System A High-Pressure Switch Fault | Float |  | 0, Normal; 1, Alarm | 0 | 1
test | 515 | 1 | 2614 | 2 | 0 | Liquid Cooling Comm Parameters | System A Low-Pressure Switch Fault | Float |  | 0, Normal; 1, Alarm | 0 | 1
test | 515 | 1 | 2616 | 2 | 0 | Liquid Cooling Comm Parameters | System A Discharge High-Temp Latch | Float |  | 0, Normal; 1, Alarm | 0 | 1
test | 515 | 1 | 2618 | 2 | 0 | Liquid Cooling Comm Parameters | System A Liquid Pipe Temp Sensor Fault | Float |  | 0, Normal; 1, Alarm | 0 | 1
test | 515 | 1 | 2620 | 2 | 0 | Liquid Cooling Comm Parameters | System A Discharge Temp Probe Fault | Float |  | 0, Normal; 1, Alarm | 0 | 1
test | 515 | 1 | 2622 | 2 | 0 | Liquid Cooling Comm Parameters | System A Suction Temp Probe Fault | Float |  | 0, Normal; 1, Alarm | 0 | 1
test | 515 | 1 | 2624 | 2 | 0 | Liquid Cooling Comm Parameters | System A Suction Pressure Probe Fault | Float |  | 0, Normal; 1, Alarm | 0 | 1
test | 515 | 1 | 2626 | 2 | 0 | Liquid Cooling Comm Parameters | System A Discharge Pressure Probe Fault | Float |  | 0, Normal; 1, Alarm | 0 | 1
test | 515 | 1 | 2628 | 2 | 0 | Liquid Cooling Comm Parameters | System A Refrigerant Leak or Insufficient | Float |  | 0, Normal; 1, Alarm | 0 | 1
test | 515 | 1 | 2630 | 2 | 0 | Liquid Cooling Comm Parameters | System A Suction/Discharge Temp Probe Wiring Abnormal | Float |  | 0, Normal; 1, Alarm | 0 | 1
test | 515 | 1 | 2632 | 2 | 0 | Liquid Cooling Comm Parameters | System A Compressor Comm Fault | Float |  | 0, Normal; 1, Alarm | 0 | 1
test | 515 | 1 | 2634 | 2 | 0 | Liquid Cooling Comm Parameters | System A Compressor Frequency Abnormal | Float |  | 0, Normal; 1, Alarm | 0 | 1
test | 515 | 1 | 2636 | 2 | 0 | Liquid Cooling Comm Parameters | System A Pump Comm Fault | Float |  | 0, Normal; 1, Alarm | 0 | 1
test | 515 | 1 | 2638 | 2 | 0 | Liquid Cooling Comm Parameters | System A Outdoor Unit Comm Fault | Float |  | 0, Normal; 1, Alarm | 0 | 1
test | 515 | 1 | 2640 | 2 | 0 | Liquid Cooling Comm Parameters | System A Compressor Drive Fault Alarm Latch | Float |  | 0, Normal; 1, Alarm | 0 | 1
test | 515 | 1 | 2642 | 2 | 0 | Liquid Cooling Comm Parameters | System A Outdoor Fan Drive Fault Alarm Latch | Float |  | 0, Normal; 1, Alarm | 0 | 1
test | 515 | 1 | 2644 | 2 | 0 | Liquid Cooling Comm Parameters | Circulation Pump 1 Drive Fault Alarm Latch | Float |  | 0, Normal; 1, Alarm | 0 | 1
test | 515 | 1 | 2646 | 2 | 0 | Liquid Cooling Comm Parameters | Circulation Pump 1 Overload Alarm | Float |  | 0, Normal; 1, Alarm | 0 | 1
test | 515 | 1 | 2648 | 2 | 0 | Liquid Cooling Comm Parameters | Circulation Pump 1 Overload Alarm Latch | Float |  | 0, Normal; 1, Alarm | 0 | 1
test | 515 | 1 | 2650 | 2 | 0 | Liquid Cooling Comm Parameters | System B High-Pressure Alarm Latch | Float |  | 0, Normal; 1, Alarm | 0 | 1
test | 515 | 1 | 2652 | 2 | 0 | Liquid Cooling Comm Parameters | System B Low-Pressure Alarm Latch | Float |  | 0, Normal; 1, Alarm | 0 | 1
test | 515 | 1 | 2654 | 2 | 0 | Liquid Cooling Comm Parameters | System B High-Pressure Switch Fault | Float |  | 0, Normal; 1, Alarm | 0 | 1
test | 515 | 1 | 2656 | 2 | 0 | Liquid Cooling Comm Parameters | System B Low-Pressure Switch Fault | Float |  | 0, Normal; 1, Alarm | 0 | 1
test | 515 | 1 | 2658 | 2 | 0 | Liquid Cooling Comm Parameters | System B Discharge High-Temp Alarm | Float |  | 0, Normal; 1, Alarm | 0 | 1
test | 515 | 1 | 2660 | 2 | 0 | Liquid Cooling Comm Parameters | System B Discharge High-Temp Latch | Float |  | 0, Normal; 1, Alarm | 0 | 1
test | 515 | 1 | 2662 | 2 | 0 | Liquid Cooling Comm Parameters | System B Liquid Pipe Temp Sensor Fault | Float |  | 0, Normal; 1, Alarm | 0 | 1
test | 515 | 1 | 2664 | 2 | 0 | Liquid Cooling Comm Parameters | System B Discharge Temp Probe Fault | Float |  | 0, Normal; 1, Alarm | 0 | 1
test | 515 | 1 | 2666 | 2 | 0 | Liquid Cooling Comm Parameters | System B Suction Temp Probe Fault | Float |  | 0, Normal; 1, Alarm | 0 | 1
test | 515 | 1 | 2668 | 2 | 0 | Liquid Cooling Comm Parameters | System B Suction Pressure Probe Fault | Float |  | 0, Normal; 1, Alarm | 0 | 1
test | 515 | 1 | 2670 | 2 | 0 | Liquid Cooling Comm Parameters | System B Discharge Pressure Probe Fault | Float |  | 0, Normal; 1, Alarm | 0 | 1
test | 515 | 1 | 2672 | 2 | 0 | Liquid Cooling Comm Parameters | System B Refrigerant Leak or Insufficient | Float |  | 0, Normal; 1, Alarm | 0 | 1
test | 515 | 1 | 2674 | 2 | 0 | Liquid Cooling Comm Parameters | System B Suction/Discharge Temp Probe Wiring Abnormal | Float |  | 0, Normal; 1, Alarm | 0 | 1
test | 515 | 1 | 2676 | 2 | 0 | Liquid Cooling Comm Parameters | System B Compressor Comm Fault | Float |  | 0, Normal; 1, Alarm | 0 | 1
test | 515 | 1 | 2678 | 2 | 0 | Liquid Cooling Comm Parameters | System B Compressor Frequency Abnormal | Float |  | 0, Normal; 1, Alarm | 0 | 1
test | 515 | 1 | 2680 | 2 | 0 | Liquid Cooling Comm Parameters | System B Pump Comm Fault | Float |  | 0, Normal; 1, Alarm | 0 | 1
test | 515 | 1 | 2682 | 2 | 0 | Liquid Cooling Comm Parameters | System B Outdoor Unit Comm Fault | Float |  | 0, Normal; 1, Alarm | 0 | 1
test | 515 | 1 | 2684 | 2 | 0 | Liquid Cooling Comm Parameters | System B Compressor Drive Fault Alarm Latch | Float |  | 0, Normal; 1, Alarm | 0 | 1
test | 515 | 1 | 2686 | 2 | 0 | Liquid Cooling Comm Parameters | System B Outdoor Fan Drive Fault Alarm Latch | Float |  | 0, Normal; 1, Alarm | 0 | 1
test | 515 | 1 | 2688 | 2 | 0 | Liquid Cooling Comm Parameters | Circulation Pump 2 Drive Fault Alarm Latch | Float |  | 0, Normal; 1, Alarm | 0 | 1
test | 515 | 1 | 2690 | 2 | 0 | Liquid Cooling Comm Parameters | Circulation Pump 2 Overload Alarm | Float |  | 0, Normal; 1, Alarm | 0 | 1
test | 515 | 1 | 2692 | 2 | 0 | Liquid Cooling Comm Parameters | Circulation Pump 2 Overload Alarm Latch | Float |  | 0, Normal; 1, Alarm | 0 | 1
test | 515 | 1 | 2694 | 2 | 0 | Liquid Cooling Comm Parameters | System A Compressor Frequency | Float | Hz |  | 0 | 1
test | 515 | 1 | 2696 | 2 | 0 | Liquid Cooling Comm Parameters | System B Compressor Frequency | Float | Hz |  | 0 | 1
test | 515 | 1 | 2698 | 2 | 0 | Remote Control | Remote Mode | Float |  | 0, Local; 1, Remote | 1 | 1
test | 515 | 1 | 2700 | 2 | 0 | Remote Control | Remote Control Mode | Float |  | 1, Shutdown; 2, Standby; 3, Charge; 4, Discharge | 1 | 1
test | 515 | 1 | 2702 | 2 | 0 | Remote Control | Remote Mode SOC Limit Enable | Float |  | 0, Disabled; 1, Enabled | 1 | 1
test | 515 | 1 | 2704 | 2 | 0 | Remote Control | Remote Mode Charge Cutoff SOC | Float | ％ |  | 1 | 1
test | 515 | 1 | 2706 | 2 | 0 | Remote Control | Remote Mode Discharge Cutoff SOC | Float | ％ |  | 1 | 1
test | 515 | 1 | 2708 | 2 | 0 | Remote Control | Period 1 - Start Hour | Float | h |  | 1 | 1
test | 515 | 1 | 2710 | 2 | 0 | Remote Control | Period 1 - Start Minute | Float | min |  | 1 | 1
test | 515 | 1 | 2712 | 2 | 0 | Remote Control | Period 1 - End Hour | Float | h |  | 1 | 1
test | 515 | 1 | 2714 | 2 | 0 | Remote Control | Period 1 - End Minute | Float | min |  | 1 | 1
test | 515 | 1 | 2716 | 2 | 0 | Remote Control | Period 1 Active Power | Float | kW |  | 1 | 1
test | 515 | 1 | 2718 | 2 | 0 | Remote Control | Period 2 - Start Hour | Float | h |  | 1 | 1
test | 515 | 1 | 2720 | 2 | 0 | Remote Control | Period 2 - Start Minute | Float | min |  | 1 | 1
test | 515 | 1 | 2722 | 2 | 0 | Remote Control | Period 2 - End Hour | Float | h |  | 1 | 1
test | 515 | 1 | 2724 | 2 | 0 | Remote Control | Period 2 - End Minute | Float | min |  | 1 | 1
test | 515 | 1 | 2726 | 2 | 0 | Remote Control | Period 2 Active Power | Float | kW |  | 1 | 1
test | 515 | 1 | 2728 | 2 | 0 | Remote Control | Period 3 - Start Hour | Float | h |  | 1 | 1
test | 515 | 1 | 2730 | 2 | 0 | Remote Control | Period 3 - Start Minute | Float | min |  | 1 | 1
test | 515 | 1 | 2732 | 2 | 0 | Remote Control | Period 3 - End Hour | Float | h |  | 1 | 1
test | 515 | 1 | 2734 | 2 | 0 | Remote Control | Period 3 - End Minute | Float | min |  | 1 | 1
test | 515 | 1 | 2736 | 2 | 0 | Remote Control | Period 3 Active Power | Float | kW |  | 1 | 1
test | 515 | 1 | 2738 | 2 | 0 | Remote Control | Period 4 - Start Hour | Float | h |  | 1 | 1
test | 515 | 1 | 2740 | 2 | 0 | Remote Control | Period 4 - Start Minute | Float | min |  | 1 | 1
test | 515 | 1 | 2742 | 2 | 0 | Remote Control | Period 4 - End Hour | Float | h |  | 1 | 1
test | 515 | 1 | 2744 | 2 | 0 | Remote Control | Period 4 - End Minute | Float | min |  | 1 | 1
test | 515 | 1 | 2746 | 2 | 0 | Remote Control | Period 4 Active Power | Float | kW |  | 1 | 1
test | 515 | 1 | 2748 | 2 | 0 | Remote Control | Period 5 - Start Hour | Float | h |  | 1 | 1
test | 515 | 1 | 2750 | 2 | 0 | Remote Control | Period 5 - Start Minute | Float | min |  | 1 | 1
test | 515 | 1 | 2752 | 2 | 0 | Remote Control | Period 5 - End Hour | Float | h |  | 1 | 1
test | 515 | 1 | 2754 | 2 | 0 | Remote Control | Period 5 - End Minute | Float | min |  | 1 | 1
test | 515 | 1 | 2756 | 2 | 0 | Remote Control | Period 5 Active Power | Float | kW |  | 1 | 1
test | 515 | 1 | 2758 | 2 | 0 | Remote Control | Period 6 - Start Hour | Float | h |  | 1 | 1
test | 515 | 1 | 2760 | 2 | 0 | Remote Control | Period 6 - Start Minute | Float | min |  | 1 | 1
test | 515 | 1 | 2762 | 2 | 0 | Remote Control | Period 6 - End Hour | Float | h |  | 1 | 1
test | 515 | 1 | 2764 | 2 | 0 | Remote Control | Period 6 - End Minute | Float | min |  | 1 | 1
test | 515 | 1 | 2766 | 2 | 0 | Remote Control | Period 6 Active Power | Float | kW |  | 1 | 1
test | 515 | 1 | 2768 | 2 | 0 | Remote Control | Period 7 - Start Hour | Float | h |  | 1 | 1
test | 515 | 1 | 2770 | 2 | 0 | Remote Control | Period 7 - Start Minute | Float | min |  | 1 | 1
test | 515 | 1 | 2772 | 2 | 0 | Remote Control | Period 7 - End Hour | Float | h |  | 1 | 1
test | 515 | 1 | 2774 | 2 | 0 | Remote Control | Period 7 - End Minute | Float | min |  | 1 | 1
test | 515 | 1 | 2776 | 2 | 0 | Remote Control | Period 7 Active Power | Float | kW |  | 1 | 1
test | 515 | 1 | 2778 | 2 | 0 | Remote Control | Period 8 - Start Hour | Float | h |  | 1 | 1
test | 515 | 1 | 2780 | 2 | 0 | Remote Control | Period 8 - Start Minute | Float | min |  | 1 | 1
test | 515 | 1 | 2782 | 2 | 0 | Remote Control | Period 8 - End Hour | Float | h |  | 1 | 1
test | 515 | 1 | 2784 | 2 | 0 | Remote Control | Period 8 - End Minute | Float | min |  | 1 | 1
test | 515 | 1 | 2786 | 2 | 0 | Remote Control | Period 8 Active Power | Float | kW |  | 1 | 1
test | 515 | 1 | 2788 | 2 | 0 | Remote Control | Period 9 - Start Hour | Float | h |  | 1 | 1
test | 515 | 1 | 2790 | 2 | 0 | Remote Control | Period 9 - Start Minute | Float | min |  | 1 | 1
test | 515 | 1 | 2792 | 2 | 0 | Remote Control | Period 9 - End Hour | Float | h |  | 1 | 1
test | 515 | 1 | 2794 | 2 | 0 | Remote Control | Period 9 - End Minute | Float | min |  | 1 | 1
test | 515 | 1 | 2796 | 2 | 0 | Remote Control | Period 9 Active Power | Float | kW |  | 1 | 1
test | 515 | 1 | 2798 | 2 | 0 | Remote Control | Period 10 - Start Hour | Float | h |  | 1 | 1
test | 515 | 1 | 2800 | 2 | 0 | Remote Control | Period 10 - Start Minute | Float | min |  | 1 | 1
test | 515 | 1 | 2802 | 2 | 0 | Remote Control | Period 10 - End Hour | Float | h |  | 1 | 1
test | 515 | 1 | 2804 | 2 | 0 | Remote Control | Period 10 - End Minute | Float | min |  | 1 | 1
test | 515 | 1 | 2806 | 2 | 0 | Remote Control | Period 10 Active Power | Float | kW |  | 1 | 1
test | 515 | 1 | 2808 | 2 | 0 | Remote Control | System Fault Reset | Float |  | 0, Normal; 1, Reset | 1 | 1
test | 515 | 1 | 2810 | 2 | 0 | Dehumidifier Comm Parameters | Online Points | Float |  | 0, Offline; 1, Online | 0 | 1
test | 515 | 1 | 2812 | 2 | 0 | Dehumidifier Comm Parameters | Working Mode | Float |  | 0, Cooling Type; 1, Heating Type | 0 | 1
test | 515 | 1 | 2814 | 2 | 0 | Dehumidifier Comm Parameters | Temperature Setpoint | Float | ℃ |  | 0 | 1
test | 515 | 1 | 2816 | 2 | 0 | Dehumidifier Comm Parameters | Temperature Differential | Float | ℃ |  | 0 | 1
test | 515 | 1 | 2818 | 2 | 0 | Dehumidifier Comm Parameters | Humidity Setpoint | Float | % |  | 0 | 1
test | 515 | 1 | 2820 | 2 | 0 | Dehumidifier Comm Parameters | Humidity Differential | Float | % |  | 0 | 1
test | 515 | 1 | 2822 | 2 | 0 | Dehumidifier Comm Parameters | Comm Address | Float |  |  | 0 | 1
test | 515 | 1 | 2824 | 2 | 0 | Dehumidifier Comm Parameters | Comm Baud Rate | Float |  |  | 0 | 1
test | 515 | 1 | 2826 | 2 | 0 | Dehumidifier Comm Parameters | Controller Internal Temperature | Float | ℃ |  | 0 | 1
test | 515 | 1 | 2828 | 2 | 0 | Dehumidifier Comm Parameters | Temperature Control Status | Float |  | 0, Off; 1, On | 0 | 1
test | 515 | 1 | 2830 | 2 | 0 | Dehumidifier Comm Parameters | Humidity Control Mode | Float |  | 0, Auto; 1, Manual | 0 | 1
test | 515 | 1 | 2832 | 2 | 0 | Dehumidifier Comm Parameters | Dehumidification Status | Float |  | 0, Stop; 1, Running | 0 | 1
test | 515 | 1 | 2834 | 2 | 0 | Dehumidifier Comm Parameters | Current Temperature | Float | ℃ |  | 0 | 1
test | 515 | 1 | 2836 | 2 | 0 | Dehumidifier Comm Parameters | Current Humidity | Float | % |  | 0 | 1
test | 515 | 1 | 2838 | 2 | 0 | Dehumidifier Comm Parameters | Alarm Status | Float |  | 0, Normal; 1, Alarm | 0 | 1
test | 515 | 1 | 2840 | 2 | 0 | Dehumidifier Comm Parameters | Dehumidification Switch Control Bit | Float |  | 0, On; 1, Off | 0 | 1