## Version
Reversion Record
Date | Version | Description | Editor | Auditor
2019-09-29 | V0 | Initial Version |  | wuhy
2020-04-13 | V1 | 1、IO list expanded to support 32 racks,0x1029-0x102f 2、Increase display content,0x100-0x111,0x2002,0x2009,0x2020-0x229f, |  | wuhy
2020-07-08 | V1.1 | 1、increase register 0x1030-0x1037 |  | wuhy
2020-08-26 | V1.2 | 1、increase register 0x1038-0x103A |  | wuhy
2021-12-17 | V1.3 | 1、增加参数配置 |  | wuhy
2023-03-18 | V2.0 | 重新梳理bms对外协议； |  | dfs
2023-04-04 | V2.1 | 1、修正部分地址； 2、Alarm地址部分； |  | dfs
2023-05-05 | V2.1.1 | 1、删除一个时间DB定义 2、删除最高单体电压 0x0231 3、缩进地址 4、增加NTP时区 5、增加最大读取寄存器数说明 |  | xlt
2023-05-22 | V2.2.1 | 1、增加均衡占空比； |  | dfs
2023-06-05 | V2.2.2 | 1、堆电流修改为32位； |  | zwq
2023-06-21 | V2.2.3 | 1.将堆信息分解成遥信/遥测/遥调/遥控 2.修改动环DB地址预留情况 |  | xzh
2023-06-26 | V2.2.4 | 1.调整簇遥信位置，将告警和故障的寄存器地址提前 2.将簇遥控信息里的遥调部分转移到遥调 |  | xzh
2023-07-18 | V2.2.5 | 1.调整“BMS系统故障汇总”BIT位定义 |  | xzh
2023-08-17 | V2.2.6 | 1、修改寄存器英文名 2、内部比特分行 3、添加use_number列 4、拆分部分一对多的寄存器（如一行number为4拆分成4行number为1） |  | tbh
2023-08-18 | V2.2.7 | 1.调整BMS对外告警故障汇总（external_fault_statu_sum），调整为一个地址，与内部DB同步 2.添加电流正负号说明 |  | xzh
2023-08-22 | V2.2.8 | 1.调整"Rack启用/停用状态","RACK 在线状态"高低位地址 |  | xzh
2023-08-22 | V2.2.9 | 1.动环信息拆分多表 2.校正部分对外地址 |  | tbh
2023-09-13 | V2.2.10 | 1.增加热失控相关寄存器 |  | xzh
2023-09-20 | V2.2.11 | 1.添加堆阈值配置 |  | xzh
2023-09-21 | V2.2.12 | 1.添加单DB形式的时间DB,一般项目部使用单个寄存器标识年月日时分秒，在核心板小板通信时会两两组合 |  | xzh
2023-10-24 | V2.2.13 | 1.增加复归对外地址 2.增加模组压差告警db |  | xzh
2023-10-24 | V2.2.14 | 1.添加簇间压差告警二级、三级阈值设置 2.增加BAU 一级、二级、三级、告警汇总 3.增加BAU所有簇告警汇总II的三级的寄存器（替换原有的预留寄存器） |  | xzh
2023-10-26 | V2.2.15 | 1.添加主控对外告警II,将新国标新增的模组压差，模组过压，模组欠压 2.添加最大限功率值配置 |  | xzh
2023-11-01 | V2.2.16 | 1.删除最大限功率配置 |  | xzh
2023-11-06 | V2.2.17 | 1.添加模组压差告警阈值寄存器 |  | xzh
2023-11-16 | V2.3.0 | 1.支持104串AFE采样配置，铜排配置 |  | xzh
2023-12-12 | V2.3.1 | 添加规范表，添加内部db列，根据规范修改列名， |  | tbh
2024-01-26 | V2.3.2 | 1.添加采样线故障状态 |  | xzh
2024-01-31 | V2.3.3 | 根据规范修改部分数值格式和数量，int16改为s16,十六进制改为十进制 |  | tbh
2024-03-24 | V2.3.4 | 修改BCU对外告警汇2总英文，与DB文档的对外告警汇2英文对应 |  | tbh
2024-04-18 | V2.3.5 | 部分寄存器英文名改为预留 |  | tbh
2024-04-25 | V2.3.6 | 对外的充放电功率对内DB映射索引标识(英文名)修改 |  | xzh
2024-05-07 | V2.3.7 | 添加电操控制失败告警相关DB |  | xzh
2024-05-23 | V2.3.8 | 添加高压箱温度故障 |  | xzh
2024-06-05 | V2.3.8 | 补充修改对外故障 |  | xzh
2024-07-17 | V2.3.9 | 远方就地模式修改映射地址 |  | xzh
2024-09-09 | V2.3.10 | 调整对外映射，删除diagsheet，修改一级和三级与新国标对齐 |  | xzh
2024-10-11 | V2.3.11 | 删掉了单体内阻，单体SOH,单体SOC,总控的热失控寄存器,统一了字体 |  | why
2024-10-18 | V2.3.12 | 将调试信息更改对外地址 |  | why
2024-11-22 | V2.3.13 | 调整PACK-极柱温度的个数 |  | why
2024-12-05 | V2.3.14 | 1.解决地址不连续，造成生成工具会报错的问题，补充预留个数 2.解决堆子网掩码地址不连续问题 |  | why
2024-12-05 | V2.3.15 | 1.添加can地址解析 |  | xzh
2024-12-25 | V2.3.15 | 修改簇间电流差告警阈值与恢复阈值的配置英文名 |  | xwj
2025/18 | V2.3.18 | 簇使能支持到128簇 |  | zwq
2025-05-28 | V2.3.19 | 修正簇间电流差一级、三级的告警阈值与恢复阈值的对外地址 |  | xwj
2025-05-30 | V2.3.20 | 将对外地址0x0234~0x0236改为预留，原始值模拟量不对外 |  | xzh
2025-06-03 | V2.3.21 | 新增充电单体压差过大、充电单体温差过大、充电模组压差过大 |  | xwj
2025-06-05 | V2.3.22 | 新增充总控里的主控对外预提示、主控里的对外预提示 |  | xwj
2025-06-06 | V2.3.23 | 修改充电单体压差过大、充电单体温差过大、充电模组压差过大的英文名 |  | xwj
2025-06-16 | V2.3.24 | 新增放电单体压差过大、放电单体温差过大、放电模组压差过大 |  | xwj
2025-06-23 | V2.3.25 | 预留的modbus点位的错误修改 |  | xwj
2025-06-27 | V2.3.26 | 修正对外预提示中的解析 |  | xwj
2025-07-10 | V2.3.27 | 修正总控db的数据格式 |  | xwj
2025-08-18 | V2.3.28 | 修正绝缘阻值过低告警阈值的单位，改为Ω/V |  | xwj
2025-08-18 | V2.3.29 | 文档修正，将电池组电压改为簇总压 |  | xwj
2025-08-21 | V2.3.29 | 适配60簇的 |  | xwj
2025-10-16 | V2.3.30 | 动环告警汇总优化区分设备层级 |  | xwj
2025-10-17 | V2.3.31 | 新增pack内温差过大告警 |  | xwj
2025-10-23 | V2.3.32 | 新增总控自检故障对外展示 |  | xwj
2025-11-06 | V2.3.33 | 文档修正,db文档适配对外协议生成工具 |  | xwj
2025-11-10 | V2.3.34 | 文档修正,db文档适配对外协议生成工具 |  | xwj
2025-11-12 | V2.3.35 | 文档修正，堆允许功率更改 |  | npj
2025-11-12 | V2.3.36 | 堆电流更改 |  | npj
2025-11-18 | V2.3.37 | 文档标准化修改 |  | npj
2025-11-21 | V2.3.38 | 簇1并网失败相关删除 |  | npj

## Define_Can
CAN ID定义 | [8 empty] | CAN报文8个数据说明
Bit28（1） | Bit27-Bit25（3） | Bit24-Bit19（6） |  | Bit18-Bit16（3） | Bit15-Bit0（16） |  |  |  | Byte1 | Byte2 | Byte3 | Byte4 | Byte5 | Byte6 | Byte7 | Byte8
固定值 | 设备类型 | 设备ID |  | 功能码 | 寄存器地址 |  |  |  | CAN报文8个数据说明 Byte1: 数据内容
1 | 011：BAU,代表EMS与BAU通信(三级架构使用) 010：BCU，代表EMS与BCU通信(二级架构使用) | 000000：BAU(设备类型为BCU时无效) 000001:BCU1 000010:BCU2 000011:BCU3 依次类推，BCU ID往后加1 111110：动环数据专用 111111：BCU广播ID |  | 001（写寄存器） | 要写的寄存器起始地址，每帧报文最多4个寄存器，大于4个寄存器，分多帧报文发送 |  |  |  | 寄存器1高位 | 寄存器1低位 | 寄存器2高位 | 寄存器2低位 | 寄存器3高位 | 寄存器3低位 | 寄存器4高位 | 寄存器4低位
|  |  |  | 010（写寄存器响应） | 该帧报文寄存器起始地址，每帧报文最多4个寄存器，大于4个寄存器，分多帧报文发送 |  |  |  | 寄存器1高位 | 寄存器1低位 | 寄存器2高位 | 寄存器2低位 | 寄存器3高位 | 寄存器3低位 | 寄存器4高位 | 寄存器4低位
|  |  |  | 011（读寄存器） | 要读的寄存器起始地址 |  |  |  | 寄存器数量高位 | 寄存器数量低位 | / | / | / | / | / | /
|  |  |  | 100（读寄存器响应） | 该帧报文寄存器起始地址，每帧报文最多4个寄存器，大于4个寄存器，分多帧报文发送 |  |  |  | 寄存器1高位 | 寄存器1低位 | 寄存器2高位 | 寄存器2低位 | 寄存器3高位 | 寄存器3低位 | 寄存器4高位 | 寄存器4低位
|  |  |  | 101（差错响应） |  |  |  |  | 寄存器高位 | 寄存器低位 | / | / | / | / | / | /
1 | 采用扩展帧格式，默认波特率500kbps;
2 | 协议采用主从式应答方式；一次建议最多读取256个寄存器
3 | 使用大端格式，即高字节在前低字节在后;
|  | 帧id |  |  |  |  | 数据data[1~8]
三级架构报文举例 | 数据帧类型 | Bit28（1） | Bit27-Bit25（3） | Bit24-Bit19（6） | Bit18-Bit16（3） | Bit15-Bit0（16） | Byte1 (寄存器数量高位 ) | Byte2 (寄存器数量低位 ) | Byte3 | Byte4 | Byte5 | Byte6 | Byte7 | Byte8
EMS与BAU通信，读取BAU内部Rack signal数据 | EMS发送 | [1] | [011] | [000001] | [011] | [‭0000 0000 0001 0000‬] | 0x00 | 0x20 | bar: CAN报文8个数据说明 Byte1 to CAN报文8个数据说明 Byte6
0x160B 0010 | bar: CAN报文8个数据说明 Byte1 to CAN报文8个数据说明 Byte6
| BAU响应 (多个寄存器返回，暂时只展示两条帧) | [1] | [011] | [000001] | [100] | [‭0000 0000 0001 0000‬] | 寄存器值高位 | 寄存器值低位 | 寄存器值高位 | 寄存器值低位 | 寄存器值高位 | 寄存器值低位 | 寄存器值高位 | 寄存器值低位
|  | 0x160C 0010 |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | [1] | [011] | [000001] | [100] | [‭0000 0000 0001 0100‬] | 寄存器值高位 | 寄存器值低位 | 寄存器值高位 | 寄存器值低位 | 寄存器值高位 | 寄存器值低位 | 寄存器值高位 | 寄存器值低位
|  | 0x160C 0014 |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0x160C 0018
依次类推
EMS与BAU通信，读取Bank Measure数据 | EMS发送 | [1] | [011] | [000000] | [011] | [‭0001 0000 0001 0001] | 0x00 | 0x22 | bar: CAN报文8个数据说明 Byte1 to CAN报文8个数据说明 Byte6
0x1603 1001 | bar: CAN报文8个数据说明 Byte1 to CAN报文8个数据说明 Byte6
| BAU响应 (多个寄存器返回，暂时只展示两条帧) | [1] | [011] | [000000] | [100] | [‭0001 0000 0001 0001] | 寄存器值高位 | 寄存器值低位 | 寄存器值高位 | 寄存器值低位 | 寄存器值高位 | 寄存器值低位 | 寄存器值高位 | 寄存器值低位
|  | 0x1604 1001 |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | [1] | [011] | [000000] | [100] | [‭0001 0000 0001 0101] | 寄存器值高位 | 寄存器值低位 | 寄存器值高位 | 寄存器值低位 | 寄存器值高位 | 寄存器值低位 | 寄存器值高位 | 寄存器值低位
|  | 0x1604 1005 |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
依次类推
EMS写堆遥控 （一键并网开关） | 写 | [1] | [011] | [000000] | [001] | [‭0011 0000 0011 0001‬] | 0x00 | 0x01 | bar: CAN报文8个数据说明 Byte1 to CAN报文8个数据说明 Byte6
0x1601 3001
| 写响应 | [1] | [011] | [000000] | [010] | [‭0011 0000 0011 0001‬] | 0x00 | 0x01 | bar: CAN报文8个数据说明 Byte1 to CAN报文8个数据说明 Byte6
0x1602 3001
注：寄存器地址参考"define"sheet中BAU和BCU的寄存器地址范围

## Define
Modbus功能码定义（BMSER使用部分）
代码 | 名称 | 作用
0x03 | 读取保持寄存器 | 在一个或多个保持寄存器中取得当前的二进制值
0x04 | 读取输入寄存器 | 在一个或多个输入寄存器中取得当前的二进制值
0x06 | 配置单寄存器 | 配置一个特定的二进制值到一个单寄存器中
0x10 | 配置多寄存器 | 配置一系列特定的二进制值到一系列多寄存器中
Modbus通讯协议定义
Write：
addr | Fun | Data start reg hi | Data start reg lo | D0 #of regs hi | D0 #of regs lo | Byte count | Value hi | Value lo
地址 | 功能码 | 寄存器起始地址高8位 | 寄存器起始地址低8位 | 寄存器数量高8位 | 寄存器数量低8位 | 字节数 | 数据高8位 | 数据低8位
Write Response:
addr | Fun | Data start reg hi | Data start reg lo | D0 #of regs hi | D0 #of regs lo | CRC16 hi | CRC16 lo
地址 | 功能码 | 寄存器起始地址高8位 | 寄存器起始地址低8位 | 寄存器数量高8位 | 寄存器数量低8位 | 校验高8位 | 校验低8位
Read:
addr | Fun | D0 addr hi | D0 addr lo | D0 #of regs hi | D0 #of regs lo | CRC16 hi | CRC16 lo
地址 | 功能码 | 寄存器起始地址高8位 | 寄存器起始地址低8位 | 寄存器数量高8位 | 寄存器数量低8位 | 校验高8位 | 校验低8位
Read Response
addr | Fun | Byte count | Data hi | Data lo | CRC16 hi | CRC16 lo
地址 | 功能码 | 字节数 | 数据位 | 数据位 | 校验高8位 | 校验低8位
ModbusTCP
ModbusTCP | MBAP |  |  |  | PDU
说明 | 事务处理标识 | 协议标识 | 长度 | 单元标识符 | modbus内容
长度 | 2字节 | 2字节 | 2字节 | 1字节 | N字节
说明 | 可以理解为报文的序列号，一般每次通信之后就要加1以区别不同的通信数据报文。 | 00 00表示ModbusTCP协议。 | 表示接下来的数据长度，单位为字节。全部的长度-6。 | 设备地址 | 功能码开始，不包含crc。
设备地址分配
设备类型 | BAU | BCU
设备地址范围 | 0x01 | 0x02-0x7E
设备类型 | BAU 动环 | BCU 动环
设备地址范围 | 0x7E +BAU ID | 0x7E +BCU ID
BAU | [7 empty] | ！！！应用说明！！！ 1、三级对外功能默认：BAU全部功能；BCU的Signal,Measure,Alarm，Control,Detail中的单体电压与温度；PowerEnv的全部功能；其它的功能选择开放； 2、二级多簇架构应用中，只能提供：虚拟BAU对外协议内容；BCU的Signal,Measure,Alarm，Control；PowerEnv的汇总以及单仓信息； 3、二级单簇架构应用中，只能提供：BCU的Signal,Measure,Alarm，Control,Detail中的单体电压与温度；PowerEnv的汇总以及单仓信息； 4、一次最大读取寄存器数 126(0x7E),超过126的需要分多次读取（Rack Detail）
设备地址 | 0x01
功能定义 | Bank Signal | Bank Measure | Bank Control | Bank Diag | Bank_Alarm Parameter Set & Read
modbus地址范围 | 0x1001-0x2000 | 0x2001-0x3000 | 0x3001-0x4000 | 0x4001-0x5000 | 0x5001-0x6000
支持功能码 | 0x03 0x04 0x10 0x06 | 0x03 0x04 | 0x03 0x04 0x10 0x06 | 0x03 0x04 0x10 0x06 | 0x03 0x04 0x10 0x06
BCU
设备地址 | 0x02-0x41
功能定义 | Rack Signal | Rack Measure | Rack Control | Rack Diag | Rack Detail | Rack_Alarm Parameter Set & Read | Balance Set & Read
modbus地址范围 | 0x0001-0x0200 | 0x0201-0x0400 | 0x0401-0x0800 | 0x0801-0x0B00 | 0x1000-0x6000 | 0x6001-0x7000 | 0x7000-0x8000
支持功能码 | 0x03 0x04 0x10 0x06 | 0x03 0x04 | 0x03 0x04 0x10 0x06 | 0x03 0x04 0x10 0x06 | 0x03 0x04 | 0x03 0x04 0x10 0x06 | 0x03 0x04 0x10 0x06
PowerEnvSupervision
设备地址 | 0x7F
功能定义 | Signal | Control
modbus地址范围 | 0x0001-0x2000 | 0x2001-0x4000
支持功能码 | 0x03 0x04 | 0x03 0x04 0x10 0x06
硬件端口配置说明
1. 物理层通讯口以太网； 2. 协议为MODBUS TCP； 3. SMS为主机，BMS为从机； 4. TCP报文头不做处理 5. 默认EMS作为客户端，BMS作为服务器； 6. BMS默认地址为10.30.4.13 6.1二级架构 （1）BCU端口号503 二级架构虚拟BAU （2）虚拟BAU端口号502 6.2三级架构 （1）BAU端口号503 | RS485通信方式说明： 1、物理层通信方式为RS485; 2、通信协议为ModbusRTU； 3、EMS作为主机，BMS作为从机； 4、BMS默认modbus设备地址为1，2，3，4，5，….； 5、BMS默认波特率为57600；
注：预留或内部db暂不存在的寄存器，其name填写reserve+数字，保证同一张表中name唯一即可

## 规范
excel基本规范
注释 | 通用规范适用于大多excel，具体到不同协议可在通用规范基础上添加新列。以动环为例
适用范围 | 类型 | 说明 | 范例
通用规范 | （列）偏移地址 | 十六进制地址以0x开头 | 0x0000
| （列）配置项中文名 | 中文名 | PCS的ID号
| （列）配置项英文名 | 1.寄存器英文名需遵守c语言变量命名规则，下划线连接，不可以数字开头，无空格，半角小写。用h16b和l16b标志高16位和低16位 | accum_chg_energy_h16b
|  | 2.比特位英文名规则：Bit + 数字 + : + 寄存器英文名 + . + 比特名 | Bit0:rack_enable_status_l16b.rack1
|  | 3.若有预留寄存器，或内部db没有对应，英文名用reserve+数字的形式表示 | reserve1
4.英文名需保证表内唯一
| （列）中文使用说明 | 若分比特，表示比特中文名 | Bit0: 主控1通讯故障
| （列）说明 | 以{值: 中文, 值:中文}的格式说明寄存器内容的实际含义，值为十进制 | {0: 正常, 1: 报警}
| （列）英文使用说明 | 若分比特，表示比特英文名
| （列）数值格式 | 内部db中，0为无符号整数，-0为有符号整数
|  | 协议中，u表示无符号，s有符号，f为float，bcd表示BCD编码，全部小写 | u16, s16
| （列）单位系数 | 若不填默认为1 | 单位系数0.1，单位%，实际表示‰
| （列）单位 | 若无单位不用填，不要填如-，/这样的符号。
| （列）数量number | 用于表示同一类型的数量，默认为1，表示类似单体电压的情况时填实际数量 | 若有512个单体电压，填512
| （列）是否可写 | 1表示可写，0为不可写
| 表注释 | 分为两行，一行为行名，一行直接添加注释 | 此sheet注释范例
| 弃用 | 加横线划去，配置项英文名置为reserve
| 大小端 | 统一大端，数据的高位放在低地址空间，数据的低位放在高地址空间 | 如图1
| 其余 | 大小写统一，如填写type时u16和u16统一u16。
| 寄存器与多个比特对应 | 寄存器用合并单元格，比特在该合并单元格右分行 | 如图1
动环附加规范 | （列）步长 | 表示一个对外配置项包含的内部寄存器数，数值格式u16用1表示，s32用2表示 | 如系统总电流，一个对外寄存器对应两个内部db
| （列）BlockID | 由EMG MQTT MSG List表定义，详见相应设备Def后缀表。0x开头，十六进制表示
| （列）设备地址 | 设备地址，根据点表配置。十进制表示
| （列）偏移 | 相对内部db基地址的偏移，内部db基地址详见MODBUS IO List的Power Env Supervision(default)子表。十进制表示 | 如图3
| 设备名 | 按照如图所示"配置项英文名"命名 | 如图3
| 表名 | 所由动环信息以Env开头，首字母大写，定义表额外带Def后缀 | 如图4
| 结构 | 以EMG MQTT MSG List表为例，每一种设备有两张表。其中一张带Def后缀，定义了设备的BlockID等信息，另一张为详细信息 | 如图2
图1
图2
图3
图4

## Bank Signal
Bank Information -- EMS Read from BMS
偏移地址 | 配置项中文名 | 配置项英文名 | 英文key | 中文使用说明 | 英文使用说明 | 英文子key | 说明(值/枚举说明) | 说明(值/枚举说明)(英文) | 范围 | 单位系数 | 单位 | 是否可写 | 数值格式 | 个数 | 备注 | 数据源 | Modbus地址
0x009B | 总控对外故障状态 | External Fault State | External_fault_state | bit0:BCU通信故障 | bit0:Inner Comm Fault | Inner_comm_fault | {0:正常;1:故障} | {0:Normal;1:Fault} | [0~1] |  | Hex | R | U16 |  |  | BAU | 0x1001
| 总控对外故障状态 | External Fault State |  | bit1:PCS通信故障 | bit1:PCS Comm Fault | PCS_comm_fault | {0:正常;1:故障} | {0:Normal;1:Fault} | [0~1]
| 总控对外故障状态 | External Fault State |  | bit2:PCS控制故障 | bit2:PCS Control Fault | PCS_ctrl | {0:正常;1:故障} | {0:Normal;1:Fault} | [0~1]
| 总控对外故障状态 | External Fault State |  | bit3:EMS通信故障 | bit3:EMS Comm Fault | EMS_comm_fault | {0:正常;1:故障} | {0:Normal;1:Fault} | [0~1]
| 总控对外故障状态 | External Fault State |  | bit4:簇间压差过大报警 | bit4:Rack Volt Diff Alarm | Rack_volt_diff_alarm | {0:正常;1:故障} | {0:Normal;1:Fault} | [0~1]
| 总控对外故障状态 | External Fault State |  | bit5:簇间电流差一级报警 | bit5:Rack Cur Diff Level1 Alarm | Rack_curr_diff_lvl1_alarm | {0:正常;1:故障} | {0:Normal;1:Fault} | [0~1]
| 总控对外故障状态 | External Fault State |  | bit6:紧急停机故障 | bit6:Emergency Stop Fault | Emergency_stop_fault | {0:正常;1:故障} | {0:Normal;1:Fault} | [0~1]
| 总控对外故障状态 | External Fault State |  | bit7:簇间电流差二级报警 | bit7:Rack Cur Diff Level2 Alarm | Rack_curr_diff_lvl2_alarm | {0:正常;1:故障} | {0:Normal;1:Fault} | [0~1]
| 总控对外故障状态 | External Fault State |  | bit8:系统预警 | bit8:System Warn | System_warn | {0:正常;1:报警} | {0:Normal;1:Alarm} | [0~1] | [5 empty] | bit8:所有三级报警
| 总控对外故障状态 | External Fault State |  | bit9:系统报警 | bit9:System Alarm | System_alarm | {0:正常;1:报警} | {0:Normal;1:Alarm} | [0~1] | [5 empty] | bit9:所有二级报警
| 总控对外故障状态 | External Fault State |  | bit10:系统故障 | bit10:System Fault | System_fault | {0:正常;1:故障} | {0:Normal;1:Fault} | [0~1] | [5 empty] | bit10:所有一级报警
| 总控对外故障状态 | External Fault State |  | bit11:系统禁充 | bit11:System Chg Prohibited | System_full | {0:正常;1:报警} | {0:Normal;1:Alarm} | [0~1] | [5 empty] | bit11:PCS充满、待机、停机状态
| 总控对外故障状态 | External Fault State |  | bit12:系统禁放 | bit12:System Dsg Prohibited | System_empty | {0:正常;1:报警} | {0:Normal;1:Alarm} | [0~1] | [5 empty] | bit12:PCS放空、待机、停机状态
| 总控对外故障状态 | External Fault State |  | bit13:汇流断路器状态反馈 | bit13:Busbar Circuit-breakers State Reply | Busbar_circuit_breaker_state_reply | {0:正常;1:故障} | {0:Normal;1:Fault} | [0~1]
| 总控对外故障状态 | External Fault State |  | bit14:充放电回路异常 | bit14:Chg/Dsg Circuit Fault | Chg/Dsg_circuit_fault | {0:正常;1:故障} | {0:Normal;1:Fault} | [0~1]
| 总控对外故障状态 | External Fault State |  | bit15:簇间电流差三级告警 | bit15:Rack Cur Diff Level3 Alarm | Rack_curr_diff_lvl3_alarm | {0:正常;1:故障} | {0:Normal;1:Fault} | [0~1]
0x009C | 主控对外三级报警信息（Warning） | BCU External Level3 Alarm | External_level3_alarm | bit0:簇总压过高 | bit0:Total OV | Total_OV | {0:正常;1:报警} | {0:Normal;1:Alarm} | [0~1] |  | Hex | R | U16 |  |  | BAU | 0x1002
| 主控对外三级报警信息（Warning） | BCU External Level3 Alarm |  | bit1:簇总压过低 | bit1:Total UV | Total_UV | {0:正常;1:报警} | {0:Normal;1:Alarm} | [0~1]
| 主控对外三级报警信息（Warning） | BCU External Level3 Alarm |  | bit2:单体电压过高 | bit2:Cell OV | Cell_OV | {0:正常;1:报警} | {0:Normal;1:Alarm} | [0~1]
| 主控对外三级报警信息（Warning） | BCU External Level3 Alarm |  | bit3:单体电压过低 | bit3:Cell UV | Cell_UV | {0:正常;1:报警} | {0:Normal;1:Alarm} | [0~1]
| 主控对外三级报警信息（Warning） | BCU External Level3 Alarm |  | bit4:放电电流过大 | bit4:Dsg OC | Dsg_OC | {0:正常;1:报警} | {0:Normal;1:Alarm} | [0~1]
| 主控对外三级报警信息（Warning） | BCU External Level3 Alarm |  | bit5:充电电流过大 | bit5:Chg OC | Chg_OC | {0:正常;1:报警} | {0:Normal;1:Alarm} | [0~1]
| 主控对外三级报警信息（Warning） | BCU External Level3 Alarm |  | bit6:放电温度过高 | bit6:Dsg OT | Dsg_OT | {0:正常;1:报警} | {0:Normal;1:Alarm} | [0~1]
| 主控对外三级报警信息（Warning） | BCU External Level3 Alarm |  | bit7:放电温度过低 | bit7:Dsg UT | Dsg_UT | {0:正常;1:报警} | {0:Normal;1:Alarm} | [0~1]
| 主控对外三级报警信息（Warning） | BCU External Level3 Alarm |  | bit8:充电温度过高 | bit8:Chg OT | Chg_OT | {0:正常;1:报警} | {0:Normal;1:Alarm} | [0~1]
| 主控对外三级报警信息（Warning） | BCU External Level3 Alarm |  | bit9:充电温度过低 | bit9:Chg UT | Chg_UT | {0:正常;1:报警} | {0:Normal;1:Alarm} | [0~1]
| 主控对外三级报警信息（Warning） | BCU External Level3 Alarm |  | bit10:绝缘阻值过低 | bit10:Low IR | Low_IR | {0:正常;1:报警} | {0:Normal;1:Alarm} | [0~1]
| 主控对外三级报警信息（Warning） | BCU External Level3 Alarm |  | bit11:极柱温度过高 | bit11:Term OT | Term_OT | {0:正常;1:报警} | {0:Normal;1:Alarm} | [0~1]
| 主控对外三级报警信息（Warning） | BCU External Level3 Alarm |  | bit12:高压箱温度过高 | bit12:PDU OT | PDU_OT | {0:正常;1:报警} | {0:Normal;1:Alarm} | [0~1]
| 主控对外三级报警信息（Warning） | BCU External Level3 Alarm |  | bit13:单体压差过大 | bit13:Cell OV Diff | Cell_OV_diff | {0:正常;1:报警} | {0:Normal;1:Alarm} | [0~1]
| 主控对外三级报警信息（Warning） | BCU External Level3 Alarm |  | bit14:单体温差过大 | bit14:Cell OT Diff | Cell_OT_diff | {0:正常;1:报警} | {0:Normal;1:Alarm} | [0~1]
| 主控对外三级报警信息（Warning） | BCU External Level3 Alarm |  | bit15:SOC过低 | bit15:Low SOH | Low_SOH | {0:正常;1:报警} | {0:Normal;1:Alarm} | [0~1]
0x009D | 主控对外二级报警信息（Alarm） | BCU External Level2 Alarm | External_level2_alarm | bit0:簇总压过高 | bit0:Total OV | Total_OV | {0:正常;1:报警} | {0:Normal;1:Alarm} | [0~1] |  | Hex | R | U16 |  |  | BAU | 0x1003
| 主控对外二级报警信息（Alarm） | BCU External Level2 Alarm |  | bit1:簇总压过低 | bit1:Total UV | Total_UV | {0:正常;1:报警} | {0:Normal;1:Alarm} | [0~1]
| 主控对外二级报警信息（Alarm） | BCU External Level2 Alarm |  | bit2:单体电压过高 | bit2:Cell OV | Cell_OV | {0:正常;1:报警} | {0:Normal;1:Alarm} | [0~1]
| 主控对外二级报警信息（Alarm） | BCU External Level2 Alarm |  | bit3:单体电压过低 | bit3:Cell UV | Cell_UV | {0:正常;1:报警} | {0:Normal;1:Alarm} | [0~1]
| 主控对外二级报警信息（Alarm） | BCU External Level2 Alarm |  | bit4:放电电流过大 | bit4:Dsg OC | Dsg_OC | {0:正常;1:报警} | {0:Normal;1:Alarm} | [0~1]
| 主控对外二级报警信息（Alarm） | BCU External Level2 Alarm |  | bit5:充电电流过大 | bit5:Chg OC | Chg_OC | {0:正常;1:报警} | {0:Normal;1:Alarm} | [0~1]
| 主控对外二级报警信息（Alarm） | BCU External Level2 Alarm |  | bit6:放电温度过高 | bit6:Dsg OT | Dsg_OT | {0:正常;1:报警} | {0:Normal;1:Alarm} | [0~1]
| 主控对外二级报警信息（Alarm） | BCU External Level2 Alarm |  | bit7:放电温度过低 | bit7:Dsg UT | Dsg_UT | {0:正常;1:报警} | {0:Normal;1:Alarm} | [0~1]
| 主控对外二级报警信息（Alarm） | BCU External Level2 Alarm |  | bit8:充电温度过高 | bit8:Chg OT | Chg_OT | {0:正常;1:报警} | {0:Normal;1:Alarm} | [0~1]
| 主控对外二级报警信息（Alarm） | BCU External Level2 Alarm |  | bit9:充电温度过低 | bit9:Chg UT | Chg_UT | {0:正常;1:报警} | {0:Normal;1:Alarm} | [0~1]
| 主控对外二级报警信息（Alarm） | BCU External Level2 Alarm |  | bit10:绝缘阻值过低 | bit10:Low IR | Low_IR | {0:正常;1:报警} | {0:Normal;1:Alarm} | [0~1]
| 主控对外二级报警信息（Alarm） | BCU External Level2 Alarm |  | bit11:极柱温度过高 | bit11:Term OT | Term_OT | {0:正常;1:报警} | {0:Normal;1:Alarm} | [0~1]
| 主控对外二级报警信息（Alarm） | BCU External Level2 Alarm |  | bit12:高压箱温度过高 | bit12:PDU OT | PDU_OT | {0:正常;1:报警} | {0:Normal;1:Alarm} | [0~1]
| 主控对外二级报警信息（Alarm） | BCU External Level2 Alarm |  | bit13:单体压差过大 | bit13:Cell OV Diff | Cell_OV_diff | {0:正常;1:报警} | {0:Normal;1:Alarm} | [0~1]
| 主控对外二级报警信息（Alarm） | BCU External Level2 Alarm |  | bit14:单体温差过大 | bit14:Cell OT Diff | Cell_OT_diff | {0:正常;1:报警} | {0:Normal;1:Alarm} | [0~1]
| 主控对外二级报警信息（Alarm） | BCU External Level2 Alarm |  | bit15:SOC过低 | bit15:Low SOH | Low_SOH | {0:正常;1:报警} | {0:Normal;1:Alarm} | [0~1]
0x009E | 主控对外一级报警信息（Critical） | BCU External Level1 Alarm | External_level1_alarm | bit0:簇总压过高 | bit0:Total OV | Total_OV | {0:正常;1:报警} | {0:Normal;1:Alarm} | [0~1] |  | Hex | R | U16 |  |  | BAU | 0x1004
| 主控对外一级报警信息（Critical） | BCU External Level1 Alarm |  | bit1:簇总压过低 | bit1:Total UV | Total_UV | {0:正常;1:报警} | {0:Normal;1:Alarm} | [0~1]
| 主控对外一级报警信息（Critical） | BCU External Level1 Alarm |  | bit2:单体电压过高 | bit2:Cell OV | Cell_OV | {0:正常;1:报警} | {0:Normal;1:Alarm} | [0~1]
| 主控对外一级报警信息（Critical） | BCU External Level1 Alarm |  | bit3:单体电压过低 | bit3:Cell UV | Cell_UV | {0:正常;1:报警} | {0:Normal;1:Alarm} | [0~1]
| 主控对外一级报警信息（Critical） | BCU External Level1 Alarm |  | bit4:放电电流过大 | bit4:Dsg OC | Dsg_OC | {0:正常;1:报警} | {0:Normal;1:Alarm} | [0~1]
| 主控对外一级报警信息（Critical） | BCU External Level1 Alarm |  | bit5:充电电流过大 | bit5:Chg OC | Chg_OC | {0:正常;1:报警} | {0:Normal;1:Alarm} | [0~1]
| 主控对外一级报警信息（Critical） | BCU External Level1 Alarm |  | bit6:放电温度过高 | bit6:Dsg OT | Dsg_OT | {0:正常;1:报警} | {0:Normal;1:Alarm} | [0~1]
| 主控对外一级报警信息（Critical） | BCU External Level1 Alarm |  | bit7:放电温度过低 | bit7:Dsg UT | Dsg_UT | {0:正常;1:报警} | {0:Normal;1:Alarm} | [0~1]
| 主控对外一级报警信息（Critical） | BCU External Level1 Alarm |  | bit8:充电温度过高 | bit8:Chg OT | Chg_OT | {0:正常;1:报警} | {0:Normal;1:Alarm} | [0~1]
| 主控对外一级报警信息（Critical） | BCU External Level1 Alarm |  | bit9:充电温度过低 | bit9:Chg UT | Chg_UT | {0:正常;1:报警} | {0:Normal;1:Alarm} | [0~1]
| 主控对外一级报警信息（Critical） | BCU External Level1 Alarm |  | bit10:绝缘阻值过低 | bit10:Low IR | Low_IR | {0:正常;1:报警} | {0:Normal;1:Alarm} | [0~1]
| 主控对外一级报警信息（Critical） | BCU External Level1 Alarm |  | bit11:极柱温度过高 | bit11:Term OT | Term_OT | {0:正常;1:报警} | {0:Normal;1:Alarm} | [0~1]
| 主控对外一级报警信息（Critical） | BCU External Level1 Alarm |  | bit12:高压箱温度过高 | bit12:PDU OT | PDU_OT | {0:正常;1:报警} | {0:Normal;1:Alarm} | [0~1]
| 主控对外一级报警信息（Critical） | BCU External Level1 Alarm |  | bit13:单体压差过大 | bit13:Cell OV Diff | Cell_OV_diff | {0:正常;1:报警} | {0:Normal;1:Alarm} | [0~1]
| 主控对外一级报警信息（Critical） | BCU External Level1 Alarm |  | bit14:单体温差过大 | bit14:Cell OT Diff | Cell_OT_diff | {0:正常;1:报警} | {0:Normal;1:Alarm} | [0~1]
| 主控对外一级报警信息（Critical） | BCU External Level1 Alarm |  | bit15:SOC过低 | bit15:Low SOH | Low_SOH | {0:正常;1:报警} | {0:Normal;1:Alarm} | [0~1]
0x0084 | 主控对外三级报警信息2（Warning） | BCU External Level3 Alarm2 | bcu_external_lv3_alm_sum_II | bit0: 簇总压校验差过高 | bit0:Pack Vol Over | totalvol_batteryvol_diff | {0:正常;1:报警} | {0:Normal;1:Alarm} | [0~1] |  | Hex | R | U16 |  |  | BAU | 0x1005
| 主控对外三级报警信息2（Warning） | BCU External Level3 Alarm2 |  | bit1: Pack电压过高 | bit1:Pack Vol Over | module_vol_over | {0:正常;1:报警} | {0:Normal;1:Alarm} | [0~1]
| 主控对外三级报警信息2（Warning） | BCU External Level3 Alarm2 |  | bit2: Pack电压过低 | bit2:Pack Vol Low | module_vol_low | {0:正常;1:报警} | {0:Normal;1:Alarm} | [0~1]
| 主控对外三级报警信息2（Warning） | BCU External Level3 Alarm2 |  | bit3: 温升过高 | bit3:Bat Hi Temp Rise Alm | bat_hi_temp_rise_alm | {0:正常;1:报警} | {0:Normal;1:Alarm} | [0~1]
| 主控对外三级报警信息2（Warning） | BCU External Level3 Alarm2 |  | bit4: Pack压差过大 | bit4:Pack Vol Differ Over | module_vol_differ_over | {0:正常;1:报警} | {0:Normal;1:Alarm} | [0~1]
| 主控对外三级报警信息2（Warning） | BCU External Level3 Alarm2 |  | bit5:动环预警汇总 | bit5:Envi Summary | envi_Summary | {0:正常;1:报警} | {0:Normal;1:Alarm} | [0~1]
| 主控对外三级报警信息2（Warning） | BCU External Level3 Alarm2 |  | bit6:铜排温度过高 | bit6:Busbar OT | Copper_OT | {0:正常;1:报警} | {0:Normal;1:Alarm} | [0~1]
| 主控对外三级报警信息2（Warning） | BCU External Level3 Alarm2 |  | bit7:充电单体压差过大 | bit7:Chg Cell Volt Diff | Chg_cell_volt_diff | {0:正常;1:报警} | {0:Normal;1:Alarm} | [0~1]
| 主控对外三级报警信息2（Warning） | BCU External Level3 Alarm2 |  | bit8:充电单体温差过大 | bit8:Chg Cell Temp Diff | Chg_cell_temp_diff | {0:正常;1:报警} | {0:Normal;1:Alarm} | [0~1]
| 主控对外三级报警信息2（Warning） | BCU External Level3 Alarm2 |  | bit9:充电Pack压差过大 | bit9:Chg Pack Volt Diff | Chg_module_volt_diff | {0:正常;1:报警} | {0:Normal;1:Alarm} | [0~1]
| 主控对外三级报警信息2（Warning） | BCU External Level3 Alarm2 |  | bit10:放电单体压差过大 | bit10:Dsg Cell Volt Diff | Dsg_cell_volt_diff | {0:正常;1:报警} | {0:Normal;1:Alarm} | [0~1]
| 主控对外三级报警信息2（Warning） | BCU External Level3 Alarm2 |  | bit11:放电单体温差过大 | bit11:Dsg Cell Temp Diff | Dsg_cell_temp_diff | {0:正常;1:报警} | {0:Normal;1:Alarm} | [0~1]
| 主控对外三级报警信息2（Warning） | BCU External Level3 Alarm2 |  | bit12:放电Pack压差过大 | bit12:Dsg Pack Volt Diff | Dsg_module_volt_diff | {0:正常;1:报警} | {0:Normal;1:Alarm} | [0~1]
|  |  |  | bit13:预留 | bit13:Reserve1 | Reserved1
|  |  |  | bit14:Pack内温差过大 | bit14:Pack Temp Diff | Pack_temp_diff | {0:正常;1:报警} | {0:Normal;1:Alarm} | [0~1]
| 主控对外三级报警信息2（Warning） | BCU External Level3 Alarm2 |  | bit15:预留 | bit15:Reserve2 | Reserved2
0x0085 | 主控对外二级报警信息2（Alarm） | BCU External Level2 Alarm2 | bcu_external_lv2_alm_sum_II | bit0: 簇总压校验差过高 | bit0:Pack Vol Over | totalvol_batteryvol_diff | {0:正常;1:报警} | {0:Normal;1:Alarm} | [0~1] |  | Hex | R | U16 |  |  | BAU | 0x1006
| 主控对外二级报警信息2（Alarm） | BCU External Level2 Alarm2 |  | bit1: Pack电压过高 | bit1:Pack Vol Over | module_vol_over | {0:正常;1:报警} | {0:Normal;1:Alarm} | [0~1]
| 主控对外二级报警信息2（Alarm） | BCU External Level2 Alarm2 |  | bit2: Pack电压过低 | bit2:Pack Vol Low | module_vol_low | {0:正常;1:报警} | {0:Normal;1:Alarm} | [0~1]
| 主控对外二级报警信息2（Alarm） | BCU External Level2 Alarm2 |  | bit3: 温升过高 | bit3:Bat Hi Temp Rise Alm | bat_hi_temp_rise_alm | {0:正常;1:报警} | {0:Normal;1:Alarm} | [0~1]
| 主控对外二级报警信息2（Alarm） | BCU External Level2 Alarm2 |  | bit4: Pack压差过大 | bit4:Pack Vol Differ Over | module_vol_differ_over | {0:正常;1:报警} | {0:Normal;1:Alarm} | [0~1]
| 主控对外二级报警信息2（Alarm） | BCU External Level2 Alarm2 |  | bit5:动环报警汇总 | bit5:Envi Summary | envi_Summary | {0:正常;1:报警} | {0:Normal;1:Alarm} | [0~1]
| 主控对外二级报警信息2（Alarm） | BCU External Level2 Alarm2 |  | bit6:铜排温度过高 | bit6:Busbar OT | Copper_OT | {0:正常;1:报警} | {0:Normal;1:Alarm} | [0~1]
| 主控对外二级报警信息2（Alarm） | BCU External Level2 Alarm2 |  | bit7:充电单体压差过大 | bit7:Chg Cell Volt Diff | Chg_cell_volt_diff | {0:正常;1:报警} | {0:Normal;1:Alarm} | [0~1]
| 主控对外二级报警信息2（Alarm） | BCU External Level2 Alarm2 |  | bit8:充电单体温差过大 | bit8:Chg Cell Temp Diff | Chg_cell_temp_diff | {0:正常;1:报警} | {0:Normal;1:Alarm} | [0~1]
| 主控对外二级报警信息2（Alarm） | BCU External Level2 Alarm2 |  | bit9:充电Pack压差过大 | bit9:Chg Pack Volt Diff | Chg_module_volt_diff | {0:正常;1:报警} | {0:Normal;1:Alarm} | [0~1]
| 主控对外二级报警信息2（Alarm） | BCU External Level2 Alarm2 |  | bit10:放电单体压差过大 | bit10:Dsg Cell Volt Diff | Dsg_cell_volt_diff | {0:正常;1:报警} | {0:Normal;1:Alarm} | [0~1]
| 主控对外二级报警信息2（Alarm） | BCU External Level2 Alarm2 |  | bit11:放电单体温差过大 | bit11:Dsg Cell Temp Diff | Dsg_cell_temp_diff | {0:正常;1:报警} | {0:Normal;1:Alarm} | [0~1]
| 主控对外二级报警信息2（Alarm） | BCU External Level2 Alarm2 |  | bit12:放电Pack压差过大 | bit12:Dsg Pack Volt Diff | Dsg_module_volt_diff | {0:正常;1:报警} | {0:Normal;1:Alarm} | [0~1]
|  |  |  | bit13:预留 | bit13:Reserve1 | Reserved1
|  |  |  | bit14:Pack内温差过大 | bit14:Pack Temp Diff | Pack_temp_diff | {0:正常;1:报警} | {0:Normal;1:Alarm} | [0~1]
| 主控对外二级报警信息2（Alarm） | BCU External Level2 Alarm2 |  | bit15:预留 | bit15:Reserve2 | Reserved2
0x0086 | 主控对外一级报警信息2（Critical） | BCU External Level1 Alarm2 | bcu_external_lv1_alm_sum_II | bit0: 簇总压校验差过高 | bit0:Pack Vol Over | totalvol_batteryvol_diff | {0:正常;1:报警} | {0:Normal;1:Alarm} | [0~1] |  | Hex | R | U16 |  |  | BAU | 0x1007
| 主控对外一级报警信息2（Critical） | BCU External Level1 Alarm2 |  | bit1: Pack电压过高 | bit1:Pack Vol Over | module_vol_over | {0:正常;1:报警} | {0:Normal;1:Alarm} | [0~1]
| 主控对外一级报警信息2（Critical） | BCU External Level1 Alarm2 |  | bit2: Pack电压过低 | bit2:Pack Vol Low | module_vol_low | {0:正常;1:报警} | {0:Normal;1:Alarm} | [0~1]
| 主控对外一级报警信息2（Critical） | BCU External Level1 Alarm2 |  | bit3: 温升过高 | bit3:Bat Hi Temp Rise Alm | bat_hi_temp_rise_alm | {0:正常;1:报警} | {0:Normal;1:Alarm} | [0~1]
| 主控对外一级报警信息2（Critical） | BCU External Level1 Alarm2 |  | bit4: Pack压差过大 | bit4:Pack Vol Differ Over | module_vol_differ_over | {0:正常;1:报警} | {0:Normal;1:Alarm} | [0~1]
| 主控对外一级报警信息2（Critical） | BCU External Level1 Alarm2 |  | bit5:动停机警汇总 | bit5:Envi Summary | envi_Summary | {0:正常;1:报警} | {0:Normal;1:Alarm} | [0~1]
| 主控对外一级报警信息2（Critical） | BCU External Level1 Alarm2 |  | bit6:铜排温度过高 | bit6:Busbar OT | Copper_OT | {0:正常;1:报警} | {0:Normal;1:Alarm} | [0~1]
| 主控对外一级报警信息2（Critical） | BCU External Level1 Alarm2 |  | bit7:充电单体压差过大 | bit7:Chg Cell Volt Diff | Chg_cell_volt_diff | {0:正常;1:报警} | {0:Normal;1:Alarm} | [0~1]
| 主控对外一级报警信息2（Critical） | BCU External Level1 Alarm2 |  | bit8:充电单体温差过大 | bit8:Chg Cell Temp Diff | Chg_cell_temp_diff | {0:正常;1:报警} | {0:Normal;1:Alarm} | [0~1]
| 主控对外一级报警信息2（Critical） | BCU External Level1 Alarm2 |  | bit9:充电Pack压差过大 | bit9:Chg Pack Volt Diff | Chg_module_volt_diff | {0:正常;1:报警} | {0:Normal;1:Alarm} | [0~1]
| 主控对外一级报警信息2（Critical） | BCU External Level1 Alarm2 |  | bit10:放电单体压差过大 | bit10:Dsg Cell Volt Diff | Dsg_cell_volt_diff | {0:正常;1:报警} | {0:Normal;1:Alarm} | [0~1]
| 主控对外一级报警信息2（Critical） | BCU External Level1 Alarm2 |  | bit11:放电单体温差过大 | bit11:Dsg Cell Temp Diff | Dsg_cell_temp_diff | {0:正常;1:报警} | {0:Normal;1:Alarm} | [0~1]
| 主控对外一级报警信息2（Critical） | BCU External Level1 Alarm2 |  | bit12:放电Pack压差过大 | bit12:Dsg Pack Volt Diff | Dsg_module_volt_diff | {0:正常;1:报警} | {0:Normal;1:Alarm} | [0~1]
|  |  |  | bit13:预留 | bit13:Reserve1 | Reserved1
|  |  |  | bit14:Pack内温差过大 | bit14:Pack Temp Diff | Pack_temp_diff | {0:正常;1:报警} | {0:Normal;1:Alarm} | [0~1]
| 主控对外一级报警信息2（Critical） | BCU External Level1 Alarm2 |  | bit15:预留 | bit15:Reserve2 | Reserved2
0x0083 | 主控通信故障(簇17-簇32) | BAU Comm Fault(BCU17-BCU32) | BAU_comm_fault_h16 | bit(0~15):主控(17~32)通讯故障 | bit(0~15):BCU(17~32) Comm Fault | BCU(17~32)_comm_fault | {0:正常;1:故障} | {0:Normal;1:Fault} | [0~1] |  | Hex | R | U16 |  |  | BAU | 0x1008
0x0082 | 主控通信故障(簇1-簇16) | BAU Comm Fault(BCU1-BCU16) | BAU_comm_fault_l16 | bit(0~15):主控(1~16)通讯故障 | bit(0~15):BCU(1~16) Comm Fault | BCU(1~16)_comm_fault | {0:正常;1:故障} | {0:Normal;1:Fault} | [0~1] |  | Hex | R | U16 |  |  | BAU | 0x1009
| 主控通信故障报警3,4 | reserve1 | reserve1 | [8 empty] | R | u16 | 2 |  | BAU | 0x100A
0x00A7 | Rack故障保护 | Rack Fault | Rack_fault | bit0:从控自检故障 | bit0:BMU Self-Check Fault | BMU_self_check_fault | {0:正常;1:故障} | {0:Normal;1:Fault} | [0~1] |  | Hex | R | U16 |  |  | BAU | 0x100C
| Rack故障保护 | Rack Fault |  | bit1:主控自检故障 | bit1:BCU Self-Check Fault | BCU_self_check_fault | {0:正常;1:故障} | {0:Normal;1:Fault} | [0~1]
| Rack故障保护 | Rack Fault |  | bit2:熔断器故障 | bit2:Fuse Fault | Fuse_fault | {0:正常;1:故障} | {0:Normal;1:Fault} | [0~1]
| Rack故障保护 | Rack Fault |  | bit3:接触器故障 | bit3:Contactor Fault | Contactor_fault | {0:正常;1:故障} | {0:Normal;1:Fault} | [0~1]
| Rack故障保护 | Rack Fault |  | bit4:从控通信故障 | bit4:BMU Comm Fault | BMU_comm_fault | {0:正常;1:故障} | {0:Normal;1:Fault} | [0~1]
| Rack故障保护 | Rack Fault |  | bit5:总控通信故障 | bit5:BAU Comm Fault | BAU_comm_fault | {0:正常;1:故障} | {0:Normal;1:Fault} | [0~1]
| Rack故障保护 | Rack Fault |  | bit6:电流采样故障 | bit6:Current Sampling Fault | Current_sampling_fault | {0:正常;1:故障} | {0:Normal;1:Fault} | [0~1]
| Rack故障保护 | Rack Fault |  | bit7:绝缘检测故障 | bit7:Insulation Detection Fault | Insulation_detection_fault | {0:正常;1:故障} | {0:Normal;1:Fault} | [0~1]
| Rack故障保护 | Rack Fault |  | bit8:隔离开关故障 | bit8:Disconnector Fault | Disconnector_fault | {0:正常;1:故障} | {0:Normal;1:Fault} | [0~1]
| Rack故障保护 | Rack Fault |  | bit9:NTC故障 | bit9:NTC Fault | NTC_fault | {0:正常;1:故障} | {0:Normal;1:Fault} | [0~1]
| Rack故障保护 | Rack Fault |  | bit10:高压箱温度故障 | bit10:PDU Temp Fault | PDU_temp_fault | {0:正常;1:故障} | {0:Normal;1:Fault} | [0~1]
| Rack故障保护 | Rack Fault |  | bit11:高压回路故障 | bit11:High Voltage Circuit Fault | High_voltage_circuit_fault | {0:正常;1:故障} | {0:Normal;1:Fault} | [0~1]
| Rack故障保护 | Rack Fault |  | bit12:功能安全故障 | bit12:Function Safety Fault | Function_safety_fault | {0:正常;1:故障} | {0:Normal;1:Fault} | [0~1]
| Rack故障保护 | Rack Fault |  | bit13:PCS通信故障 | bit13:PCS Comm Fault | PCS_communication_fault | {0:正常;1:故障} | {0:Normal;1:Fault} | [0~1]
| Rack故障保护 | Rack Fault |  | bit14:预留 | bit14:Reserved | Reserved1
| Rack故障保护 | Rack Fault |  | bit15:预留 | bit15:Reserved | Reserved2
0x00AC | 总控对外故障状态2 | BAU Fault Info Sum2 | fault_info_sum2 | bit0:BDU通信故障 | bit0:BDU Communicate Fault | bdu_communicate_fault | {0:正常;1:故障} | {0:Normal;1:Fault} | [0~1] |  | Hex | R | U16 |  |  | BAU | 0x100D
| 总控对外故障状态2 | BAU Fault Info Sum2 |  | bit1:电操闭合故障 | bit1:Electric Operate Close Fault | electric_operate_close_fault | {0:正常;1:故障} | {0:Normal;1:Fault} | [0~1]
| 总控对外故障状态2 | BAU Fault Info Sum2 |  | bit2:电操断开故障 | bit2:Electric Operate Cut Fault | electric_operate_cut_fault | {0:正常;1:故障} | {0:Normal;1:Fault} | [0~1]
| 总控对外故障状态2 | BAU Fault Info Sum2 |  | bit3:总控自检故障 | bit3:BAU Self Check Fault | BAU_self_check_fault | {0:正常;1:故障} | {0:Normal;1:Fault} | [0~1]
|  |  |  | bit[4~15]:预留 | bit[4~15]:Reserve | Reserve
0x00B8 | 主控对外预提示 | BCU External Warn Tip | BCU_external_warn_tipI | bit0:簇总压过高 | bit0:Total OV | Total_OV | {0:正常;1:故障} | {0:Normal;1:Alarm} | [0~1] |  | Hex | R | U16 |  |  | BAU | 0x100E
| 主控对外预提示 | BCU External Warn Tip |  | bit1:簇总压过低 | bit1:Total UV | Total_UV | {0:正常;1:故障} | {0:Normal;1:Alarm} | [0~1]
| 主控对外预提示 | BCU External Warn Tip |  | bit2:单体电压过高 | bit2:Cell OV | Cell_OV | {0:正常;1:故障} | {0:Normal;1:Alarm} | [0~1]
| 主控对外预提示 | BCU External Warn Tip |  | bit3:单体电压过低 | bit3:Cell UV | Cell_UV | {0:正常;1:故障} | {0:Normal;1:Alarm} | [0~1]
| 主控对外预提示 | BCU External Warn Tip |  | bit4:放电电流过大 | bit4:Dsg OC | Dsg_OC | {0:正常;1:故障} | {0:Normal;1:Alarm} | [0~1]
| 主控对外预提示 | BCU External Warn Tip |  | bit5:充电电流过大 | bit5:Chg OC | Chg_OC | {0:正常;1:故障} | {0:Normal;1:Alarm} | [0~1]
| 主控对外预提示 | BCU External Warn Tip |  | bit6:放电温度过高 | bit6:Dsg OT | Dsg_OT | {0:正常;1:故障} | {0:Normal;1:Alarm} | [0~1]
| 主控对外预提示 | BCU External Warn Tip |  | bit7:放电温度过低 | bit7:Dsg UT | Dsg_UT | {0:正常;1:故障} | {0:Normal;1:Alarm} | [0~1]
| 主控对外预提示 | BCU External Warn Tip |  | bit8:充电温度过高 | bit8:Chg OT | Chg_OT | {0:正常;1:故障} | {0:Normal;1:Alarm} | [0~1]
| 主控对外预提示 | BCU External Warn Tip |  | bit9:充电温度过低 | bit9:Chg UT | Chg_UT | {0:正常;1:故障} | {0:Normal;1:Alarm} | [0~1]
| 主控对外预提示 | BCU External Warn Tip |  | bit10:预留 | bit10:Reserved | Low_IR | {0:正常;1:故障} | {0:Normal;1:Alarm} | [0~1]
| 主控对外预提示 | BCU External Warn Tip |  | bit11:预留 | bit11:Reserved | Term_OT | {0:正常;1:故障} | {0:Normal;1:Alarm} | [0~1]
| 主控对外预提示 | BCU External Warn Tip |  | bit12:预留 | bit12:Reserved | PDU_OT | {0:正常;1:故障} | {0:Normal;1:Alarm} | [0~1]
| 主控对外预提示 | BCU External Warn Tip |  | bit13:单体压差过大 | bit13:Cell OV Diff | Cell_OV_diff | {0:正常;1:故障} | {0:Normal;1:Alarm} | [0~1]
| 主控对外预提示 | BCU External Warn Tip |  | bit14:单体温差过大 | bit14:Cell OT Diff | Cell_OT_diff | {0:正常;1:故障} | {0:Normal;1:Alarm} | [0~1]
| 主控对外预提示 | BCU External Warn Tip |  | bit15:预留 | bit15:Low SOH | Low_SOH | {0:正常;1:故障} | {0:Normal;1:Alarm} | [0~1]
0x00B9 | 主控对外预提示2 | BCU External Warn Tip2 | BCU_external_warn_tipII | bit0:预留 | bit0:Reserved | Total_OV_diff | {0:正常;1:故障} | {0:Normal;1:Alarm} | [0~1] |  | Hex | R | U16 |  |  | BAU | 0x100F
| 主控对外预提示2 | BCU External Warn Tip2 |  | bit1:Pack电压过高 | bit1:Pack OverVoltage | Module_OV | {0:正常;1:故障} | {0:Normal;1:Alarm} | [0~1]
| 主控对外预提示2 | BCU External Warn Tip2 |  | bit2:Pack电压过低 | bit2:Pack UnderVoltage | Module_UV | {0:正常;1:故障} | {0:Normal;1:Alarm} | [0~1]
| 主控对外预提示2 | BCU External Warn Tip2 |  | bit3:预留 | bit3:Reserved | Cell_temp_rise | {0:正常;1:故障} | {0:Normal;1:Alarm} | [0~1]
| 主控对外预提示2 | BCU External Warn Tip2 |  | bit4:Pack压差过大 | bit4:Pack OverVoltage Difference | Module_OV_diff | {0:正常;1:故障} | {0:Normal;1:Alarm} | [0~1]
| 主控对外预提示2 | BCU External Warn Tip2 |  | bit5:预留 | bit5:Reserved | Run_warn_summary | {0:正常;1:故障} | {0:Normal;1:Alarm} | [0~1]
| 主控对外预提示2 | BCU External Warn Tip2 |  | bit6:预留 | bit6:Reserved | Copper_OT | {0:正常;1:报警} | {0:Normal;1:Alarm} | [0~1]
| 主控对外预提示2 | BCU External Warn Tip2 |  | bit7:充电单体压差过大 | bit7:Chg Cell Volt Diff | Chg_cell_volt_diff | {0:正常;1:报警} | {0:Normal;1:Alarm} | [0~1]
| 主控对外预提示2 | BCU External Warn Tip2 |  | bit8:充电单体温差过大 | bit8:Chg Cell Temp Diff | Chg_cell_temp_diff | {0:正常;1:报警} | {0:Normal;1:Alarm} | [0~1]
| 主控对外预提示2 | BCU External Warn Tip2 |  | bit9:充电Pack压差过大 | bit9:Chg Moulde Volt Diff | Chg_module_volt_diff | {0:正常;1:报警} | {0:Normal;1:Alarm} | [0~1]
| 主控对外预提示2 | BCU External Warn Tip2 |  | bit10:放电单体压差过大 | bit10:Dsg Cell Volt Diff | Dsg_cell_volt_diff | {0:正常;1:报警} | {0:Normal;1:Alarm} | [0~1]
| 主控对外预提示2 | BCU External Warn Tip2 |  | bit11:放电单体温差过大 | bit11:Dsg Cell Temp Diff | Dsg_cell_temp_diff | {0:正常;1:报警} | {0:Normal;1:Alarm} | [0~1]
| 主控对外预提示2 | BCU External Warn Tip2 |  | bit12:放电Pack压差过大 | bit12:Dsg Moulde Volt Diff | Dsg_module_volt_diff | {0:正常;1:报警} | {0:Normal;1:Alarm} | [0~1]
|  |  |  | bit13:预留 | bit13:Reserve1 | Reserved1
|  |  |  | bit14:Pack内温差过大 | bit14:Pack Temp Diff | Pack_temp_diff | {0:正常;1:报警} | {0:Normal;1:Alarm} | [0~1]
| 主控对外预提示2 | BCU External Warn Tip2 |  | bit15:预留 | bit14:Reserve2 | Reserved2
0x0040 | 项目版本号 | Project Version Num | project_version_num | [8 empty] | R | U16 |  |  | BAU | 0x1010
0x0041 | 主版本号 | Main Version Num | main_version_num | [8 empty] | R | U16 |  |  | BAU | 0x1011
0x0042 | 子版本号 | Branch Version Num | branch_version_num | [8 empty] | R | U16 |  |  | BAU | 0x1012
0x0043 | 修正版本号 | Corrected Version Num | corrected_version_num | [8 empty] | R | U16 |  |  | BAU | 0x1013
0x05A2 | EMS对外协议版本号 | Ems Modbus Version | EMS_MODBUS_version | [8 empty] | R | U16 |  |  | BAU | 0x1014
| 預留 | reserve3 | reserve3 | [8 empty] | R | u16 | 19 |  | BAU | 0x1015
0x0098 | 一键并网状态 | Auto Connected State | Auto_connected_state |  |  |  | {0:未开始;1:开始;2:成功;3:失败} | {0:Not Started;1:Started;2:Success;3:Failure} | [0~3] |  |  | R | U16 |  |  | BAU | 0x1028
0x0090 | Rack使能状态(簇17-簇32) | Rack Enable State (BCU17-BCU32) | Rack_enable_state_h16 | bit(0~15):Rack(17~32)使能状态 | bit(0~15):Rack(17~32) Enable State | Rack(17~32)_enable_state | {0:禁用;1:使能} | {0:Disable;1:Enable} | [0~1] |  | Hex | R | U16 |  |  | BAU | 0x1029
0x0091 | Rack使能状态(簇1-簇16) | Rack Enable State (BCU1-BCU16) | Rack_enable_state_l16 | bit(0~15):Rack(1~16)使能状态 | bit(0~15):Rack(1~16) Enable State | Rack(1~16)_enable_state | {0:禁用;1:使能} | {0:Disable;1:Enable} | [0~1] |  | Hex | R | U16 |  |  | BAU | 0x102A
| 預留 | reserve4 | reserve4 | [8 empty] | R | U16 | 2 |  | BAU | 0x102B
0x0096 | 并网状态(簇17-簇32) | Connected State (BCU17-BCU32) | Connected_state_h16 | bit(0~15):Rack(17~32)并网状态 | bit(0~15):Rack(17~32) Connected State | Rack(17~32)_connected_state | {0:离网;1:在网} | {0:Disconnected;1:Connected} | [0~1] |  | Hex | R | U16 |  |  | BAU | 0x102D
0x0097 | 并网状态(簇1-簇16) | Connected State (BCU1-BCU16) | Connected_state_l16 | bit(0~15):Rack(1~16)并网状态 | bit(0~15):Rack(1~16) Connected State | Rack(1~16)_connected_state | {0:离网;1:在网} | {0:Disconnected;1:Connected} | [0~1] |  | Hex | R | U16 |  |  | BAU | 0x102E
| 預留 | reserve5 | reserve5 | [8 empty] | R | U16 | 2 |  | BAU | 0x102F
0x0048 | 运行状态 | Run State | Run_state |  |  |  | {0x00:正常;0x01:禁充;0x02:禁放;0x03:待机;0x04:停机} | {0x00:Normal;0x01:Full;0x02:Empty;0x03:Standby;0x04:Stop} | [0~4] |  | Hex | R | U16 |  |  | BAU | 0x1031
0x0044 | 充放电状态 | Chg/Dsg | Chg/Dsg_state |  |  |  | {0x00:静置;0x01:放电;0x02:充电} | {0x00:Rest;0x01:Dsg;0x02:Chg} | [0~2] |  | Hex | R | U16 |  |  | BAU | 0x1032
0x009F | 干接点输出状态 | Dry Contact Output Status | dry_contact_output_status | bit(0~3): 干接点(1~4)输出 | bit(0~3):Dry(1~4) Contact Output Status | dry(1~4)_contact_output_status | {0:低电平;1:高电平} | {0:Low;1:High} | [0~1] |  | Hex | R | U16 |  |  | BAU | 0x1033
0x007B | 心跳 | Heartbeat | heartbeat | 预留 | Reserved | [6 empty] | R | U16 |  |  | BAU | 0x1034
0x00C1 | 总控自动分配主控ID | Assign Racks ID Auto | BCU_address_distribute |  |  |  | {0:初始化;1:启动分配;2:分配成功;3:分配失败;11:网络分配} | {0:Initialization;1:Start Distribute;2:Distribute Success;3:Distribute Fail;11:Network Distribution} | [0~11] |  |  | R/W | U16 |  | {1:CAN分配;11:TCP分配} | BAU | 0x1035
| 预留 | reserve8 | reserve8 | [8 empty] | R | U16 | 131 |  |  | 0x1036
0x00AD | 主控对外复归报警汇总1 | External Revert Alarm1 Summary | External_revert_alarm1_sum | bit0:簇总压过高复归 | bit0:Total OV Revert | Total_OV_revert | {0:正常;1:报警} | {0:Normal;1:Alarm} | [0~1] |  | Hex | R | U16 |  |  | BAU | 0x10B9
| 主控对外复归报警汇总1 | External Revert Alarm1 Summary |  | bit1:簇总压过低复归 | bit1:Total UV Revert | Total_UV_revert | {0:正常;1:报警} | {0:Normal;1:Alarm} | [0~1]
| 主控对外复归报警汇总1 | External Revert Alarm1 Summary |  | bit2:单体电压过高复归 | bit2:Cell OV Revert | Cell_OV_revert | {0:正常;1:报警} | {0:Normal;1:Alarm} | [0~1]
| 主控对外复归报警汇总1 | External Revert Alarm1 Summary |  | bit3:单体电压过低复归 | bit3:Cell UV Revert | Cell_UV_revert | {0:正常;1:报警} | {0:Normal;1:Alarm} | [0~1]
| 主控对外复归报警汇总1 | External Revert Alarm1 Summary |  | bit4:放电电流过大复归 | bit4:Dsg OC Revert | Dsg_OC_revert | {0:正常;1:报警} | {0:Normal;1:Alarm} | [0~1]
| 主控对外复归报警汇总1 | External Revert Alarm1 Summary |  | bit5:充电电流过大复归 | bit5:Chg OC Revert | Chg_OC_revert | {0:正常;1:报警} | {0:Normal;1:Alarm} | [0~1]
| 主控对外复归报警汇总1 | External Revert Alarm1 Summary |  | bit6:放电温度过高复归 | bit6:Dsg OT Revert | Dsg_OT_revert | {0:正常;1:报警} | {0:Normal;1:Alarm} | [0~1]
| 主控对外复归报警汇总1 | External Revert Alarm1 Summary |  | bit7:放电温度过低复归 | bit7:Dsg UT Revert | Dsg_UT_revert | {0:正常;1:报警} | {0:Normal;1:Alarm} | [0~1]
| 主控对外复归报警汇总1 | External Revert Alarm1 Summary |  | bit8:充电温度过高复归 | bit8:Chg OT Revert | Chg_OT_revert | {0:正常;1:报警} | {0:Normal;1:Alarm} | [0~1]
| 主控对外复归报警汇总1 | External Revert Alarm1 Summary |  | bit9:充电温度过低复归 | bit9:Chg UT Revert | Chg_UT_revert | {0:正常;1:报警} | {0:Normal;1:Alarm} | [0~1]
| 主控对外复归报警汇总1 | External Revert Alarm1 Summary |  | bit10:绝缘阻值过低复归 | bit10:Low IR Revert | Low_IR_revert | {0:正常;1:报警} | {0:Normal;1:Alarm} | [0~1]
| 主控对外复归报警汇总1 | External Revert Alarm1 Summary |  | bit11:极柱温度过高复归 | bit11:Term OT Revert | Term_OT_revert | {0:正常;1:报警} | {0:Normal;1:Alarm} | [0~1]
| 主控对外复归报警汇总1 | External Revert Alarm1 Summary |  | bit12:高压箱温度过高复归 | bit12:PDU OT Revert | PDU_OT_revert | {0:正常;1:报警} | {0:Normal;1:Alarm} | [0~1]
| 主控对外复归报警汇总1 | External Revert Alarm1 Summary |  | bit13:单体压差过大复归 | bit13:Cell OV Diff Revert | Cell_OV_diff_revert | {0:正常;1:报警} | {0:Normal;1:Alarm} | [0~1]
| 主控对外复归报警汇总1 | External Revert Alarm1 Summary |  | bit14:单体温差过大复归 | bit14:Cell OT Diff Revert | Cell_OT_diff_revert | {0:正常;1:报警} | {0:Normal;1:Alarm} | [0~1]
| 主控对外复归报警汇总1 | External Revert Alarm1 Summary |  | bit15:预留 | bit15:Reserved | Reserved
0x00AE | 主控对外复归报警汇总2 | External Revert Alarm2 Summary | External_revert_alarm2_sum | bit0:簇总压校验差过大复归 | bit0:Rack Voltage Calibration Revert | Vrack_cal_diff_revert | {0:正常;1:报警} | {0:Normal;1:Alarm} | [0~1] |  | Hex | R | U16 |  |  | BAU | 0x10BA
| 主控对外复归报警汇总2 | External Revert Alarm2 Summary |  | bit1:Pack电压过高复归 | bit1:Pack OV Revert | Module_OV_revert | {0:正常;1:报警} | {0:Normal;1:Alarm} | [0~1]
| 主控对外复归报警汇总2 | External Revert Alarm2 Summary |  | bit2:Pack电压过低复归 | bit2:Pack UV Revert | Module_UV_revert | {0:正常;1:报警} | {0:Normal;1:Alarm} | [0~1]
| 主控对外复归报警汇总2 | External Revert Alarm2 Summary |  | bit3:单体温升过高复归 | bit3:Cell Temp Rise Revert | Cell_temp_rise_revert | {0:正常;1:报警} | {0:Normal;1:Alarm} | [0~1]
| 主控对外复归报警汇总2 | External Revert Alarm2 Summary |  | bit4:Pack压差过大复归 | bit4:Pack OV Diff Revert | Module_OV_diff_revert | {0:正常;1:报警} | {0:Normal;1:Alarm} | [0~1]
| 主控对外复归报警汇总2 | External Revert Alarm2 Summary |  | bit5:动环报警汇总复归 | bit5:Run Alarm Summary | Run_alarm_summary | {0:正常;1:报警} | {0:Normal;1:Alarm} | [0~1]
| 主控对外复归报警汇总2 | External Revert Alarm2 Summary |  | bit6:铜排温度过高复归 | bit6:Busbar OT Revert | Copper_OT_revert | {0:正常;1:报警} | {0:Normal;1:Alarm} | [0~1]
| 主控对外复归报警汇总2 | External Revert Alarm2 Summary |  | bit7:充电单体压差过大复归 | bit7:Chg Cell Volt Diff Revert | Chg_cell_volt_diff_revert | {0:正常;1:报警} | {0:Normal;1:Alarm} | [0~1]
| 主控对外复归报警汇总2 | External Revert Alarm2 Summary |  | bit8:充电单体温差过大复归 | bit8:Chg Cell Temp Diff Revert | Chg_cell_temp_diff_revert | {0:正常;1:报警} | {0:Normal;1:Alarm} | [0~1]
| 主控对外复归报警汇总2 | External Revert Alarm2 Summary |  | bit9:充电Pack压差过大复归 | bit9:Chg Pack Volt Diff Revert | Chg_module_volt_diff_revert | {0:正常;1:报警} | {0:Normal;1:Alarm} | [0~1]
| 主控对外复归报警汇总2 | External Revert Alarm2 Summary |  | bit10:放电单体压差过大复归 | bit10:Dsg Cell Volt Diff Revert | Dsg_cell_volt_diff_revert | {0:正常;1:报警} | {0:Normal;1:Alarm} | [0~1]
| 主控对外复归报警汇总2 | External Revert Alarm2 Summary |  | bit11:放电单体温差过大复归 | bit11:Chg Cell Temp Diff Revert | Dsg_cell_temp_diff_revert | {0:正常;1:报警} | {0:Normal;1:Alarm} | [0~1]
| 主控对外复归报警汇总2 | External Revert Alarm2 Summary |  | bit12:放电Pack压差过大复归 | bit12:Chg Pack Volt Diff Revert | Dsg_module_volt_diff_revert | {0:正常;1:报警} | {0:Normal;1:Alarm} | [0~1]
|  |  |  | bit13:预留 | bit13:Reserve1 | Reserved1
|  |  |  | bit14:Pack内温差过大复归 | bit14:Pack Temp Diff Revert | Pack_temp_diff_revert | {0:正常;1:报警} | {0:Normal;1:Alarm} | [0~1]
| 主控对外复归报警汇总2 | External Revert Alarm2 Summary |  | bit15:预留 | bit15:Reserve2 | Reserved2
0x00AF | 总控对外复归报警 | BAU External Revert Alarm | BAU_External_ revert_alarm | bit0:簇间电流差过大复归 | bit0:Rack OC Diff Revert | Rack_OC_diff_revert | {0:正常;1:故障} | {0:Normal;1:Fault} | [0~1] |  | Hex | R | U16 |  |  | BAU | 0x10BB
| 总控对外复归报警 | BAU External Revert Alarm |  | bit1:簇间压差过大复归 | bit1:Rack OV Diff Revert | Rack_OV_diff_revert | {0:正常;1:故障} | {0:Normal;1:Fault} | [0~1]
| 总控对外复归报警 | BAU External Revert Alarm |  | bit[2~15]:预留 | bit[2~15]:Reserved | Reserved
0x0088 | 总控对外三级报警信息（Warning） | BAU External Level3 Alarm | external_bau_lv3_alm_sum | bit0:簇间电流差预警 | bit0:Lv1 Rack Cur Diff Warn | lv1_rack_cur_diff_warn | {0:正常;1:报警} | {0:Normal;1:Alarm} | [0~1] |  | Hex | R | U16 |  |  | BAU | 0x10BC
| 总控对外三级报警信息（Warning） | BAU External Level3 Alarm |  | bit1:簇间压差预警 | bit1:Lv1 Rack Vol Diff Warn | lv1_rack_vol_diff_warn | {0:正常;1:报警} | {0:Normal;1:Alarm} | [0~1]
| 总控对外三级报警信息（Warning） | BAU External Level3 Alarm |  | bit2:动环预警汇总 | bit2:Lv1 Envi Summary | lv1_envi_Summary | {0:正常;1:报警} | {0:Normal;1:Alarm} | [0~1]
0x0089 | 总控对外二级报警信息（Alarm） | BAU External Level2 Alarm | external_bau_lv2_alm_sum | bit0:簇间电流差报警 | bit0:Lv2 Rack Cur Diff Alm | lv2_rack_cur_diff_alm | {0:正常;1:报警} | {0:Normal;1:Alarm} | [0~1] |  | Hex | R | U16 |  |  | BAU | 0x10BD
| 总控对外二级报警信息（Alarm） | BAU External Level2 Alarm |  | bit1:簇间压差报警 | bit1:Lv2 Rack Vol Diff Alm | lv2_rack_vol_diff_alm | {0:正常;1:报警} | {0:Normal;1:Alarm} | [0~1]
| 总控对外二级报警信息（Alarm） | BAU External Level2 Alarm |  | bit2:动环报警汇总 | bit2:Lv2 Envi Summary | lv2_envi_Summary | {0:正常;1:报警} | {0:Normal;1:Alarm} | [0~1]
0x008A | 总控对外一级报警信息（Critical） | BAU External Level1 Alarm | external_bau_lv1_alm_sum | bit0:簇间电流差保护 | bit0:Lv3 Rack Cur Diff Critical | lv3_rack_cur_diff_critical | {0:正常;1:报警} | {0:Normal;1:Alarm} | [0~1] |  | Hex | R | U16 |  |  | BAU | 0x10BE
| 总控对外一级报警信息（Critical） | BAU External Level1 Alarm |  | bit1:簇间压差保护 | bit1:Lv3 Rack Vol Diff Critical | lv3_rack_vol_diff_critical | {0:正常;1:报警} | {0:Normal;1:Alarm} | [0~1]
| 总控对外一级报警信息（Critical） | BAU External Level1 Alarm |  | bit2:动环保护汇总 | bit2:Lv3 Envi Summary | lv3_envi_Summary | {0:正常;1:报警} | {0:Normal;1:Alarm} | [0~1]
| 预留 | reserve9 | reserve9 | [7 empty] | Hex | R | U16 | 2 |  | BAU | 0x10BF
0x0A20 | 主控通信故障(簇33-簇48) | BAU Comm Fault(BCU33-BCU48) | BAU_comm_fault_3 | bit(0~15):主控(33~48)通信故障 | bit(0~15):BCU(33~48) COMM Fault | BCU(33~48)_COMM_Fault | {0:正常;1:故障} | {0:Normal;1:Fault} | [0~1] |  | Hex | R | U16 |  |  | BAU | 0x10C1
| 预留 | reserve10 | reserve10 | [7 empty] | Hex | R | U16 | 7 |  | BAU | 0x10C2
0x0A26 | Rack使能状态(簇33-簇48) | Rack Enable Status(BCU33-BCU48) | rack_enable_status_3 | bit(0~15):Rack(33~48)启用/停用状态 | bit(0~15):Rack(33~48) Enable Status | rack(33~48)_enable_status | {0:停用;1:启用} | {0:Disenable;1:Enable} | [0~1] |  | Hex | R | U16 |  |  | BAU | 0x10C9
| 预留 | reserve11 | reserve11 | [7 empty] | Hex | R | U16 | 7 |  | BAU | 0x10CA
0x0A2C | 并网状态(簇33-簇48) | Rack Connect Status(BCU33-BCU48) | rack_connect_status_3 | bit(0~15):Rack(33~48)并网状态 | bit(0~15):Rack(33~48) Connect Status | rack(33~48)_connect_status | {0:离网;1:在网} | {0:Disconnected;1:Connected} | [0~1] |  | Hex | R | U16 |  |  | BAU | 0x10D1
| 预留 | reserve14 | reserve14 | [10 empty] | 5 |  |  | 0x10D2
| 标注协议预留位置 | reserve12 |  | 无 | 无 | [6 empty] | R/W | u16 | 228 | 项目不可以使用该空间 | EMS | 0x10D7
| 项目部门预留位置 | reserve13 |  | 无 | 无 | [6 empty] | R/W | u16 | 256 | 特殊项目可以使用该空间 | EMS | 0x11BB

## Bank Measure
Bank Information -- EMS Read from BMS
偏移地址 | 配置项中文名 | 配置项英文名 | 英文key | 中文使用说明 | 英文使用说明 | 英文子key | 说明(值/枚举说明) | 说明(值/枚举说明)(英文) | 范围 | 单位系数 | 单位 | 是否可写 | 数值格式 | 个数 | 备注 | 数据源 | Modbus地址
0x0049 | 堆电压 | Bank Voltage | Bank_voltage | [6 empty] | 0.1 | V | R | U16 |  |  | BAU | 0x2001
0x0590 | 堆电流 | Bank Curr | Ibank | [6 empty] | 0.1 | A | R | S32 |  |  | BAU | 0x2002
0x0047 | SOC | SOC | SOC | [6 empty] | 0.1 | % | R | U16 |  |  | BAU | 0x2004
0x0050 | SOH | SOH | Bank_SOH | [6 empty] | 0.1 | % | R | U16 |  |  | BAU | 0x2005
0x004A | 绝缘电阻 | IR | IR | [7 empty] | kΩ | R | U16 |  |  | BAU | 0x2006
0x004B | 可充电能量 | E_chargable | Echg_avl | [7 empty] | kWh | R | U16 |  |  | BAU | 0x2007
0x004C | 可放电能量 | E_dischargable | Edsg_avl | [7 empty] | kWh | R | U16 |  |  | BAU | 0x2008
0x004E | 允许充电电流 | I_chg_limit | Ibank_chg_lim | 系统对外充电SOP | System External Charging SOP |  |  |  |  | 0.1 | A | R | U16 |  |  | BAU | 0x2009
0x004F | 允许放电电流 | I_dsg_limit | Ibank_dsg_lim | 系统对外放电SOP | System External Discharge SOP |  |  |  |  | 0.1 | A | R | U16 |  |  | BAU | 0x200A
0x0071 | 簇间电流差 | Max IRack Diff | Irack_diff | [6 empty] | 0.1 | A | R | U16 |  | 当母线电流绝对值大于10A时开始计算簇间电流差，否则为0. （防止静置时因为环流触发告警）,堆中最大的簇电流减去最小的簇电流的值 | BAU | 0x200B
0x0072 | 簇间最大总压差 | Max Vrack Diff | Vrack_diff | [6 empty] | 0.1 | V | R | U16 |  | 堆中最大的簇总压减去最小的簇总压 | BAU | 0x200C
0x0051 | 最高电压电池所在Rack号 | Bank Max Vol Rack Num | Vcell_max_rack | [8 empty] | R | U16 |  | 1～最大Rack数 | BAU | 0x200D
0x0052 | 最高电压电池所在组 | Bank Max Vol Pack Num | Vcell_max_pack | [8 empty] | R | U16 |  | 该电池所在的从控编号, 1～最大从控编号 | BAU | 0x200E
0x0053 | 最高电压电池所在位置 | Bank Max Vol Cell Num | Vcell_max_position | [8 empty] | R | U16 |  | 该电池在电池箱内的ID, 1～从控电池串数 | BAU | 0x200F
0x0054 | 最高单体电压 | Vcell_max | Vcell_max | [7 empty] | mV | R | U16 |  |  | BAU | 0x2010
0x0055 | 最低电压电池所在Rack号 | Bank Min Vol Rack Num | Vcell_min_rack | [8 empty] | R | U16 |  | 1～最大Rack数 | BAU | 0x2011
0x0056 | 最低电压电池所在组 | Bank Min Vol Pack Num | Vcell_min_pack | [8 empty] | R | U16 |  | 该电池所在的从控编号, 1～最大从控编号 | BAU | 0x2012
0x0057 | 最低电压电池所在位置 | Bank Min Vol Cell Num | Vcell_min_position | [8 empty] | R | U16 |  | 该电池在电池箱内的ID, 1～从控电池串数 | BAU | 0x2013
0x0058 | 最低单体电压 | Vcell_min | Vcell_min | [7 empty] | mV | R | U16 |  |  | BAU | 0x2014
0x0070 | 平均单体电压 | Vcell_avg | Vavg | [7 empty] | mV | R | U16 |  |  | BAU | 0x2015
0x0059 | 最高温度电池所在Rack号 | Bank Max Temp Pack Num | Tcell_max_rack | [8 empty] | R | U16 |  | 1～最大Rack数 | BAU | 0x2016
0x005A | 最高温度电池所在组 | Bank Max Temp Cell Num | Tcell_max_pack | [8 empty] | R | U16 |  | 该电池所在的从控编号, 1～最大从控编号 | BAU | 0x2017
0x005B | 最高温度电池所在位置 | Bank Max Vol Cell Num | Tcell_max_position | [8 empty] | R | U16 |  | 该电池在电池箱内的ID, 1～从控电池串数 | BAU | 0x2018
0x005C | 最高单体温度 | Tcell_max | Tcell_max | [6 empty] | 0.1 | ℃ | R | S16 |  |  | BAU | 0x2019
0x005D | 最低温度电池所在Rack号 | Bank Min Temp Rack Num | Tcell_min_rack | [8 empty] | R | U16 |  | 1～最大Rack数 | BAU | 0x201A
0x005E | 最低温度电池所在组 | Bank Min Temp Pack Num | Tcell_min_pack | [8 empty] | R | U16 |  | 该电池所在的从控编号, 1～最大从控编号 | BAU | 0x201B
0x005F | 最低温度电池所在位置 | Bank Min Temp Cell Num | Tcell_min_position | [8 empty] | R | U16 |  | 该电池在电池箱内的ID, 1～从控电池串数 | BAU | 0x201C
0x0060 | 最低单体温度 | Tcell_min | Tcell_min | [6 empty] | 0.1 | ℃ | R | S16 |  |  | BAU | 0x201D
0x006f | 平均单体温度 | Tcell_avg | Tavg | [6 empty] | 0.1 | ℃ | R | S16 |  | 16位有符号数 | BAU | 0x201E
0x0061 | 累计充电能量 | E_chg_sum | Bank_Echg_cum | [7 empty] | kWh | R | U32 |  |  | BAU | 0x201F
0x0063 | 累计放电能量 | E_dsg_sum | Bank_Edsg_cum | [7 empty] | kWh | R | U32 |  |  | BAU | 0x2021
0x04C0 | 在网簇数 | Conn Racks | grid_connect_clu_num | [8 empty] | R | U16 |  |  | BAU | 0x2023
0x04C1 | 系统总簇数 | System Total Racks | System_total_racks | [8 empty] | R | U16 |  |  | BAU | 0x2024
0x0003 | 最小并网簇数 | Minimum Connected Racks Number | Min_connected_racks | [8 empty] | R/W | U16 |  |  | BAU | 0x2025
0x0069 | 堆允许放电功率 | BankDsg Power Limit | Bank_dsgable_power | [7 empty] | kW | R | U16 |  |  | BAU | 0x2026
0x006a | 堆允许充电功率 | Bank Chg Power Limit | Bank_chgable_power | [7 empty] | kW | R | U16 |  |  | BAU | 0x2027
0x006d | 当天放电能量 | Today Dsg Cum Cap | Bank_today_dsg_energy | [7 empty] | kWh | R | U16 |  |  | BAU | 0x2028
0x006e | 当天充电能量 | Today Chg Cum Cap | Bank_today_chg_energy | [7 empty] | kWh | R | U16 |  |  | BAU | 0x2029
0x0580 | 当月累计充电能量 | Month Echg Cum | Month_Echg_cum | [7 empty] | kWh | R | U32 |  |  | BAU | 0x202A
0x0582 | 当月累计放电能量 | Month Edsg Cum | Month_Edsg_cum | [7 empty] | kWh | R | U32 |  |  | BAU | 0x202C
0x0584 | 当年累计充电能量 | Year Echg Cum | Year_Echg_cum | [7 empty] | kWh | R | U32 |  |  | BAU | 0x202E
0x0586 | 当年累计放电能量 | Year Edsg Cum | Year_Edsg_cum | [7 empty] | kWh | R | U32 |  |  | BAU | 0x2030
| 标注协议预留位置 | reserve20 |  | 无 | 无 | [6 empty] | R/W | u16 | 246 | 项目不可以使用该空间 | EMS | 0x2032
| 项目部门预留位置 | reserve21 |  | 无 | 无 | [6 empty] | R/W | u16 | 256 | 特殊项目可以使用该空间 | EMS | 0x2128

## Bank Control
Bank Information -- EMS Write into BMS(BAU)
偏移地址 | 配置项中文名 | 配置项英文名 | 英文key | 中文使用说明 | 英文使用说明 | 英文子key | 说明(值/枚举说明) | 说明(值/枚举说明)(英文) | 范围 | 单位系数 | 单位 | 是否可写 | 数值格式 | 个数 | 备注 | 数据源 | Modbus地址
0x00C3 | 一键并网 | Auto Connected | Auto_onnected |  |  |  | {0x01:闭合;0x02:断开} | {0x01:Close;0x02:Cut off} | [0~1] |  |  | R/W | U16 |  |  | HMI or EMS | 0x3001
0x0005 | 总控复位 | Reset | reset |  |  |  | {0:无效;1:复位} | {0:invalidity;1:Reset} | [0~1] |  |  | R/W | U16 |  |  | EMS | 0x3002
0x0011 | 绝缘采样开关 | IR Detection Function | Insulation_sampling_switch |  |  |  | {1:开启;2:关闭} | {1:On;2:OFF} | [1~2] |  |  | R/W | U16 |  |  | HMI | 0x3003
0x00C0 | 清除PCS待机失败报警 | Clear PCS Standby Fail Alarm | Clear_PCS_standby_fail_alarm |  |  |  | {0:无效;1:清除报警} | {0:invalidity;1:Clear} | [0~1] |  |  | R/W | U16 |  |  | EMS | 0x3004
0x0400 | Rack1使能控制 | Rack1 Enable Control | Rack1_enable_control |  |  |  | {1:使能;2:禁止} | {1:Enable;2:Prohibit} | [1~2] |  |  | R/W | U16 | 32 |  | HMI or EMS | 0x3005
0x0800 | Rack33使能控制 | Rack33 Enable Control | Rack33_enable_control |  |  |  | {1:使能;2:禁止} | {1:Enable;2:Prohibit} | [1~2] |  |  | R/W | U16 | 16 |  | HMI or EMS | 0x3025
| 预留 | reserve15 | reserve15 | [10 empty] | 16 |  |  | 0x3035
0x00CA | 本地/远程控制 | Local Remote Control | local_remote_ctrl |  |  |  | {0:本地+远程;1:本地;2:远程} | {0:Local&Remote;1:Loca;2:Remote} | [0~2] |  |  | R/W | U16 |  |  | HMI or EMS | 0x3045
0x00C1 | 总控自动分配主控ID | Assign Racks ID Auto | BCU_address_distribute |  |  |  | {0:初始化;1:启动分配;2:分配成功;3:分配失败;11:网络分配} | {0:Initialization;1:Start Distribute;2:Distribute Success;3:Distribute Fail;11:Network Distribution} | [0~11] |  |  | R/W | U16 |  | {1:CAN分配;11:TCP分配} |  | 0x3046
0x0019 | 一键复归 | Auto Revert | One_Click_revert |  |  |  | {0:无效;1:复归} | {0:invalidity;1:triger} | [0~1] |  |  | R/W | U16 |  |  |  | 0x3047
0x003A | 外部电气器件控制 | Cabinet Breaker | extern_ElecDev_ctrl_on_off | bit[0~1]:电操控制 | bit[0~1]:Extern ElecDev Ctrl On Off | extern_ElecDev_ctrl_on_off | {0:初始状态;1:闭合电操;2:断开电操;3:脱扣电操} | {0:Initialization state;1:Close;2:Open;3:Disconnect} | [0~3] |  | Hex | R/W | U16 |  | 电操（断路器） |  | 0x3048
| 外部电气器件控制 | Cabinet Breaker |  | bit[2~15]:预留 | bit[2~15]:Reserve | reserve | [5 empty] | R/W
| 预留64 | reserve31 |  |  |  |  | {1:使能;2:禁止} | {1:Enable;2:Prohibit} | [1~2] |  |  | R/W | U16 | 64 |  | HMI or EMS | 0x3049
| 标注协议预留位置 | reserve32 |  |  | 无 | [6 empty] | R/W | u16 | 189 | 项目不可以使用该空间 | EMS | 0x3089
| 项目部门预留位置 | reserve33 |  |  | 无 | [6 empty] | R/W | u16 | 256 | 特殊项目可以使用该空间 | EMS | 0x3146

## Bank Parameter Set & Read
BANK Alarm Parameter Threshold Set & Read
Register type: Rack参数设置(保持寄存器, 每Rack Modbus地址独立,从2开始,功能码:0x10或0x06); Rack Parameter Settings (Holding Registers Modbus Addr:each rack independent,from 2 Function Code:0x10 or 0x06)
Modbus Addr: 2 to N+1 (N is rack number)
偏移地址 | 配置项中文名 | 配置项英文名 | 英文key | 中文使用说明 | 英文使用说明 | 英文子key | 说明(值/枚举说明) | 说明(值/枚举说明)(英文) | 范围 | 单位系数 | 单位 | 是否可写 | 数值格式 | 个数 | 备注 | 数据源 | Modbus地址
0x000E | 静态簇间压差过大三级报警 | Static Rack Volt Diff Level 3 Alarm | Static_rack_volt_diff_trigger | [5 empty] | [-32767~32767] | 0.1 | V | R/W | S16 |  |  | BAU, BCU[1] | 0x5001
0x000F | 静态簇间压差过大三级报警恢复值 | Static Rack Volt Diff Level 3 Alarm Recovery | Static_rack_volt_diff_recovery | [5 empty] | [-32767~32767] | 0.1 | V | R/W | S16 |  |  | BAU, BCU[1] | 0x5002
0x0030 | 动态簇间压差过大三级报警 | Dynamic Rack Volt Diff Trigger | Dynamic_rack_volt_diff_trigger | [5 empty] | [-32767~32767] | 0.1 | V | R/W | S16 |  |  | BAU, BCU[1] | 0x5003
0x0031 | 动态簇间压差过大三级报警恢复值 | Dynamic Rack Volt Diff Recovery | Dynamic_rack_volt_diff_recovery | [5 empty] | [-32767~32767] | 0.1 | V | R/W | S16 |  |  | BAU, BCU[1] | 0x5004
0x0032 | 簇间电流差过高一级报警 | Rack OC Diff Level1 Alarm | Rack_OC_diff_lvl1_trigger | [5 empty] | [-32767~32767] | 0.1 | A | R/W | S16 |  |  | BAU, BCU[1] | 0x5005
0x0035 | 簇间电流差过高一级报警恢复值 | Rack OC Diff Level1 Alarm Recovery | Rack_OC_diff_lvl1_recovery | [5 empty] | [-32767~32767] | 0.1 | A | R/W | S16 |  |  | BAU, BCU[1] | 0x5006
0x0033 | 簇间电流差过高二级报警 | Rack OC Diff Level2 Alarm | Rack_OC_diff_lvl2_trigger | [5 empty] | [-32767~32767] | 0.1 | A | R/W | S16 |  |  | BAU, BCU[1] | 0x5007
0x0036 | 簇间电流差过高二级报警恢复值 | Rack OC Diff Level2 Alarm Recovery | Rack_OC_diff_lvl2_recovery | [5 empty] | [-32767~32767] | 0.1 | A | R/W | S16 |  |  | BAU, BCU[1] | 0x5008
0x0034 | 簇间电流差过高一级报警恢复值 | Rack OC Diff Level1 Alarm Recovery | Rack_OC_diff_lvl1_recovery | [5 empty] | [-32767~32767] | 0.1 | A | R/W | S16 |  |  | BAU, BCU[1] | 0x5009
0x0037 | 簇间电流差过高三级报警恢复值 | Rack OC Diff Level3 Alarm Recovery | Rack_OC_diff_lvl3_recovery | [5 empty] | [-32767~32767] | 0.1 | A | R/W | S16 |  |  | BAU, BCU[1] | 0x500A
0x01C0 | 动态簇间压差过大二级报警 | Dynamic Rack Volt Diff Alarm Trigger | Dyn_rack_volt_diff_alarm_trigger | [5 empty] | [-32767~32767] | 0.1 | V | R/W | S16 |  |  | BAU | 0x500B
0x01C1 | 动态簇间压差过大一级报警 | Dynamic Rack Volt Diff Protection Trigger | Dyn_rack_volt_diff_protection_trigger | [5 empty] | [-32767~32767] | 0.1 | V | R/W | S16 |  |  | BAU | 0x500C
0x01C2 | 静态簇间压差过大二级报警 | Static Rack Volt Diff Level 2 Alarm | Stat_rack_volt_diff_alarm_trigger | [5 empty] | [-32767~32767] | 0.1 | V | R/W | S16 |  |  | BAU | 0x500D
0x01C3 | 静态簇间压差过大一级报警 | Static Rack Volt Diff Level 1 Alarm | Stat_rack_volt_diff_protection_trigger | [5 empty] | [-32767~32767] | 0.1 | V | R/W | U16 |  |  | BAU | 0x500E
0x01C4 | 动态簇间压差过大二级报警恢复值 | Dynamic Rack Volt Diff Alarm Recovery | Dyn_rack_volt_diff_alarm_recovery | [5 empty] | [-32767~32767] | 0.1 | V | R/W | S16 |  |  | BAU | 0x500F
0x01C5 | 动态簇间压差过大一级报警恢复值 | Dynamic Rack Volt Diff Protection Recovery | Dyn_rack_volt_diff_protection_recovery | [5 empty] | [-32767~32767] | 0.1 | V | R/W | S16 |  |  | BAU | 0x5010
0x01C6 | 静态簇间压差过大二级报警恢复值 | Static Rack Volt Diff Level 2 Alarm Recovery | Stat_rack_volt_diff_alarm_recovery | [5 empty] | [-32767~32767] | 0.1 | V | R/W | S16 |  |  | BAU | 0x5011
0x01C7 | 静态簇间压差过大一级报警恢复值 | Static Rack Volt Diff Level 1 Alarm Recovery | Stat_rack_volt_diff_protection_recovery | [5 empty] | [-32767~32767] | 0.1 | V | R/W | S16 |  |  | BAU | 0x5012
| 预留 | reserve40 | reserve40 | [8 empty] | R/W | U16 | 493 |  |  | 0x5013
0x0200 | 网口1本地IP地址1 | IP Address | IP_address_1 | [5 empty] | [0~255] |  |  | R/W | U16 |  |  | HMI or EMS | 0x5200
0x0201 | 网口1本地IP地址2 | IP Address | IP_address_2 | [5 empty] | [0~255] |  |  | R/W | U16 |  |  | HMI or EMS | 0x5201
0x0202 | 网口1本地IP地址3 | IP Address | IP_address_3 | [5 empty] | [0~255] |  |  | R/W | U16 |  |  | HMI or EMS | 0x5202
0x0203 | 网口1本地IP地址4 | IP Address | IP_address_4 | [5 empty] | [0~255] |  |  | R/W | U16 |  |  | HMI or EMS | 0x5203
0x0204 | 网口1默认网关1 | Gateway | Gateway_1 | [5 empty] | [0~255] |  |  | R/W | U16 |  |  | HMI or EMS | 0x5204
0x0205 | 网口1默认网关2 | Gateway | Gateway_2 | [5 empty] | [0~255] |  |  | R/W | U16 |  |  | HMI or EMS | 0x5205
0x0206 | 网口1默认网关3 | Gateway | Gateway_3 | [5 empty] | [0~255] |  |  | R/W | U16 |  |  | HMI or EMS | 0x5206
0x0207 | 网口1默认网关4 | Gateway | Gateway_4 | [5 empty] | [0~255] |  |  | R/W | U16 |  |  | HMI or EMS | 0x5207
0x0208 | 网口1子网掩码1 | Subnet Mask | Subnet_mask_1 | [5 empty] | [0~255] |  |  | R/W | U16 |  |  | HMI or EMS | 0x5208
0x0209 | 网口1子网掩码2 | Subnet Mask | Subnet_mask_2 | [5 empty] | [0~255] |  |  | R/W | U16 |  |  | HMI or EMS | 0x5209
0x020A | 网口1子网掩码3 | Subnet Mask | Subnet_mask_3 | [5 empty] | [0~255] |  |  | R/W | U16 |  |  | HMI or EMS | 0x520A
0x020B | 网口1子网掩码4 | Subnet Mask | Subnet_mask_4 | [5 empty] | [0~255] |  |  | R/W | U16 |  |  | HMI or EMS | 0x520B
0x0212 | 网口1Socket1本地端口 | Local Port | socket1_local_port | [5 empty] | [0~65535] |  |  | R/W | U16 |  |  | HMI or EMS | 0x520C
0x021A | 网口1Socket2本地端口 | Local Port | socket2_local_port | [5 empty] | [0~65535] |  |  | R/W | U16 |  |  | HMI or EMS | 0x520D
0x0222 | 网口1Socket3本地端口 | Local Port | socket3_local_port | [5 empty] | [0~65535] |  |  | R/W | U16 |  |  | HMI or EMS | 0x520E
0x022A | 网口1Socket4本地端口 | Net1 Socket4 Local Port | net1_socket4_local_port | [5 empty] | [0~65535] |  |  | R/W | U16 |  |  | HMI or EMS | 0x520F
0x0232 | 网口1Socket5本地端口 | Net1 Socket5 Local Port | net1_socket5_local_port | [5 empty] | [0~65535] |  |  | R/W | U16 |  |  | HMI or EMS | 0x5210
0x023A | 网口1Socket6本地端口 | Net1 Socket6 Local Port | net1_socket6_local_port | [5 empty] | [0~65535] |  |  | R/W | U16 |  |  | HMI or EMS | 0x5211
0x0242 | 网口1Socket7本地端口 | Net1 Socket7 Local Port | net1_socket7_local_port | [5 empty] | [0~65535] |  |  | R/W | U16 |  |  | HMI or EMS | 0x5212
0x024A | 网口1Socket8本地端口 | Net1 Socket8 Local Port | net1_socket8_local_port | [5 empty] | [0~65535] |  |  | R/W | U16 |  |  | HMI or EMS | 0x5213
0x024C | 网口2本地IP地址1 | Net2 IP 1 | net2_IP_1 | [5 empty] | [0~255] |  |  | R/W | U16 |  |  | HMI or EMS | 0x5214
0x024D | 网口2本地IP地址2 | Net2 IP 2 | net2_IP_2 | [5 empty] | [0~255] |  |  | R/W | U16 |  |  | HMI or EMS | 0x5215
0x024E | 网口2本地IP地址3 | Net2 IP 3 | net2_IP_3 | [5 empty] | [0~255] |  |  | R/W | U16 |  |  | HMI or EMS | 0x5216
0x024F | 网口2本地IP地址4 | Net2 IP 4 | net2_IP_4 | [5 empty] | [0~255] |  |  | R/W | U16 |  |  | HMI or EMS | 0x5217
0x0250 | 网口2网关IP地址1 | Net2 Gateway 1 | net2_gateway_1 | [5 empty] | [0~255] |  |  | R/W | U16 |  |  | HMI or EMS | 0x5218
0x0251 | 网口2网关IP地址2 | Net2 Gateway 2 | net2_gateway_2 | [5 empty] | [0~255] |  |  | R/W | U16 |  |  | HMI or EMS | 0x5219
0x0252 | 网口2网关IP地址3 | Net2 Gateway 3 | net2_gateway_3 | [5 empty] | [0~255] |  |  | R/W | U16 |  |  | HMI or EMS | 0x521A
0x0253 | 网口2网关IP地址4 | Net2 Gateway 4 | net2_gateway_4 | [5 empty] | [0~255] |  |  | R/W | U16 |  |  | HMI or EMS | 0x521B
0x0254 | 网口2子网掩码1 | Net2 Subnetmask 1 | net2_subnetmask_1 | [5 empty] | [0~255] |  |  | R/W | U16 |  |  | HMI or EMS | 0x521C
0x0255 | 网口2子网掩码2 | Net2 Subnetmask 2 | net2_subnetmask_2 | [5 empty] | [0~255] |  |  | R/W | U16 |  |  | HMI or EMS | 0x521D
0x0256 | 网口2子网掩码3 | Net2 Subnetmask 3 | net2_subnetmask_3 | [5 empty] | [0~255] |  |  | R/W | U16 |  |  | HMI or EMS | 0x521E
0x0257 | 网口2子网掩码4 | Net2 Subnetmask 4 | net2_subnetmask_4 | [5 empty] | [0~255] |  |  | R/W | U16 |  |  | HMI or EMS | 0x521F
0x025E | 网口2Socket1本地端口 | Net2 Socket1 Local Port | net2_socket1_local_port | [5 empty] | [0~65535] |  |  | R/W | U16 |  |  | HMI or EMS | 0x5220
0x0266 | 网口2Socket2本地端口 | Net2 Socket2 Local Port | net2_socket2_local_port | [5 empty] | [0~65535] |  |  | R/W | U16 |  |  | HMI or EMS | 0x5221
0x026E | 网口2Socket3本地端口 | Net2 Socket3 Local Port | net2_socket3_local_port | [5 empty] | [0~65535] |  |  | R/W | U16 |  |  | HMI or EMS | 0x5222
0x0276 | 网口2Socket4本地端口 | Net2 Socket4 Local Port | net2_socket4_local_port | [5 empty] | [0~65535] |  |  | R/W | U16 |  |  | HMI or EMS | 0x5223
0x027E | 网口2Socket5本地端口 | Net2 Socket5 Local Port | net2_socket5_local_port | [5 empty] | [0~65535] |  |  | R/W | U16 |  |  | HMI or EMS | 0x5224
0x0286 | 网口2Socket6本地端口 | Net2 Socket6 Local Port | net2_socket6_local_port | [5 empty] | [0~65535] |  |  | R/W | U16 |  |  | HMI or EMS | 0x5225
0x028E | 网口2Socket7本地端口 | Net2 Socket7 Local Port | net2_socket7_local_port | [5 empty] | [0~65535] |  |  | R/W | U16 |  |  | HMI or EMS | 0x5226
0x0296 | 网口2Socket8本地端口 | Net2 Socket8 Local Port | net2_socket8_local_port | [5 empty] | [0~65535] |  |  | R/W | U16 |  |  | HMI or EMS | 0x5227
| 年 | reserve_bank_year | reserve_bank_year | 以2000年为起始,设置兼容从0代表2000年和2000代表2000年 | Starting with the year 2000, compatible with 0 and 2000 for the year 2000. |  |  |  | [2000~65535] |  | year | R/W | U16 |  | 以2000年为起始 设置兼容从0代表2000年和2000代表2000年 | HMI or EMS | 0x5228
| 月 | reserve_bank_month | reserve_bank_month | 月(1--12) | Month (1--12) |  |  |  | [1~12] |  | month | R/W | U16 |  |  | HMI or EMS | 0x5229
| 日 | reserve_bank_day | reserve_bank_day | 日(1--31) | Day (1--31) |  |  |  | [1~31] |  | day | R/W | U16 |  |  | HMI or EMS | 0x522A
| 毫秒 | reserve41 | reserve41 |  | Millisecond 0~999 | [6 empty] | R/W | u16 |  | Millisecond | HMI or EMS | 0x522B
0x001B | NTP对时时区 | Time Zero | time_zero | [8 empty] | R/W | U16 |  |  | HMI or EMS | 0x522C
0x0006 | 年 | Bank Year | bank_year | 以2000年为起始,设置兼容从0代表2000年和2000代表2000年 | Starting with the year 2000, compatible with 0 and 2000 for the year 2000. |  |  |  | [2000~65535] |  | year | R/W | U16 |  | 以2000年为起始 设置兼容从0代表2000年和2000代表2000年 | HMI or EMS | 0x522D
0x0007 | 月 | Bank Month | bank_month | 月(1--12) | Month (1--12) |  |  |  | [1~12] |  | month | R/W | U16 |  |  | HMI or EMS | 0x522E
0x0008 | 日 | Bank Day | bank_day | 日(1--31) | Day (1--31) |  |  |  | [1~31] |  | day | R/W | U16 |  |  | HMI or EMS | 0x522F
0x0009 | 时 | Bank Hour | bank_hour | 时(0--23)24小时制 | Hour (0--23) 24-hour clock |  |  |  | [0~23] |  | hour | R/W | U16 |  |  | HMI or EMS | 0x5230
0x000A | 分 | Bank Minute | bank_minute | 分(0--59) | Minutes (0--59) |  |  |  | [0~60] |  | minute | R/W | U16 |  |  | HMI or EMS | 0x5231
0x000B | 秒 | Bank Second | bank_second | 秒(0--59) | Second(0--59) |  |  |  | [0~60] |  | s | R/W | U16 |  |  | HMI or EMS | 0x5232
0x00C4 | SMS心跳控制 | SMS Heartbeat Control | SMS_heartbeat_control | [8 empty] | R/W | U16 |  |  | EMS | 0x5233
| EIS测量频率数量 | [15 empty] | 0x5234
| EIS功能上电延迟时间 | [15 empty] | 0x5235
| EIS允许采样最小SOC | [15 empty] | 0x5236
| EIS允许采样最大SOC | [15 empty] | 0x5237
| EIS采样周期 | [15 empty] | 0x5238
| EIS允许采样静置时间 | [15 empty] | 0x5239
| EIS采样放电时间 | [15 empty] | 0x523A
| EIS测量频率配置 | [12 empty] | 100 |  |  | 0x523B
| EIS定频采样频率 | [15 empty] | 0x529F
| 标注协议预留位置 | reserve42 |  |  | 无 | [6 empty] | R/W | u16 | 151 | 项目不可以使用该空间 | EMS | 0x52A0
| 项目部门预留位置 | reserve43 |  |  | 无 | [6 empty] | R/W | u16 | 256 | 特殊项目可以使用该空间 | EMS | 0x5337

## Env(signal)
Rack Signal -- EMS Read From BMS(BAU)
偏移地址 | 配置项中文名 | 配置项英文名 | 英文key | 中文使用说明 | 英文使用说明 | 英文子key | 说明(值/枚举说明) | 说明(值/枚举说明)(英文) | 范围 | 单位系数 | 单位 | 是否可写 | 数值格式 | 个数 | 备注 | 数据源 | Modbus地址
0x002 | 空调通讯故障 | HVAC Comm Fault | HVAC_comm_fault | bit0:空调1通讯故障 | bit0:Air1 Comm Fault | Air1_Comm_Fault | {0:正常;1:故障} <0:绿色;1:红色> | {0:Normal;1:Fault} | [0~1] | 1 | Hex | R | U16 |  |  |  | 0x0600 | 1536 | 0x0600
0x005 | 液冷通讯故障 | Liquid Cooling Comm Fault | Liquid_cooling_comm_fault | bit0:液冷机1通讯故障 | bit0:Liquid Cooling1 Comm Fault | Liquid_Cooling1_Comm_Fault | {0:正常;1:故障} <0:绿色;1:红色> | {0:Normal;1:Fault} | [0~1] | 1 | Hex | R | U16 |  |  |  | 0x0601 | 1537 | 0x0601
0x007 | 电表通讯故障 | Energy Meter Comm Fault | Energy_meter_comm_fault | bit0:电表1通讯故障 | bit0:Energy Meter1 Comm Fault | Energy_Meter1_Comm_Fault | {0:正常;1:故障} <0:绿色;1:红色> | {0:Normal;1:Fault} | [0~1] | 1 | Hex | R | U16 |  |  |  | 0x0602 | 1538 | 0x0602
0x009 | 风冷机通讯故障 | Chiller Fan Comm Fault | Chiller_fan_comm_fault | bit0:除湿机1通讯故障 | bit0:Dehumidifier1 Comm Fault | Chiller_Fan1_Comm_Fault | {0:正常;1:故障} <0:绿色;1:红色> | {0:Normal;1:Fault} | [0~1] | 1 | Hex | R | U16 |  |  |  | 0x0603 | 1539 | 0x0603
|  |  |  | bit1:除湿机2通讯故障 | bit1:Dehumidifier2 Comm Fault | Chiller_Fan2_Comm_Fault | {0:正常;1:故障} <0:绿色;1:红色> | {0:Normal;1:Fault} | [0~1]
0x0121 | DI1舱内外急停 | E-Stop | DI1H | [5 empty] | [0~1] | 1 |  | R | U16 |  |  |  | 0x0604 | 1540 | 0x0604
0x0122 | DI2远方就地反馈 | Remote Local FBK Sig | DI2H | [5 empty] | [0~1] | 1 |  | R | U16 |  |  |  | 0x0605 | 1541 | 0x0605
0x0123 | 预留 | Reserved | DI3H | [5 empty] | [0~1] | 1 |  | R | U16 |  |  |  | 0x0606 | 1542 | 0x0606
0x0124 | DI4消防二级火警 | Fire Alarm Level 2 | DI4H | [5 empty] | [0~1] | 1 |  | R | U16 |  |  |  | 0x0607 | 1543 | 0x0607
0x0125 | DI5消防故障反馈 | Fire Fault FBK | DI5H | [5 empty] | [0~1] | 1 |  | R | U16 |  |  |  | 0x0608 | 1544 | 0x0608
0x0126 | DI6消防一级火警 | Fire Alarm Level 1 | DI6H | [5 empty] | [0~1] | 1 |  | R | U16 |  |  |  | 0x0609 | 1545 | 0x0609
0x0127 | DI7门禁反馈 | Access Door Feedback | DI7L | [5 empty] | [0~1] | 1 |  | R | U16 |  |  |  | 0x060A | 1546 | 0x060A
0x0128 | DI8电气舱水浸 | Electrical Cabinet Water Leak | DI8L | [5 empty] | [0~1] | 1 |  | R | U16 |  |  |  | 0x060B | 1547 | 0x060B
0x0129 | 预留 | Reserved | DI9L | [5 empty] | [0~1] | 1 |  | R | U16 |  |  |  | 0x060C | 1548 | 0x060C
0x012A | DI10电池舱水浸 | Battery Cabinet Water Leak | DI10L | [5 empty] | [0~1] | 1 |  | R | U16 |  |  |  | 0x060D | 1549 | 0x060D
0x012B | DI11直流断路器QS2断开 | DC Circuit Breaker QS2 Open | DI11L | [5 empty] | [0~1] | 1 |  | R | U16 |  |  |  | 0x060E | 1550 | 0x060E
0x012C | DI12交流防雷检测 | AC Surge/Lightning Fault | DI12L | [5 empty] | [0~1] | 1 |  | R | U16 |  |  |  | 0x060F | 1551 | 0x060F
0x012D | DI13消防喷洒反馈 | Fire Spray FBK | DI13H | [5 empty] | [0~1] | 1 |  | R | U16 |  |  |  | 0x0610 | 1552 | 0x0610
0x012E | DI14 UPS掉电反馈 | UPS Power Off Feedback | DI14L | [5 empty] | [0~1] | 1 |  | R | U16 |  |  |  | 0x0611 | 1553 | 0x0611
0x0101 | 预留 | Reserved | DI15 | [5 empty] | [0~1] | 1 |  | R | U16 |  |  |  | 0x0612 | 1554 | 0x0612
0x0102 | 预留 | Reserved | DI16 | [5 empty] | [0~1] | 1 |  | R | U16 |  |  |  | 0x0613 | 1555 | 0x0613
0x0141 | DO1 PCS干接点 | PCS Dry Contact | DO1 | [5 empty] | [0~1] | 1 |  | R | U16 |  |  |  | 0x0614 | 1556 | 0x0614
0x0142 | DO2故障指示灯 | Fault LED | DO2 | [5 empty] | [0~1] | 1 |  | R | U16 |  |  |  | 0x0615 | 1557 | 0x0615
0x0143 | DO3运行指示灯 | Run LED | DO3 | [5 empty] | [0~1] | 1 |  | R | U16 |  |  |  | 0x0616 | 1558 | 0x0616
0x0144 | DO4交直流脱扣 | AC/DC Trip Relay | DO4 | [5 empty] | [0~1] | 1 |  | R | U16 |  |  |  | 0x0617 | 1559 | 0x0617
0x0145 | 预留 | Reserved | DO5 | [5 empty] | [0~1] | 1 |  | R | U16 |  |  |  | 0x0618 | 1560 | 0x0618
0x0146 | 预留 | Reserved | DO6 | [5 empty] | [0~1] | 1 |  | R | U16 |  |  |  | 0x0619 | 1561 | 0x0619
0x0147 | 预留 | Reserved | DO7 | [5 empty] | [0~1] | 1 |  | R | U16 |  |  |  | 0x061A | 1562 | 0x061A
0x0148 | 预留 | Reserved | DO8 | [5 empty] | [0~1] | 1 |  | R | U16 |  |  |  | 0x061B | 1563 | 0x061B
0x0C01 | A相电压 | UA | EssMeter_1_1 | [6 empty] | 1 | V | R | U32 |  |  |  | 0x061C | 1564 | 0x061C
0x0C03 | B相电压 | UB | EssMeter_1_2 | [6 empty] | 1 | V | R | U32 |  |  |  | 0x061E | 1566 | 0x061E
0x0C05 | C相电压 | UC | EssMeter_1_3 | [6 empty] | 1 | V | R | U32 |  |  |  | 0x0620 | 1568 | 0x0620
0x0C07 | AB线电压 | UAB | EssMeter_1_4 | [6 empty] | 1 | V | R | U32 |  |  |  | 0x0622 | 1570 | 0x0622
0x0C09 | BC线电压 | UBC | EssMeter_1_5 | [6 empty] | 1 | V | R | U32 |  |  |  | 0x0624 | 1572 | 0x0624
0x0C0B | CA线电压 | UCA | EssMeter_1_6 | [6 empty] | 1 | V | R | U32 |  |  |  | 0x0626 | 1574 | 0x0626
0x0C0D | A相电流 | Ia | EssMeter_1_7 | [6 empty] | 1 | A | R | U32 |  |  |  | 0x0628 | 1576 | 0x0628
0x0C0F | B相电流 | Ib | EssMeter_1_8 | [6 empty] | 1 | A | R | U32 |  |  |  | 0x062A | 1578 | 0x062A
0x0C11 | C相电流 | Ic | EssMeter_1_9 | [6 empty] | 1 | A | R | U32 |  |  |  | 0x062C | 1580 | 0x062C
0x0C13 | N线电流 | In | EssMeter_1_10 | [6 empty] | 1 | A | R | U32 |  |  |  | 0x062E | 1582 | 0x062E
0x0C15 | A相有功功率 | Pa | EssMeter_1_11 | [6 empty] | 1 | kW | R | U32 |  |  |  | 0x0630 | 1584 | 0x0630
0x0C17 | B相有功功率 | Pb | EssMeter_1_12 | [6 empty] | 1 | kW | R | U32 |  |  |  | 0x0632 | 1586 | 0x0632
0x0C19 | C相有功功率 | Pc | EssMeter_1_13 | [6 empty] | 1 | kW | R | U32 |  |  |  | 0x0634 | 1588 | 0x0634
0x0C1B | 总有功功率 | Pt | EssMeter_1_14 | [6 empty] | 1 | kW | R | U32 |  |  |  | 0x0636 | 1590 | 0x0636
0x0C1D | A相无功功率 | Qa | EssMeter_1_15 | [6 empty] | 1 | Kvar | R | U32 |  |  |  | 0x0638 | 1592 | 0x0638
0x0C1F | B相无功功率 | Qb | EssMeter_1_16 | [6 empty] | 1 | Kvar | R | U32 |  |  |  | 0x063A | 1594 | 0x063A
0x0C21 | C相无功功率 | Qc | EssMeter_1_17 | [6 empty] | 1 | Kvar | R | U32 |  |  |  | 0x063C | 1596 | 0x063C
0x0C23 | 总无功功率 | Qt | EssMeter_1_18 | [6 empty] | 1 | Kvar | R | U32 |  |  |  | 0x063E | 1598 | 0x063E
0x0C25 | A相视在功率 | SA | EssMeter_1_19 | [6 empty] | 1 | KVA | R | U32 |  |  |  | 0x0640 | 1600 | 0x0640
0x0C27 | B相视在功率 | SB | EssMeter_1_20 | [6 empty] | 1 | KVA | R | U32 |  |  |  | 0x0642 | 1602 | 0x0642
0x0C29 | C相视在功率 | SC | EssMeter_1_21 | [6 empty] | 1 | KVA | R | U32 |  |  |  | 0x0644 | 1604 | 0x0644
0x0C2B | 总视在功率 | ST | EssMeter_1_22 | [6 empty] | 1 | KVA | R | U32 |  |  |  | 0x0646 | 1606 | 0x0646
0x0C2D | A相功率因数 | PFA | EssMeter_1_23 | [6 empty] | 1 |  | R | U32 |  |  |  | 0x0648 | 1608 | 0x0648
0x0C2F | B相功率因数 | PFB | EssMeter_1_24 | [6 empty] | 1 |  | R | U32 |  |  |  | 0x064A | 1610 | 0x064A
0x0C31 | C相功率因数 | PFC | EssMeter_1_25 | [6 empty] | 1 |  | R | U32 |  |  |  | 0x064C | 1612 | 0x064C
0x0C33 | 总功率因数 | PF | EssMeter_1_26 | [6 empty] | 1 |  | R | U32 |  |  |  | 0x064E | 1614 | 0x064E
0x0C35 | 频率 | F | EssMeter_1_27 | [6 empty] | 1 | Hz | R | U32 |  |  |  | 0x0650 | 1616 | 0x0650
0x0C37 | 相电压平均值 | UN Avg | EssMeter_1_28 | [6 empty] | 1 | V | R | U32 |  |  |  | 0x0652 | 1618 | 0x0652
0x0C39 | 线电压平均值 | UL Avg | EssMeter_1_29 | [6 empty] | 1 | V | R | U32 |  |  |  | 0x0654 | 1620 | 0x0654
0x0C3B | 电流平均值 | I Avg | EssMeter_1_30 | [6 empty] | 1 | A | R | U32 |  |  |  | 0x0656 | 1622 | 0x0656
0x01D1 | 运行状态 | Operating Status | Dehumidifier_1 | bit0:压缩机运行状态 | bit0:Compressor running status | Dehumidifier_1_1 | {0:停止;1:运行} | {0:Stop;1:Run} | [0~1] | 1 | Hex | R | U16 |  |  |  | 0x0658 | 1624 | 0x0658
|  |  |  | bit1:风机运行状态 | bit1:Fan running status | Dehumidifier_1_2 | {0:停止;1:运行} | {0:Stop;1:Run} | [0~1]
|  |  |  | bit2:化霜运行状态 | bit2:Defrosting running status | Dehumidifier_1_3 | {0:停止;1:运行} | {0:Stop;1:Run} | [0~1]
|  |  |  | bit3:预留 | bit3:Reserved | Dehumidifier_1_4
|  |  |  | bit4:预留 | bit4:Reserved | Dehumidifier_1_5
|  |  |  | bit5:预留 | bit5:Reserved | Dehumidifier_1_6
|  |  |  | bit6:预留 | bit6:Reserved | Dehumidifier_1_7
|  |  |  | bit7:预留 | bit7:Reserved | Dehumidifier_1_8
0x01D2 | 告警状态 | Alarm Status | Dehumidifier_2 | bit0:低温保护 | bit0:Low temperature protection | Dehumidifier_2_1 | {0:正常;1:故障} <0:绿色;1:红色> | {0:Normal;1:Fault} | [0~1] | 1 | Hex | R | U16 |  |  |  | 0x0659 | 1625 | 0x0659
|  |  |  | bit1:高温保护 | bit1:High temperature protection | Dehumidifier_2_2 | {0:正常;1:故障} <0:绿色;1:红色> | {0:Normal;1:Fault} | [0~1]
|  |  |  | bit2:盘管温度传感器故障状态 | bit2:Coil temperature sensor fault status | Dehumidifier_2_3 | {0:正常;1:故障} <0:绿色;1:红色> | {0:Normal;1:Fault} | [0~1]
|  |  |  | bit3:湿度传感器故障状态 | bit3:Humidity sensor fault status | Dehumidifier_2_4 | {0:正常;1:故障} <0:绿色;1:红色> | {0:Normal;1:Fault} | [0~1]
|  |  |  | bit4:环境温度传感器故障状态 | bit4:Ambient temperature sensor fault status | Dehumidifier_2_5 | {0:正常;1:故障} <0:绿色;1:红色> | {0:Normal;1:Fault} | [0~1]
|  |  |  | bit5:预留 | bit5:Reserved | Dehumidifier_2_6
|  |  |  | bit6:预留 | bit6:Reserved | Dehumidifier_2_7
|  |  |  | bit7:预留 | bit7:Reserved | Dehumidifier_2_8
0x01D3 | 露点温度 | Dew Point Temperature | Dehumidifier_3 | [6 empty] | 0.01 | ℃ | R | S16 |  |  |  | 0x065A | 1626 | 0x065A
0x01D4 | 当前湿度 | Current Humidity | Dehumidifier_4 | [6 empty] | 0.1 | % | R | U16 |  |  |  | 0x065B | 1627 | 0x065B
0x01D5 | 当前温度1-原始 | Current Temperature 1 - Raw | Dehumidifier_5 | [7 empty] | ℃ | R | S16 |  |  |  | 0x065C | 1628 | 0x065C
0x01D6 | 当前温度2-原始 | Current Temperature 2 - Raw | Dehumidifier_6 | [7 empty] | ℃ | R | S16 |  |  |  | 0x065D | 1629 | 0x065D
0x01E1 | 运行状态 | Operating Status | Dehumidifier2_1 | bit0:压缩机运行状态 | bit0:Compressor running status | Dehumidifier2_1_1 | {0:停止;1:运行} | {0:Stop;1:Run} | [0~1] | 1 | Hex | R | U16 |  |  |  | 0x065E | 1630 | 0x065E
|  |  |  | bit1:风机运行状态 | bit1:Fan running status | Dehumidifier2_1_2 | {0:停止;1:运行} | {0:Stop;1:Run} | [0~1]
|  |  |  | bit2:化霜运行状态 | bit2:Defrosting running status | Dehumidifier2_1_3 | {0:停止;1:运行} | {0:Stop;1:Run} | [0~1]
|  |  |  | bit3:预留 | bit3:Reserved | Dehumidifier2_1_4
|  |  |  | bit4:预留 | bit4:Reserved | Dehumidifier2_1_5
|  |  |  | bit5:预留 | bit5:Reserved | Dehumidifier2_1_6
|  |  |  | bit6:预留 | bit6:Reserved | Dehumidifier2_1_7
|  |  |  | bit7:预留 | bit7:Reserved | Dehumidifier2_1_8
0x01E2 | 告警状态 | Alarm Status | Dehumidifier2_2 | bit0:低温保护 | bit0:Low temperature protection | Dehumidifier2_2_1 | {0:正常;1:故障} <0:绿色;1:红色> | {0:Normal;1:Fault} | [0~1] | 1 | Hex | R | U16 |  |  |  | 0x065F | 1631 | 0x065F
|  |  |  | bit1:高温保护 | bit1:High temperature protection | Dehumidifier2_2_2 | {0:正常;1:故障} <0:绿色;1:红色> | {0:Normal;1:Fault} | [0~1]
|  |  |  | bit2:盘管温度传感器故障状态 | bit2:Coil temperature sensor fault status | Dehumidifier2_2_3 | {0:正常;1:故障} <0:绿色;1:红色> | {0:Normal;1:Fault} | [0~1]
|  |  |  | bit3:湿度传感器故障状态 | bit3:Humidity sensor fault status | Dehumidifier2_2_4 | {0:正常;1:故障} <0:绿色;1:红色> | {0:Normal;1:Fault} | [0~1]
|  |  |  | bit4:环境温度传感器故障状态 | bit4:Ambient temperature sensor fault status | Dehumidifier2_2_5 | {0:正常;1:故障} <0:绿色;1:红色> | {0:Normal;1:Fault} | [0~1]
|  |  |  | bit5:预留 | bit5:Reserved | Dehumidifier2_2_6
|  |  |  | bit6:预留 | bit6:Reserved | Dehumidifier2_2_7
|  |  |  | bit7:预留 | bit7:Reserved | Dehumidifier2_2_8
0x01E3 | 露点温度 | Dew Point Temperature | Dehumidifier2_3 | [6 empty] | 0.01 | ℃ | R | S16 |  |  |  | 0x0660 | 1632 | 0x0660
0x01E4 | 当前湿度 | Current Humidity | Dehumidifier2_4 | [6 empty] | 0.1 | % | R | U16 |  |  |  | 0x0661 | 1633 | 0x0661
0x01E5 | 当前温度1-原始 | Current Temperature 1 - Raw | Dehumidifier2_5 | [7 empty] | ℃ | R | S16 |  |  |  | 0x0662 | 1634 | 0x0662
0x01E6 | 当前温度2-原始 | Current Temperature 2 - Raw | Dehumidifier2_6 | [7 empty] | ℃ | R | S16 |  |  |  | 0x0663 | 1635 | 0x0663
0x0801 | 水泵运行状态 | Pump Speed | LiquidCool_1_1 |  |  |  | {0:停止;1:运行} <0:红色;1:绿色> | {0:Stop;1:Run} | [0~1] | 1 | Hex | R | U16 |  |  |  | 0x0664 | 1636 | 0x0664
0x0802 | 压缩机运行状态#1 | Compressor Status #1 | LiquidCool_1_2 |  |  |  | {0:停止;1:运行} <0:红色;1:绿色> | {0:Stop;1:Run} | [0~1] | 1 | Hex | R | U16 |  |  |  | 0x0665 | 1637 | 0x0665
0x0803 | 压缩机运行状态#2 | Compressor Status #2 | LiquidCool_1_3 |  |  |  | {0:停止;1:运行} <0:红色;1:绿色> | {0:Stop;1:Run} | [0~1] | 1 | Hex | R | U16 |  |  |  | 0x0666 | 1638 | 0x0666
0x0804 | 电加热运行状态 | Electric Heater Status | LiquidCool_1_4 |  |  |  | {0:停止;1:运行} <0:红色;1:绿色> | {0:Stop;1:Run} | [0~1] | 1 | Hex | R | U16 |  |  |  | 0x0667 | 1639 | 0x0667
0x0805 | 冷凝风机运行状态 | Condenser Fan Status | LiquidCool_1_5 |  |  |  | {0:停止;1:运行} <0:红色;1:绿色> | {0:Stop;1:Run} | [0~1] | 1 | Hex | R | U16 |  |  |  | 0x0668 | 1640 | 0x0668
0x0806 | 出水温度 | Outlet Water Temp | LiquidCool_1_6 | [6 empty] | 0.1 | ℃ | R | S16 |  |  |  | 0x0669 | 1641 | 0x0669
0x0807 | 回水温度 | Return Water Temp | LiquidCool_1_7 | [6 empty] | 0.1 | ℃ | R | S16 |  |  |  | 0x066A | 1642 | 0x066A
0x0808 | 出水压力 | Outlet Water Pressure | LiquidCool_1_8 | [6 empty] | 0.01 | Bar | R | U16 |  |  |  | 0x066B | 1643 | 0x066B
0x0809 | 回水压力 | Return Water Pressure | LiquidCool_1_9 | [6 empty] | 0.01 | Bar | R | U16 |  |  |  | 0x066C | 1644 | 0x066C
0x080A | 机组外环境温度 | Unit Ambient Temp | LiquidCool_1_10 | [6 empty] | 0.1 | ℃ | R | S16 |  |  |  | 0x066D | 1645 | 0x066D
0x080B | 补液状态 | Fluid Replenishment Status | LiquidCool_1_11 |  |  |  | {0:补液停止;1:补液运行} <0:绿色;1:绿色> | {0:Stop;1:Run} | [0~1] | 1 | Hex | R | U16 |  |  |  | 0x066E | 1646 | 0x066E
0x080C | 机组开关机状态 | Unit On/Off Status | LiquidCool_1_12 |  |  |  | {0:机组关机;1:机组开机} <0:红色;1:绿色> | {0:CLose;1:Open} | [0~1] | 1 | Hex | R | U16 |  |  |  | 0x066F | 1647 | 0x066F
0x080D | 本地远程状态 | Local/Remote Status | LiquidCool_1_13 |  |  |  | {0:本地;1:远程} <0:绿色;1:绿色> | {0:Local;1:Remote} | [0~1] | 1 | Hex | R | U16 |  |  |  | 0x0670 | 1648 | 0x0670
0x080E | 告警状态1 | LiquidCool Alarm1 | LiquidCool_1_alarm1 | Bit0:系统缺水告警 | Bit0:System Water Lack Alarm | LiquidCool_1_14_1 | {0:正常;1:告警} <0:绿色;1:红色> | {0:Normal;1:Alarm} | [0~1] | 1 | Hex | R | U16 |  |  |  | 0x0671 | 1649 | 0x0671
|  |  |  | Bit1:冷凝压力过高告警1 | Bit1:1Condensing Pressure High Alarm 1 | LiquidCool_1_14_2 | {0:正常;1:告警} <0:绿色;1:红色> | {0:Normal;1:Alarm} | [0~1] | 1
|  |  |  | Bit2:冷凝压力过高告警2 | Bit2:Condensing Pressure High Alarm 2 | LiquidCool_1_14_3 | {0:正常;1:告警} <0:绿色;1:红色> | {0:Normal;1:Alarm} | [0~1] | 1
|  |  |  | Bit3:出水压力过高告警 | Bit3:Outlet Water Pressure High Alarm | LiquidCool_1_14_4 | {0:正常;1:告警} <0:绿色;1:红色> | {0:Normal;1:Alarm} | [0~1] | 1
|  |  |  | Bit4:回水压力过低告警 | Bit4:Return Water Pressure Low Alarm | LiquidCool_1_14_5 | {0:正常;1:告警} <0:绿色;1:红色> | {0:Normal;1:Alarm} | [0~1] | 1
0x080F | 告警状态3 | LiquidCool Alarm3 | LiquidCool_1_alarm3 | Bit0:排气温感失效1 | Bit0:Discharge Temp Sensor Fault | LiquidCool_1_15_1 | {0:正常;1:告警} <0:绿色;1:红色> | {0:Normal;1:Alarm} | [0~1] | 1 | Hex | R | U16 |  |  |  | 0x0672 | 1650 | 0x0672
|  |  |  | Bit1:冷凝温感失效1 | Bit1:Condensing Temp Sensor Fault | LiquidCool_1_15_2 | {0:正常;1:告警} <0:绿色;1:红色> | {0:Normal;1:Alarm} | [0~1] | 1
|  |  |  | Bit2:排气温感失效2 | Bit2:Discharge Temp Sensor Fault | LiquidCool_1_15_3 | {0:正常;1:告警} <0:绿色;1:红色> | {0:Normal;1:Alarm} | [0~1] | 1
|  |  |  | Bit3:冷凝温感失效2 | Bit3:Condensing Temp Sensor Fault | LiquidCool_1_15_4 | {0:正常;1:告警} <0:绿色;1:红色> | {0:Normal;1:Alarm} | [0~1] | 1
|  |  |  | Bit4:回水温感故障 | Bit4:Return Water Temp Sensor Fault | LiquidCool_1_15_5 | {0:正常;1:告警} <0:绿色;1:红色> | {0:Normal;1:Alarm} | [0~1] | 1
|  |  |  | Bit5:出水温感故障 | Bit5:Outlet Water Temp Sensor Fault | LiquidCool_1_15_6 | {0:正常;1:告警} <0:绿色;1:红色> | {0:Normal;1:Alarm} | [0~1] | 1
|  |  |  | Bit6:环境温感失效 | Bit6:Ambient Temp Sensor Fault | LiquidCool_1_15_7 | {0:正常;1:告警} <0:绿色;1:红色> | {0:Normal;1:Alarm} | [0~1] | 1
|  |  |  | Bit7:异常掉电告警 | Bit7:Abnormal Power Loss Alarm | LiquidCool_1_15_8 | {0:正常;1:告警} <0:绿色;1:红色> | {0:Normal;1:Alarm} | [0~1] | 1
|  |  |  | Bit8:高压压力传感器失效1 | Bit8:High Pressure Sensor Fault | LiquidCool_1_15_9 | {0:正常;1:告警} <0:绿色;1:红色> | {0:Normal;1:Alarm} | [0~1] | 1
|  |  |  | Bit9:高压压力传感器失效2 | Bit9:High Pressure Sensor Fault | LiquidCool_1_15_10 | {0:正常;1:告警} <0:绿色;1:红色> | {0:Normal;1:Alarm} | [0~1] | 1
|  |  |  | Bit10:补水箱低水位 | Bit10:Make-up Tank Low Level | LiquidCool_1_15_11 | {0:正常;1:告警} <0:绿色;1:红色> | {0:Normal;1:Alarm} | [0~1] | 1
|  |  |  | Bit11:预留 | Bit11:Reserved | LiquidCool_1_15_12 | {0:正常;1:告警} <0:绿色;1:红色> | {0:Normal;1:Alarm} | [0~1] | 1
|  |  |  | Bit12:预留 | Bit12:Reserved | LiquidCool_1_15_13 | {0:正常;1:告警} <0:绿色;1:红色> | {0:Normal;1:Alarm} | [0~1] | 1
|  |  |  | Bit13:回水压力传感器故障 | Bit13:Return Water Pressure Sensor Fault | LiquidCool_1_15_14 | {0:正常;1:告警} <0:绿色;1:红色> | {0:Normal;1:Alarm} | [0~1] | 1
|  |  |  | Bit14:出水压力传感器故障 | Bit14:Outlet Water Pressure Sensor Fault | LiquidCool_1_15_15 | {0:正常;1:告警} <0:绿色;1:红色> | {0:Normal;1:Alarm} | [0~1] | 1
|  |  |  | Bit15:预留 | Bit15:Reserved | LiquidCool_1_15_16 | {0:正常;1:告警} <0:绿色;1:红色> | {0:Normal;1:Alarm} | [0~1] | 1
0x0810 | 告警状态5 | LiquidCool Alarm5 | LiquidCool_1_alarm5 | Bit0:高压力锁定1 | Bit0:High Pressure Lock 1 | LiquidCool_1_16_1 | {0:正常;1:告警} <0:绿色;1:红色> | {0:Normal;1:Alarm} | [0~1] | 1 | Hex | R | U16 |  |  |  | 0x0673 | 1651 | 0x0673
|  |  |  | Bit1:排气过温锁定1 | Bit1:Discharge Over Temp Lock 1 | LiquidCool_1_16_2 | {0:正常;1:告警} <0:绿色;1:红色> | {0:Normal;1:Alarm} | [0~1] | 1
|  |  |  | Bit2:系统低压力告警锁定1 | Bit2:System Low Pressure Alarm Lock 1 | LiquidCool_1_16_3 | {0:正常;1:告警} <0:绿色;1:红色> | {0:Normal;1:Alarm} | [0~1] | 1
|  |  |  | Bit3:低压压力传感器失效1 | Bit3:Low Pressure Sensor Fault 1 | LiquidCool_1_16_4 | {0:正常;1:告警} <0:绿色;1:红色> | {0:Normal;1:Alarm} | [0~1] | 1
|  |  |  | Bit4:蒸发出口温感失效1 | Bit4:Evaporation Outlet Temp Sensor Fault 1 | LiquidCool_1_16_5 | {0:正常;1:告警} <0:绿色;1:红色> | {0:Normal;1:Alarm} | [0~1] | 1
|  |  |  | Bit5:压缩机变频器故障1 | Bit5:Compressor Inverter Fault 1 | LiquidCool_1_16_6 | {0:正常;1:告警} <0:绿色;1:红色> | {0:Normal;1:Alarm} | [0~1] | 1
|  |  |  | Bit6:压机变频器通信故障1 | Bit6:Compressor Inverter Comm Fault 1 | LiquidCool_1_16_7 | {0:正常;1:告警} <0:绿色;1:红色> | {0:Normal;1:Alarm} | [0~1] | 1
|  |  |  | Bit7:外风机变频器故障1 | Bit7:External Fan Inverter Fault 1 | LiquidCool_1_16_8 | {0:正常;1:告警} <0:绿色;1:红色> | {0:Normal;1:Alarm} | [0~1] | 1
|  |  |  | Bit8:外风机变频器通信故障1 | Bit8:External Fan Inverter Comm Fault 1 | LiquidCool_1_16_9 | {0:正常;1:告警} <0:绿色;1:红色> | {0:Normal;1:Alarm} | [0~1] | 1
|  |  |  | Bit9:高压力锁定2 | Bit9:High Pressure Lock 2 | LiquidCool_1_16_10 | {0:正常;1:告警} <0:绿色;1:红色> | {0:Normal;1:Alarm} | [0~1] | 1
|  |  |  | Bit10:排气过温锁定2 | Bit10:Discharge Over Temp Lock 2 | LiquidCool_1_16_11 | {0:正常;1:告警} <0:绿色;1:红色> | {0:Normal;1:Alarm} | [0~1] | 1
|  |  |  | Bit11:系统低压力告警锁定2 | Bit11:System Low Pressure Alarm Lock 2 | LiquidCool_1_16_12 | {0:正常;1:告警} <0:绿色;1:红色> | {0:Normal;1:Alarm} | [0~1] | 1
|  |  |  | Bit12:低压压力传感器失效2 | Bit12:Low Pressure Sensor Fault 2 | LiquidCool_1_16_13 | {0:正常;1:告警} <0:绿色;1:红色> | {0:Normal;1:Alarm} | [0~1] | 1
|  |  |  | Bit13:蒸发出口温感失效2 | Bit13:Evaporation Outlet Temp Sensor Fault 2 | LiquidCool_1_16_14 | {0:正常;1:告警} <0:绿色;1:红色> | {0:Normal;1:Alarm} | [0~1] | 1
|  |  |  | Bit14:压缩机变频器故障2 | Bit14:Compressor Inverter Fault 2 | LiquidCool_1_16_15 | {0:正常;1:告警} <0:绿色;1:红色> | {0:Normal;1:Alarm} | [0~1] | 1
|  |  |  | Bit15:压机变频器通信故障2 | Bit15:Compressor Inverter Comm Fault 2 | LiquidCool_1_16_16 | {0:正常;1:告警} <0:绿色;1:红色> | {0:Normal;1:Alarm} | [0~1] | 1
0x0811 | 告警状态6 | LiquidCool Alarm6 | LiquidCool_1_alarm6 | Bit0:扩展模块通信故障 | Bit0:Expansion Module Comm Fault | LiquidCool_1_17_1 | {0:正常;1:告警} <0:绿色;1:红色> | {0:Normal;1:Alarm} | [0~1] | 1 | Hex | R | U16 |  |  |  | 0x0674 | 1652 | 0x0674
|  |  |  | Bit1:外风机变频器故障2 | Bit1:External Fan Inverter Fault 2 | LiquidCool_1_17_2 | {0:正常;1:告警} <0:绿色;1:红色> | {0:Normal;1:Alarm} | [0~1] | 1
|  |  |  | Bit2:外风机变频器通信故障2 | Bit2:External Fan Inverter Comm Fault 2 | LiquidCool_1_17_3 | {0:正常;1:告警} <0:绿色;1:红色> | {0:Normal;1:Alarm} | [0~1] | 1
|  |  |  | Bit3:水泵压差低 | Bit3:Pump Differential Pressure Low | LiquidCool_1_17_4 | {0:正常;1:告警} <0:绿色;1:红色> | {0:Normal;1:Alarm} | [0~1] | 1
|  |  |  | Bit4:回水温感故障and出水温感故障 | Bit4:Return & Outlet Water Temp Sensor Fault | LiquidCool_1_17_5 | {0:正常;1:告警} <0:绿色;1:红色> | {0:Normal;1:Alarm} | [0~1] | 1
|  |  |  | Bit5:电源故障 | Bit5:Power Supply Fault | LiquidCool_1_17_6 | {0:正常;1:告警} <0:绿色;1:红色> | {0:Normal;1:Alarm} | [0~1] | 1
|  |  |  | Bit6:回水压力传感器故障And出水压力传感器故障 | Bit6:Return & Outlet Water Pressure Sensor Fault | LiquidCool_1_17_7 | {0:正常;1:告警} <0:绿色;1:红色> | {0:Normal;1:Alarm} | [0~1] | 1
|  |  |  | Bit7:预留 | Bit7:Reserved | LiquidCool_1_17_8 | {0:正常;1:告警} <0:绿色;1:红色> | {0:Normal;1:Alarm} | [0~1] | 1
|  |  |  | Bit8:循环水泵变频器故障1 | Bit8:Circulation Pump Inverter Fault 1 | LiquidCool_1_17_9 | {0:正常;1:告警} <0:绿色;1:红色> | {0:Normal;1:Alarm} | [0~1] | 1
|  |  |  | Bit9:循环水泵变频器通信故障1 | Bit9:Circulation Pump Inverter Comm Fault 1 | LiquidCool_1_17_10 | {0:正常;1:告警} <0:绿色;1:红色> | {0:Normal;1:Alarm} | [0~1] | 1
|  |  |  | Bit10:电加热故障锁定1 | Bit10:Electric Heater Fault Lock 1 | LiquidCool_1_17_11 | {0:正常;1:告警} <0:绿色;1:红色> | {0:Normal;1:Alarm} | [0~1] | 1
|  |  |  | Bit11:出水高温 | Bit11:Outlet Water High Temp | LiquidCool_1_17_12 | {0:正常;1:告警} <0:绿色;1:红色> | {0:Normal;1:Alarm} | [0~1] | 1
|  |  |  | Bit12:回水低温 | Bit12:Return Water Low Temp | LiquidCool_1_17_13 | {0:正常;1:告警} <0:绿色;1:红色> | {0:Normal;1:Alarm} | [0~1] | 1
|  |  |  | Bit13:循环水泵过热保护告警锁定1 | Bit13:Circulation Pump Overheat Protection Lock 1 | LiquidCool_1_17_14 | {0:正常;1:告警} <0:绿色;1:红色> | {0:Normal;1:Alarm} | [0~1] | 1
|  |  |  | Bit14:循环水泵过热保护告警锁定2 | Bit14:Circulation Pump Overheat Protection Lock 2 | LiquidCool_1_17_15 | {0:正常;1:告警} <0:绿色;1:红色> | {0:Normal;1:Alarm} | [0~1] | 1
|  |  |  | Bit15:循环水泵过载保护锁定1 | Bit15:Circulation Pump Overload Protection Lock 1 | LiquidCool_1_17_16 | {0:正常;1:告警} <0:绿色;1:红色> | {0:Normal;1:Alarm} | [0~1] | 1
0x0812 | 告警状态7 | LiquidCool Alarm7 | LiquidCool_1_alarm7 | Bit0:循环水泵过载保护锁定2 | Bit0:Circulation Pump Overload Protection Lock 2 | LiquidCool_1_18_1 | {0:正常;1:告警} <0:绿色;1:红色> | {0:Normal;1:Alarm} | [0~1] | 1 | Hex | R | U16 |  |  |  | 0x0675 | 1653 | 0x0675
|  |  |  | Bit1:循环水泵变频器故障2 | Bit1:Circulation Pump Inverter Fault 2 | LiquidCool_1_18_2 | {0:正常;1:告警} <0:绿色;1:红色> | {0:Normal;1:Alarm} | [0~1] | 1
|  |  |  | Bit2:循环水泵变频器通信故障2 | Bit2:Circulation Pump Inverter Comm Fault 2 | LiquidCool_1_18_3 | {0:正常;1:告警} <0:绿色;1:红色> | {0:Normal;1:Alarm} | [0~1] | 1
|  |  |  | Bit3:2#电加热故障锁定 | Bit3:Electric Heater Fault Lock | LiquidCool_1_18_4 | {0:正常;1:告警} <0:绿色;1:红色> | {0:Normal;1:Alarm} | [0~1] | 1
|  |  |  | Bit4:预留 | Bit4:Reserved | LiquidCool_1_18_5 | {0:正常;1:告警} <0:绿色;1:红色> | {0:Normal;1:Alarm} | [0~1] | 1
|  |  |  | Bit5:DC_DC1模块故障 | Bit5:DC_DC1 Module Fault | LiquidCool_1_18_6 | {0:正常;1:告警} <0:绿色;1:红色> | {0:Normal;1:Alarm} | [0~1] | 1
|  |  |  | Bit6:DC_DC2模块故障 | Bit6:DC_DC2 Module Fault | LiquidCool_1_18_7 | {0:正常;1:告警} <0:绿色;1:红色> | {0:Normal;1:Alarm} | [0~1] | 1
|  |  |  | Bit7:冷凝过温锁定1 | Bit7:Condensing Over Temp Lock 1 | LiquidCool_1_18_8 | {0:正常;1:告警} <0:绿色;1:红色> | {0:Normal;1:Alarm} | [0~1] | 1
|  |  |  | Bit8:冷凝过温锁定2 | Bit8:Condensing Over Temp Lock 2 | LiquidCool_1_18_9 | {0:正常;1:告警} <0:绿色;1:红色> | {0:Normal;1:Alarm} | [0~1] | 1
|  |  |  | Bit9:冷凝高压锁定1 | Bit9:Condensing High Pressure Lock 1 | LiquidCool_1_18_10 | {0:正常;1:告警} <0:绿色;1:红色> | {0:Normal;1:Alarm} | [0~1] | 1
|  |  |  | Bit10:冷凝高压锁定2 | Bit10:Condensing High Pressure Lock 2 | LiquidCool_1_18_11 | {0:正常;1:告警} <0:绿色;1:红色> | {0:Normal;1:Alarm} | [0~1] | 1
|  |  |  | Bit11:板换侧出水高压锁定 | Bit11:Plate Exchanger Outlet High Pressure Lock | LiquidCool_1_18_12 | {0:正常;1:告警} <0:绿色;1:红色> | {0:Normal;1:Alarm} | [0~1] | 1
|  |  |  | Bit12:1#外风机过温告警锁定 | Bit12:No.1 External Fan Overheat Alarm Lock | LiquidCool_1_18_13 | {0:正常;1:告警} <0:绿色;1:红色> | {0:Normal;1:Alarm} | [0~1] | 1
|  |  |  | Bit13:2#外风机过温告警锁定 | Bit13:No.2 External Fan Overheat Alarm Lock | LiquidCool_1_18_14 | {0:正常;1:告警} <0:绿色;1:红色> | {0:Normal;1:Alarm} | [0~1] | 1
|  |  |  | Bit14:3#外风机过温告警锁定 | Bit14:No.3 External Fan Overheat Alarm Lock | LiquidCool_1_18_15 | {0:正常;1:告警} <0:绿色;1:红色> | {0:Normal;1:Alarm} | [0~1] | 1
|  |  |  | Bit15:4#外风机过温告警锁定 | Bit15:No.4 External Fan Overheat Alarm Lock | LiquidCool_1_18_16 | {0:正常;1:告警} <0:绿色;1:红色> | {0:Normal;1:Alarm} | [0~1] | 1
0x0813 | 告警等级 | Alarm Level | LiquidCool_1_19 |  |  |  | {0:无;1:一级告警;2:二级告警;3:三级告警} | {0:NULL;1:Level1Alarm;2:Level2Alarm;3:Level3Alarm} |  | 1 |  | R | U16 |  |  |  | 0x0676 | 1654 | 0x0676
0x0814 | 液冷机组控制模式 | Liquid Cooling Control Mode | LiquidCool_1_20 |  |  |  | {0:自动模式;1:制冷模式;2:制热模式;3:自循环;4:停止模式} | {0:AutoMode;1:CoolingMode;2:HeatingMode;3:SelfCirculation;4:StopMode} | [0~4] | 1 |  | R/W | U16 |  |  |  | 0x0677 | 1655 | 0x0677
0x0815 | 机组开关机使能 | Unit On/Off Enable | LiquidCool_1_21 |  |  |  | {0:监控关机;1:监控开机} | {0:MonitorShutdown;1:MonitorStartup} | [0~1] | 1 |  | R/W | U16 |  |  |  | 0x0678 | 1656 | 0x0678
0x0816 | 水泵转速设定 | Pump Speed Setting | LiquidCool_1_22 | [6 empty] | 1 | % | R/W | U16 |  |  |  | 0x0679 | 1657 | 0x0679
0x0817 | 冷凝风机除雪使能 | Condenser Fan Defrost Enable | LiquidCool_1_23 |  |  |  | {0:关闭;1:开启} | {0:Off;1:On} | [0~1] | 1 |  | R/W | U16 |  |  |  | 0x067A | 1658 | 0x067A
0x0818 | 水温目标控制模式 | Water Temp Target Ctrl Mode | LiquidCool_1_24 |  |  |  | {0:出水温度;1:回水温度;2:监控温度;3:平均温度} | {0:OutWaterTempe;1:ReWaterTempe;2:MonTempe;3:AveTempe} | [0~3] | 1 |  | R/W | U16 |  |  |  | 0x067B | 1659 | 0x067B
0x0819 | 机组制冷点 | Unit Cooling Setpoint | LiquidCool_1_25 | [6 empty] | 0.1 | ℃ | R/W | S16 |  |  |  | 0x067C | 1660 | 0x067C
0x081A | 机组加热点 | Unit Heating Setpoint | LiquidCool_1_26 | [6 empty] | 0.1 | ℃ | R/W | S16 |  |  |  | 0x067D | 1661 | 0x067D
0x081B | 出水压力过高告警设定点 | High Outlet Pressure Alarm Setpt | LiquidCool_1_27 | [6 empty] | 0.01 | Bar | R/W | U16 |  |  |  | 0x067E | 1662 | 0x067E
0x081C | 回水压力过低告警设定点 | Low Return Pressure Alarm Setpt | LiquidCool_1_28 | [6 empty] | 0.01 | Bar | R/W | U16 |  |  |  | 0x067F | 1663 | 0x067F
0x081D | 制冷灵敏度 | Cooling Sensitivity | LiquidCool_1_29 | [6 empty] | 0.1 | ℃ | R/W | S16 |  |  |  | 0x0680 | 1664 | 0x0680
0x081E | 制热灵敏度 | Heating Sensitivity | LiquidCool_1_30 | [6 empty] | 0.1 | ℃ | R/W | S16 |  |  |  | 0x0681 | 1665 | 0x0681
0x081F | 出水高温设定点 | High Outlet Temp Setpoint | LiquidCool_1_31 | [6 empty] | 0.1 | ℃ | R/W | S16 |  |  |  | 0x0682 | 1666 | 0x0682
0x0820 | 出水低温设定点 | Low Outlet Temp Setpoint | LiquidCool_1_32 | [6 empty] | 0.1 | ℃ | R/W | S16 |  |  |  | 0x0683 | 1667 | 0x0683
0x0821 | 制冷制热设定点处理动作 | Processing action for cooling and heating setpoints | LiquidCool_1_33 |  |  |  | {0:保持;1:恢复} | {0:Hold;1:Restore} |  | 1 |  | R/W | U16 |  |  |  | 0x0684 | 1668 | 0x0684
0x0822 | 预留 | Reserved | LiquidCool_1_34 | [6 empty] | 0.1 |  | R/W | S16 |  |  |  | 0x0685 | 1669 | 0x0685
0x0823 | 预留 | Reserved | LiquidCool_1_35 | [6 empty] | 0.1 |  | R/W | S16 |  |  |  | 0x0686 | 1670 | 0x0686
0x0824 | 预留 | Reserved | LiquidCool_1_36 | [6 empty] | 0.1 |  | R/W | S16 |  |  |  | 0x0687 | 1671 | 0x0687
0x0401 | 整机状态 | Unit Status | AirCond_1_1 |  |  |  | {0:停止;1:运行} | {0:Stop;1:Run} | [0~1] | 1 |  | R | U16 |  |  |  | 0x0688 | 1672 | 0x0688
0x0402 | 内风机状态 | Indoor Fan Status | AirCond_1_2 |  |  |  | {0:停止;1:运行} | {0:Stop;1:Run} | [0~1] | 1 |  | R | U16 |  |  |  | 0x0689 | 1673 | 0x0689
0x0403 | 外风机状态 | Outdoor Fan Status | AirCond_1_3 |  |  |  | {0:停止;1:运行} | {0:Stop;1:Run} | [0~1] | 1 |  | R | U16 |  |  |  | 0x068A | 1674 | 0x068A
0x0404 | 压缩机状态 | Compressor Status | AirCond_1_4 |  |  |  | {0:停止;1:运行} | {0:Stop;1:Run} | [0~1] | 1 |  | R | U16 |  |  |  | 0x068B | 1675 | 0x068B
0x0405 | 电加热运行状态 | Electric Heater Status | AirCond_1_5 |  |  |  | {0:停止;1:运行} | {0:Stop;1:Run} | [0~1] | 1 |  | R | U16 |  |  |  | 0x068C | 1676 | 0x068C
0x0407 | 盘管温度 | Coil Temp | AirCond_1_7 | [6 empty] | 0.1 | ℃ | R | S16 |  |  |  | 0x068D | 1677 | 0x068D
0x0409 | 冷凝温度 | Condensing Temp | AirCond_1_9 | [6 empty] | 0.1 | ℃ | R | S16 |  |  |  | 0x068E | 1678 | 0x068E
0x040A | 室内温度 | Indoor Temp | AirCond_1_10 | [6 empty] | 0.1 | ℃ | R | S16 |  |  |  | 0x068F | 1679 | 0x068F
0x040B | 湿度 | Humidity | AirCond_1_11 | [6 empty] | 1 | % | R | U16 |  |  |  | 0x0690 | 1680 | 0x0690
0x040E | 交流电压 | Voltage | AirCond_1_14 | [6 empty] | 1 | V | R | U16 |  |  |  | 0x0691 | 1681 | 0x0691
0x0410 | 高温告警 | High Temp Alarm | AirCond_1_16 |  |  |  | {0:正常;1:报警} <0:绿色;1:红色> | {00:Normal;01:Alarm} | [0~1] | 1 |  | R | U16 |  |  |  | 0x0692 | 1682 | 0x0692
0x0412 | 高湿告警 | High Humidity Alarm | AirCond_1_18 |  |  |  | {0:正常;1:报警} <0:绿色;1:红色> | {00:Normal;01:Alarm} | [0~1] | 1 |  | R | U16 |  |  |  | 0x0693 | 1683 | 0x0693
0x0414 | 盘管防冻 | Coil Anti-Freeze | AirCond_1_20 |  |  |  | {0:正常;1:报警} <0:绿色;1:红色> | {00:Normal;01:Alarm} | [0~1] | 1 |  | R | U16 |  |  |  | 0x0694 | 1684 | 0x0694
0x0416 | 盘管温感失效 | Coil Sensor Fault | AirCond_1_22 |  |  |  | {0:正常;1:报警} <0:绿色;1:红色> | {00:Normal;01:Alarm} | [0~1] | 1 |  | R | U16 |  |  |  | 0x0695 | 1685 | 0x0695
0x0418 | 冷凝温感失效 | Condensing Sensor Fault | AirCond_1_24 |  |  |  | {0:正常;1:报警} <0:绿色;1:红色> | {00:Normal;01:Alarm} | [0~1] | 1 |  | R | U16 |  |  |  | 0x0696 | 1686 | 0x0696
0x0419 | 内温感失效 | Indoor Sensor Fault | AirCond_1_25 |  |  |  | {0:正常;1:报警} <0:绿色;1:红色> | {00:Normal;01:Alarm} | [0~1] | 1 |  | R | U16 |  |  |  | 0x0697 | 1687 | 0x0697
0x041B | 湿感失效 | Humidity Sensor Fault | AirCond_1_27 |  |  |  | {0:正常;1:报警} <0:绿色;1:红色> | {00:Normal;01:Alarm} | [0~1] | 1 |  | R | U16 |  |  |  | 0x0698 | 1688 | 0x0698
0x0421 | 高压告警 | High Pressure Alarm | AirCond_1_33 |  |  |  | {0:正常;1:报警} <0:绿色;1:红色> | {00:Normal;01:Alarm} | [0~1] | 1 |  | R | U16 |  |  |  | 0x0699 | 1689 | 0x0699
0x0426 | 高压锁定 | High Pressure Lockout | AirCond_1_38 |  |  |  | {0:正常;1:报警} <0:绿色;1:红色> | {00:Normal;01:Alarm} | [0~1] | 1 |  | R | U16 |  |  |  | 0x069A | 1690 | 0x069A
0x0429 | 交流过压 | Over Voltage | AirCond_1_41 |  |  |  | {0:正常;1:报警} <0:绿色;1:红色> | {00:Normal;01:Alarm} | [0~1] | 1 |  | R | U16 |  |  |  | 0x069B | 1691 | 0x069B
0x042A | 交流欠压 | Under Voltage | AirCond_1_42 |  |  |  | {0:正常;1:报警} <0:绿色;1:红色> | {00:Normal;01:Alarm} | [0~1] | 1 |  | R | U16 |  |  |  | 0x069C | 1692 | 0x069C
0x0431 | 制冷点 | Cooling Setpoint | AirCond_1_49 | [6 empty] | 1 | ℃ | R/W | S16 |  |  |  | 0x069D | 1693 | 0x069D
0x0432 | 制冷回差 | Cooling Differential | AirCond_1_50 | [6 empty] | 1 | ℃ | R/W | S16 |  |  |  | 0x069E | 1694 | 0x069E
0x0433 | 加热点 | Heating Setpoint | AirCond_1_51 | [6 empty] | 1 | ℃ | R/W | S16 |  |  |  | 0x069F | 1695 | 0x069F
0x0434 | 加热回差 | Heating Differential | AirCond_1_52 | [6 empty] | 1 | ℃ | R/W | S16 |  |  |  | 0x06A0 | 1696 | 0x06A0
0x0435 | 除湿点 | Dehumidify Setpoint | AirCond_1_53 | [6 empty] | 1 | % | R/W | U16 |  |  |  | 0x06A1 | 1697 | 0x06A1
0x0436 | 除湿回差 | Dehumidify Hysteresis | AirCond_1_54 | [6 empty] | 1 | % | R/W | U16 |  |  |  | 0x06A2 | 1698 | 0x06A2
0x0437 | 高温点 | High Temp Setpoint | AirCond_1_55 | [6 empty] | 1 | ℃ | R/W | S16 |  |  |  | 0x06A3 | 1699 | 0x06A3
0x0438 | 低温点 | Low Temp Setpoint | AirCond_1_56 | [6 empty] | 1 | ℃ | R/W | S16 |  |  |  | 0x06A4 | 1700 | 0x06A4
0x0439 | 高湿点 | High Humidity Setpoint | AirCond_1_57 | [6 empty] | 1 | % | R/W | U16 |  |  |  | 0x06A5 | 1701 | 0x06A5
0x043A | 预留 | Reserved | AirCond_1_58 | [6 empty] | 1 | ℃ | R/W | U16 |  |  |  | 0x06A6 | 1702 | 0x06A6
0x043B | 当前运行模式 | Current Run Mode | AirCond_1_59 |  |  |  | {0:待机;1:送风;2:保留;3:除湿;4:制冷;5:制热} | {0:Standby;1:Fan;2:Reserved;3:Dehumidify;4:Cool;5:Heat} |  | 1 |  | R | U16 |  |  |  | 0x06A7 | 1703 | 0x06A7
0x043C | 监控开关机 | Remote On/Off | AirCond_1_60 |  |  |  | {0:关机;1:开机} <0:灰色;1:蓝色> | {0:Shutdown;1:Boot} |  | 1 |  | R/W | U16 |  |  |  | 0x06A8 | 1704 | 0x06A8
0x043D | 预留 | Reserved | AirCond_1_61 | [6 empty] | 0.1 | ℃ | R/W | S16 |  |  |  | 0x06A9 | 1705 | 0x06A9
0x043E | 预留 | Reserved | AirCond_1_62 | [6 empty] | 0.1 | ℃ | R/W | S16 |  |  |  | 0x06AA | 1706 | 0x06AA
0x043F | 预留 | Reserved | AirCond_1_63 | [6 empty] | 1 | % | R/W | U16 |  |  |  | 0x06AB | 1707 | 0x06AB
0x0440 | 启动制冷指令 | Start Cool Cmd | AirCond_1_64 |  |  |  | {0:关闭;1:开启} | {0:Close;1:Open} |  | 1 |  | R/W | U16 |  |  |  | 0x06AC | 1708 | 0x06AC
0x0441 | 启动送风指令 | Start Fan Cmd | AirCond_1_65 |  |  |  | {0:关闭;1:开启} | {0:Close;1:Open} |  | 1 |  | R/W | U16 |  |  |  | 0x06AD | 1709 | 0x06AD
0x0442 | 启动待机指令 | Start Standby Cmd | AirCond_1_66 |  |  |  | {0:关闭;1:开启} | {0:Close;1:Open} |  | 1 |  | R/W | U16 |  |  |  | 0x06AE | 1710 | 0x06AE
0x0443 | 启动加热指令 | Start Heat Cmd | AirCond_1_67 |  |  |  | {0:关闭;1:开启} | {0:Close;1:Open} |  | 1 |  | R/W | U16 |  |  |  | 0x06AF | 1711 | 0x06AF

## Env(control) (hidden)
Rack Signal -- EMS Write TO BMS(BAU)
配置项中文名 | 配置项英文名 | 中文使用说明 | 说明 | 英文使用说明 | 使用注意事项 | 数据源 | 数量 | 步长 | Modbus地址 | 单位系数 | 单位 | 是否可写 | 数值格式 | 使用数量 | 内部地址
仓1动环遥控/遥调 | reserve_env_compartment_yk_dz_1 |  |  |  |  | BAU | 512 |  | 0x2001-0x2200 |  |  | R/W | u16 |  | 0xFFFF
仓2动环遥控/遥调 | reserve_env_compartment_yk_dz_2 |  |  |  |  | BAU | 512 |  | 0x2201-0x2400 |  |  | R/W | u16 |  | 0xFFFF
仓3动环遥控/遥调 | reserve_env_compartment_yk_dz_3 |  |  |  |  | BAU | 512 |  | 0x2401-0x2600 |  |  | R/W | u16 |  | 0xFFFF
仓4动环遥控/遥调 | reserve_env_compartment_yk_dz_4 |  |  |  |  | BAU | 512 |  | 0x2601-0x2800 |  |  | R/W | u16 |  | 0xFFFF
仓5动环遥控/遥调 | reserve_env_compartment_yk_dz_5 |  |  |  |  | BAU | 512 |  | 0x2801-0x2A00 |  |  | R/W | u16 |  | 0xFFFF
仓6动环遥控/遥调 | reserve_env_compartment_yk_dz_6 |  |  |  |  | BAU | 512 |  | 0x2A01-0x2C00 |  |  | R/W | u16 |  | 0xFFFF
仓7动环遥控/遥调 | reserve_env_compartment_yk_dz_7 |  |  |  |  | BAU | 512 |  | 0x2C01-0x2E00 |  |  | R/W | u16 |  | 0xFFFF

## Env(default) (hidden)
寄存器地址分配定义 | [15 empty] | 说明
配置项中文名 | 配置项英文名 | 中文使用说明 | 说明 | 英文使用说明 | 使用注意事项 | 数据源 | 数量 | 步长 | Modbus地址 | 单位系数 | 单位 | 是否可写 | 数值格式 | 使用数量 | 内部地址
空调 | reserve_AirCond | 空调n基地址：0x4001+0x100*n（0=<n<21） |  |  |  | BAU | 0x2000 |  | 0x4001-0x6000 |  |  | R/W | u16 |  | 0xFFFF
电表 | reserve2 | 电表n基地址：0x6001+0x400*n（0=<n<5） |  |  |  | BAU | 0x1400 |  | 0x6001-0x7400 |  |  | R/W | u16 |  | 0xFFFF
直连IO模块 | reserve_DirIO | 直连IO模块n基地址：0x7401+0x80*n（0=<n<8） |  |  |  | BAU | 0x400 |  | 0x7401-0x7800 |  |  | R/W | u16 |  | 0xFFFF
拓展IO模块 | reserve_ExtIO | 拓展IO模块n基地址：0x7801+0x80*n（0=<n<8） |  |  |  | BAU | 0x400 |  | 0x7801-0x7C00 |  |  | R/W | u16 |  | 0xFFFF
水浸 | reserve5 | 水浸n基地址：0x7C01+0x40*n（0=<n<16） |  |  |  | BAU | 0x400 |  | 0x7C01-0x8000 |  |  | R/W | u16 |  | 0xFFFF
温湿度 | reserve_HumTemp | 温湿度n基地址：0x8001+0x40*n（0=<n<16） |  |  |  | BAU | 0x400 |  | 0x8001-0x8400 |  |  | R/W | u16 |  | 0xFFFF
消防 | reserve_FireFight | 消防n基地址：0x8401+0x40*n（0=<n<16） |  |  |  | BAU | 0x1000 |  | 0x8401-0x9400 |  |  | R/W | u16 |  | 0xFFFF
液冷机 | reserve_LiquidCool | 液冷机n基地址：0x9401+0x40*n（0=<n<16） |  |  |  | BAU | 0x1000 |  | 0x9401-0xA400 |  |  | R/W | u16 |  | 0xFFFF
PCS | reserve_PCS | PCSn基地址：0xA401+0x40*n（0=<n<16） |  |  |  | BAU | 0x1000 |  | 0xA401-0xB400 |  |  | R/W | u16 |  | 0xFFFF
EMS | reserve_EMS | EMS基地址：0xB401 |  |  |  | BAU | 0x200 |  | 0xB401-0xB600 |  |  | R/W | u16 |  | 0xFFFF
充电机 | reserve11 |  |  |  |  | BAU | （0x400*？） | [7 empty] | 0xFFFF
电网侧电表 | reserve_GridMeter | 电网侧电表n基地址：0xB601+0x400*n（0=<n<3） |  |  |  | BAU | 0xC00 |  | 0xB601-0xC200 |  |  | R/W | u16 |  | 0xFFFF
储能电表 | reserve_EssMeter | 储能电表n基地址：0xC201+0x400*n（0=<n<3） |  |  |  | BAU | 0xC00 |  | 0xC201-0xCE00 |  |  | R/W | u16 |  | 0xFFFF
负载侧电表 | reserve_LoadMeter | 负载侧电表n基地址：0xCE01+0x400*n（0=<n<3） |  |  |  | BAU | 0xC00 |  | 0xCE01-0xDA00 |  |  | R/W | u16 |  | 0xFFFF

## Rack Signal
Rack Signal -- EMS Read From BMS(BCU)
偏移地址 | 配置项中文名 | 配置项英文名 | 英文key | 中文使用说明 | 英文使用说明 | 英文子key | 说明(值/枚举说明) | 说明(值/枚举说明)(英文) | 范围 | 单位系数 | 单位 | 是否可写 | 数值格式 | 个数 | 备注 | 数据源 | Modbus地址
0x0118 | 功能安全告警详细故障 | Function Safety Alarm Inf | functional_safety_warn | bit0:簇总压校验差过大 | bit0:Total Vol Diff | total_vol_diff | {0:正常;1:报警} | {0:Normal;1:Alarm} | [0~1] |  | Hex | R | U16 |  |  | BCU | 0x0010
| 功能安全告警详细故障 | Function Safety Alarm Inf |  | bit1:绝缘过低 | bit1:Ins Low | ins_low | {0:正常;1:报警} | {0:Normal;1:Alarm} | [0~1] |  |  | R
| 功能安全告警详细故障 | Function Safety Alarm Inf |  | bit2:单体电压过高 | bit2:Bat Vol High | bat_vol_high | {0:正常;1:报警} | {0:Normal;1:Alarm} | [0~1] |  |  | R
| 功能安全告警详细故障 | Function Safety Alarm Inf |  | bit3:电池温度过高 | bit3:Bat Temp High | bat_temp_high | {0:正常;1:报警} | {0:Normal;1:Alarm} | [0~1] |  |  | R
| 功能安全告警详细故障 | Function Safety Alarm Inf |  | bit4:单体电压更新异常 | bit4:Bat Vol Update | bat_vol_update | {0:正常;1:报警} | {0:Normal;1:Alarm} | [0~1] |  |  | R
| 功能安全告警详细故障 | Function Safety Alarm Inf |  | bit5:极柱温度过高 | bit5:Polarity Temp High | polarity_temp_high | {0:正常;1:报警} | {0:Normal;1:Alarm} | [0~1] |  |  | R
| 功能安全告警详细故障 | Function Safety Alarm Inf |  | bit6:放电电流过大 | bit6:Cur High | cur_high | {0:正常;1:报警} | {0:Normal;1:Alarm} | [0~1] |  |  | R
| 功能安全告警详细故障 | Function Safety Alarm Inf |  | bit7:绝缘监测故障 | bit7:Ins Err | ins_err | {0:正常;1:故障} | {0:Normal;1:Fault} | [0~1] |  |  | R
| 功能安全告警详细故障 | Function Safety Alarm Inf |  | bit8:Pack箱NTC故障 | bit8:NTC Fault | NTC_fault | {0:正常;1:故障} | {0:Normal;1:Fault} | [0~1] |  |  | R
| 功能安全告警详细故障 | Function Safety Alarm Inf |  | bit9:极柱温度传感器故障 | bit9:Polarity Temp Sensor | polarity_temp_sensor | {0:正常;1:报警} | {0:Normal;1:Alarm} | [0~1] |  |  | R
| 功能安全告警详细故障 | Function Safety Alarm Inf |  | bit10:电池温度传感器故障 | bit10:Bat Temp Sensor | bat_temp_sensor | {0:正常;1:报警} | {0:Normal;1:Alarm} | [0~1] |  |  | R
| 功能安全告警详细故障 | Function Safety Alarm Inf |  | bit11:电压采样故障 | bit11:Vol Sample Fault | vol_sample_fault | {0:正常;1:故障} | {0:Normal;1:Fault} | [0~1] |  |  | R
| 功能安全告警详细故障 | Function Safety Alarm Inf |  | bit12:采样芯片故障 | bit12:Sample Chip Fault | sample_chip_fault | {0:正常;1:故障} | {0:Normal;1:Fault} | [0~1] |  |  | R
| 功能安全告警详细故障 | Function Safety Alarm Inf |  | bit13:电流采样故障 | bit13:Cur Sample Fault | cur_sample_fault | {0:正常;1:故障} | {0:Normal;1:Fault} | [0~1] |  |  | R
| 功能安全告警详细故障 | Function Safety Alarm Inf |  | bit14:单体电压过低 | bit14:Bat Vol Low | bat_vol_low | {0:正常;1:报警} | {0:Normal;1:Alarm} | [0~1] |  |  | R
| 功能安全告警详细故障 | Function Safety Alarm Inf |  | bit15:充电电流过大 | bit15:Vhg Cur High | vhg_cur_high | {0:正常;1:报警} | {0:Normal;1:Alarm} | [0~1] |  |  | R
0x0136 | 主控对外故障报警 | BCU External Fault Alarm | BCU_external_fault_alarm | bit0:从控自检故障 | bit0:BMU Self-Check Fault | BMU_self_check_fault | {0:正常;1:故障} | {0:Normal;1:Fault} | [0~1] |  | Hex | R | U16 |  |  | BCU | 0x0011
| 主控对外故障报警 | BCU External Fault Alarm |  | bit1:主控自检故障 | bit1:BCU Self-Check Fault | BCU_self_check_fault | {0:正常;1:故障} | {0:Normal;1:Fault} | [0~1]
| 主控对外故障报警 | BCU External Fault Alarm |  | bit2:熔断器故障 | bit2:Fuse Fault | Fuse_fault | {0:正常;1:故障} | {0:Normal;1:Fault} | [0~1]
| 主控对外故障报警 | BCU External Fault Alarm |  | bit3:接触器故障 | bit3:Contactor Fault | Contactor_fault | {0:正常;1:故障} | {0:Normal;1:Fault} | [0~1]
| 主控对外故障报警 | BCU External Fault Alarm |  | bit4:从控通信故障 | bit4:BMU Communication Fault | BMU_comm_fault | {0:正常;1:故障} | {0:Normal;1:Fault} | [0~1]
| 主控对外故障报警 | BCU External Fault Alarm |  | bit5:总控通信故障 | bit5:BAU Communication Fault | BAU_comm_fault | {0:正常;1:故障} | {0:Normal;1:Fault} | [0~1]
| 主控对外故障报警 | BCU External Fault Alarm |  | bit6:电流采样故障 | bit6:Current Sampling Fault | Current_sampling_fault | {0:正常;1:故障} | {0:Normal;1:Fault} | [0~1]
| 主控对外故障报警 | BCU External Fault Alarm |  | bit7:绝缘检测故障 | bit7:Insulation Detection Fault | Insulation_detection_fault | {0:正常;1:故障} | {0:Normal;1:Fault} | [0~1]
| 主控对外故障报警 | BCU External Fault Alarm |  | bit8:隔离开关故障 | bit8:Disconnector Fault | Disconnector_fault | {0:正常;1:故障} | {0:Normal;1:Fault} | [0~1]
| 主控对外故障报警 | BCU External Fault Alarm |  | bit9:Pack箱NTC故障 | bit9:NTC Fault | NTC_fault | {0:正常;1:故障} | {0:Normal;1:Fault} | [0~1]
| 主控对外故障报警 | BCU External Fault Alarm |  | bit10:高压箱温度故障 | bit10:PDU Temperature Fault | PDU_temp_fault | {0:正常;1:故障} | {0:Normal;1:Fault} | [0~1]
| 主控对外故障报警 | BCU External Fault Alarm |  | bit11:高压回路故障 | bit11:High Voltage Circuit Fault | High_voltage_circuit_fault | {0:正常;1:故障} | {0:Normal;1:Fault} | [0~1]
| 主控对外故障报警 | BCU External Fault Alarm |  | bit12:功能安全故障 | bit12:Function Safety Fault | Function_safety_fault | {0:正常;1:故障} | {0:Normal;1:Fault} | [0~1]
| 主控对外故障报警 | BCU External Fault Alarm |  | bit13:PCS通信故障 | bit13:PCS Communication Fault | PCS_communication_fault | {0:正常;1:故障} | {0:Normal;1:Fault} | [0~1]
| 主控对外故障报警 | BCU External Fault Alarm |  | bit14:预留 | bit14:Reserved | Reserved1
| 主控对外故障报警 | BCU External Fault Alarm |  | bit15:预留 | bit15:Reserved | Reserved2
0x0139 | 对外一级报警信息（Critical） | External Critical | External_critical | bit0:簇总压过高 | bit0:Total Over Voltage | Total_OV | {0:正常;1:报警} | {0:Normal;1:Alarm} | [0~1] |  | Hex | R | U16 |  |  | BCU | 0x0012
| 对外一级报警信息（Critical） | External Critical |  | bit1:簇总压过低 | bit1:Total Under Voltage | Total_UV | {0:正常;1:报警} | {0:Normal;1:Alarm} | [0~1]
| 对外一级报警信息（Critical） | External Critical |  | bit2:单体电压过高 | bit2:Cell Over Voltage | Cell_OV | {0:正常;1:报警} | {0:Normal;1:Alarm} | [0~1]
| 对外一级报警信息（Critical） | External Critical |  | bit3:单体电压过低 | bit3:Cell Under Voltage | Cell_UV | {0:正常;1:报警} | {0:Normal;1:Alarm} | [0~1]
| 对外一级报警信息（Critical） | External Critical |  | bit4:放电电流过大 | bit4:Disharge Over Current | Dsg_OC | {0:正常;1:报警} | {0:Normal;1:Alarm} | [0~1]
| 对外一级报警信息（Critical） | External Critical |  | bit5:充电电流过大 | bit5:Charge Over Current | Chg_OC | {0:正常;1:报警} | {0:Normal;1:Alarm} | [0~1]
| 对外一级报警信息（Critical） | External Critical |  | bit6:放电温度过高 | bit6:Discharge Over Temperature | Dsg_OT | {0:正常;1:报警} | {0:Normal;1:Alarm} | [0~1]
| 对外一级报警信息（Critical） | External Critical |  | bit7:放电温度过低 | bit7:Discharge Under Temperature | Dsg_UT | {0:正常;1:报警} | {0:Normal;1:Alarm} | [0~1]
| 对外一级报警信息（Critical） | External Critical |  | bit8:充电温度过高 | bit8:Charge Over Temperature | Chg_OT | {0:正常;1:报警} | {0:Normal;1:Alarm} | [0~1]
| 对外一级报警信息（Critical） | External Critical |  | bit9:充电温度过低 | bit9:Charge Under Temperature | Chg_UT | {0:正常;1:报警} | {0:Normal;1:Alarm} | [0~1]
| 对外一级报警信息（Critical） | External Critical |  | bit10:绝缘阻值过低 | bit10:Low Insulation Resistance | Low_IR | {0:正常;1:报警} | {0:Normal;1:Alarm} | [0~1]
| 对外一级报警信息（Critical） | External Critical |  | bit11:极柱温度过高 | bit11:Terminal Over Temperature | Term_OT | {0:正常;1:报警} | {0:Normal;1:Alarm} | [0~1]
| 对外一级报警信息（Critical） | External Critical |  | bit12:高压箱温度过高 | bit12:PDU Over Temperature | PDU_OT | {0:正常;1:报警} | {0:Normal;1:Alarm} | [0~1]
| 对外一级报警信息（Critical） | External Critical |  | bit13:单体压差过大 | bit13:Cell Over Voltage Difference | Cell_OV_diff | {0:正常;1:报警} | {0:Normal;1:Alarm} | [0~1]
| 对外一级报警信息（Critical） | External Critical |  | bit14:单体温差过大 | bit14:Cell OverTemperature Difference | Cell_OT_diff | {0:正常;1:报警} | {0:Normal;1:Alarm} | [0~1]
| 对外一级报警信息（Critical） | External Critical |  | bit15:SOC过低 | bit15:Low SOC | Low_SOH | {0:正常;1:报警} | {0:Normal;1:Alarm} | [0~1]
0x013A | 对外二级报警信息（Alarm） | External Alarm | External_alarm | bit0:簇总压过高 | bit0:Total OverVoltage | Total_OV | {0:正常;1:报警} | {0:Normal;1:Alarm} | [0~1] |  | Hex | R | U16 |  |  | BCU | 0x0013
| 对外二级报警信息（Alarm） | External Alarm |  | bit1:簇总压过低 | bit1:Total UnderVoltage | Total_UV | {0:正常;1:报警} | {0:Normal;1:Alarm} | [0~1]
| 对外二级报警信息（Alarm） | External Alarm |  | bit2:单体电压过高 | bit2:Cell OverVoltage | Cell_OV | {0:正常;1:报警} | {0:Normal;1:Alarm} | [0~1]
| 对外二级报警信息（Alarm） | External Alarm |  | bit3:单体电压过低 | bit3:Cell UnderVoltage | Cell_UV | {0:正常;1:报警} | {0:Normal;1:Alarm} | [0~1]
| 对外二级报警信息（Alarm） | External Alarm |  | bit4:放电电流过大 | bit4:Disharge OverCurrent | Dsg_OC | {0:正常;1:报警} | {0:Normal;1:Alarm} | [0~1]
| 对外二级报警信息（Alarm） | External Alarm |  | bit5:充电电流过大 | bit5:Charge OverCurrent | Chg_OC | {0:正常;1:报警} | {0:Normal;1:Alarm} | [0~1]
| 对外二级报警信息（Alarm） | External Alarm |  | bit6:放电温度过高 | bit6:Discharge OverTemperature | Dsg_OT | {0:正常;1:报警} | {0:Normal;1:Alarm} | [0~1]
| 对外二级报警信息（Alarm） | External Alarm |  | bit7:放电温度过低 | bit7:Discharge UnderTemperature | Dsg_UT | {0:正常;1:报警} | {0:Normal;1:Alarm} | [0~1]
| 对外二级报警信息（Alarm） | External Alarm |  | bit8:充电温度过高 | bit8:Charge OverTemperature | Chg_OT | {0:正常;1:报警} | {0:Normal;1:Alarm} | [0~1]
| 对外二级报警信息（Alarm） | External Alarm |  | bit9:充电温度过低 | bit9:Charge UnderTemperature | Chg_UT | {0:正常;1:报警} | {0:Normal;1:Alarm} | [0~1]
| 对外二级报警信息（Alarm） | External Alarm |  | bit10:绝缘阻值过低 | bit10:Low Insulation Resistance | Low_IR | {0:正常;1:报警} | {0:Normal;1:Alarm} | [0~1]
| 对外二级报警信息（Alarm） | External Alarm |  | bit11:极柱温度过高 | bit11:Terminal OverTemperature | Term_OT | {0:正常;1:报警} | {0:Normal;1:Alarm} | [0~1]
| 对外二级报警信息（Alarm） | External Alarm |  | bit12:高压箱温度过高 | bit12:PDU OverTemperature | PDU_OT | {0:正常;1:报警} | {0:Normal;1:Alarm} | [0~1]
| 对外二级报警信息（Alarm） | External Alarm |  | bit13:单体压差过大 | bit13:Cell OverVoltage Difference | Cell_OV_diff | {0:正常;1:报警} | {0:Normal;1:Alarm} | [0~1]
| 对外二级报警信息（Alarm） | External Alarm |  | bit14:单体温差过大 | bit14:Cell OverTemperature Difference | Cell_OT_diff | {0:正常;1:报警} | {0:Normal;1:Alarm} | [0~1]
| 对外二级报警信息（Alarm） | External Alarm |  | bit15:SOC过低 | bit15:Low SOC | Low_SOH | {0:正常;1:报警} | {0:Normal;1:Alarm} | [0~1]
0x013B | 对外三级报警信息（Warning） | External Warn | External_warn | bit0:簇总压过高 | bit0:Total OverVoltage | Total_OV | {0:正常;1:报警} | {0:Normal;1:Alarm} | [0~1] |  | Hex | R | U16 |  |  | BCU | 0x0014
| 对外三级报警信息（Warning） | External Warn |  | bit1:簇总压过低 | bit1:Total UnderVoltage | Total_UV | {0:正常;1:报警} | {0:Normal;1:Alarm} | [0~1]
| 对外三级报警信息（Warning） | External Warn |  | bit2:单体电压过高 | bit2:Cell OverVoltage | Cell_OV | {0:正常;1:报警} | {0:Normal;1:Alarm} | [0~1]
| 对外三级报警信息（Warning） | External Warn |  | bit3:单体电压过低 | bit3:Cell UnderVoltage | Cell_UV | {0:正常;1:报警} | {0:Normal;1:Alarm} | [0~1]
| 对外三级报警信息（Warning） | External Warn |  | bit4:放电电流过大 | bit4:Disharge OverCurrent | Dsg_OC | {0:正常;1:报警} | {0:Normal;1:Alarm} | [0~1]
| 对外三级报警信息（Warning） | External Warn |  | bit5:充电电流过大 | bit5:Charge OverCurrent | Chg_OC | {0:正常;1:报警} | {0:Normal;1:Alarm} | [0~1]
| 对外三级报警信息（Warning） | External Warn |  | bit6:放电温度过高 | bit6:Discharge OverTemperature | Dsg_OT | {0:正常;1:报警} | {0:Normal;1:Alarm} | [0~1]
| 对外三级报警信息（Warning） | External Warn |  | bit7:放电温度过低 | bit7:Discharge UnderTemperature | Dsg_UT | {0:正常;1:报警} | {0:Normal;1:Alarm} | [0~1]
| 对外三级报警信息（Warning） | External Warn |  | bit8:充电温度过高 | bit8:Charge OverTemperature | Chg_OT | {0:正常;1:报警} | {0:Normal;1:Alarm} | [0~1]
| 对外三级报警信息（Warning） | External Warn |  | bit9:充电温度过低 | bit9:Charge UnderTemperature | Chg_UT | {0:正常;1:报警} | {0:Normal;1:Alarm} | [0~1]
| 对外三级报警信息（Warning） | External Warn |  | bit10:绝缘阻值过低 | bit10:Low Insulation Resistance | Low_IR | {0:正常;1:报警} | {0:Normal;1:Alarm} | [0~1]
| 对外三级报警信息（Warning） | External Warn |  | bit11:极柱温度过高 | bit11:Terminal OverTemperature | Term_OT | {0:正常;1:报警} | {0:Normal;1:Alarm} | [0~1]
| 对外三级报警信息（Warning） | External Warn |  | bit12:高压箱温度过高 | bit12:PDU OverTemperature | PDU_OT | {0:正常;1:报警} | {0:Normal;1:Alarm} | [0~1]
| 对外三级报警信息（Warning） | External Warn |  | bit13:单体压差过大 | bit13:Cell OverVoltage Difference | Cell_OV_diff | {0:正常;1:报警} | {0:Normal;1:Alarm} | [0~1]
| 对外三级报警信息（Warning） | External Warn |  | bit14:单体温差过大 | bit14:Cell OverTemperature Difference | Cell_OT_diff | {0:正常;1:报警} | {0:Normal;1:Alarm} | [0~1]
| 对外三级报警信息（Warning） | External Warn |  | bit15:SOC过低 | bit15:Low SOC | Low_SOH | {0:正常;1:报警} | {0:Normal;1:Alarm} | [0~1]
0x0BC6 | 对外一级报警信息2（Critical） | External Critical2 | External_stop_alarm2 | bit0:簇总压校验差过大 | bit0:Total Over Voltage Differencen | Total_OV_diff | {0:正常;1:报警} | {0:Normal;1:Alarm} | [0~1] |  | Hex | R | U16 |  |  | BCU | 0x0015
| 对外一级报警信息2（Critical） | External Critical2 |  | bit1:Pack电压过高 | bit1:Module Over Voltage | Module_OV | {0:正常;1:报警} | {0:Normal;1:Alarm} | [0~1]
| 对外一级报警信息2（Critical） | External Critical2 |  | bit2:Pack电压过低 | bit2:Module Under Voltage | Module_UV | {0:正常;1:报警} | {0:Normal;1:Alarm} | [0~1]
| 对外一级报警信息2（Critical） | External Critical2 |  | bit3:单体温升过高 | bit3:Cell Temperature Rise | Cell_temp_rise | {0:正常;1:报警} | {0:Normal;1:Alarm} | [0~1]
| 对外一级报警信息2（Critical） | External Critical2 |  | bit4:Pack压差过大 | bit4:Module Over Voltage Difference | Module_OV_diff | {0:正常;1:报警} | {0:Normal;1:Alarm} | [0~1]
| 对外一级报警信息2（Critical） | External Critical2 |  | bit5:动环停机汇总 | bit5:Run Stop Summary | Run_stop_summary | {0:正常;1:报警} | {0:Normal;1:Alarm} | [0~1]
| 对外一级报警信息2（Critical） | External Critical2 |  | bit6:铜排温度过高 | bit6:Busbar OT | Copper_OT | {0:正常;1:报警} | {0:Normal;1:Alarm} | [0~1]
| 对外一级报警信息2（Critical） | External Critical2 |  | bit7:充电单体压差过大 | bit7:Chg Cell Volt Diff | Chg_cell_volt_diff | {0:正常;1:报警} | {0:Normal;1:Alarm} | [0~1]
| 对外一级报警信息2（Critical） | External Critical2 |  | bit8:充电单体温差过大 | bit8:Chg Cell Temp Diff | Chg_cell_temp_diff | {0:正常;1:报警} | {0:Normal;1:Alarm} | [0~1]
| 对外一级报警信息2（Critical） | External Critical2 |  | bit9:充电Pack压差过大 | bit9:Chg Module Volt Diff | Chg_odule_volt_diff | {0:正常;1:报警} | {0:Normal;1:Alarm} | [0~1]
| 对外一级报警信息2（Critical） | External Critical2 |  | bit10:放电单体压差过大 | bit10:Dsg Cell Volt Diff | Dsg_cell_volt_diff | {0:正常;1:报警} | {0:Normal;1:Alarm} | [0~1]
| 对外一级报警信息2（Critical） | External Critical2 |  | bit11:放电单体温差过大 | bit11:Dsg Cell Temp Diff | Dsg_cell_temp_diff | {0:正常;1:报警} | {0:Normal;1:Alarm} | [0~1]
| 对外一级报警信息2（Critical） | External Critical2 |  | bit12:放电Pack压差过大 | bit12:Dsg Module Volt Diff | Dsg_module_volt_diff | {0:正常;1:报警} | {0:Normal;1:Alarm} | [0~1]
|  |  |  | bit13:预留 | bit13:Reserve1 | Reserved1
|  |  |  | bit14:Pack内温差过大 | bit14:Pack Temp Diff | Pack_temp_diff | {0:正常;1:报警} | {0:Normal;1:Alarm} | [0~1]
| 对外一级报警信息2（Critical） | External Critical2 |  | bit15:预留 | bit15:Reserve2 | Reserved2
0x0BC7 | 对外二级报警信息2（Alarm） | External Alarm2 | External_alarm2 | bit0:簇总压校验差过大 | bit0:Total OverVoltage Differencen | Total_OV_diff | {0:正常;1:报警} | {0:Normal;1:Alarm} | [0~1] |  | Hex | R | U16 |  |  | BCU | 0x0016
| 对外二级报警信息2（Alarm） | External Alarm2 |  | bit1:Pack电压过高 | bit1:Module Over Voltage | Module_OV | {0:正常;1:报警} | {0:Normal;1:Alarm} | [0~1]
| 对外二级报警信息2（Alarm） | External Alarm2 |  | bit2:Pack电压过低 | bit2:Module Under Voltage | Module_UV | {0:正常;1:报警} | {0:Normal;1:Alarm} | [0~1]
| 对外二级报警信息2（Alarm） | External Alarm2 |  | bit3:单体温升过高 | bit3:Cell Temperature Rise | Cell_temp_rise | {0:正常;1:报警} | {0:Normal;1:Alarm} | [0~1]
| 对外二级报警信息2（Alarm） | External Alarm2 |  | bit4:Pack压差过大 | bit4:Module OverVoltage Difference | Module_OV_diff | {0:正常;1:报警} | {0:Normal;1:Alarm} | [0~1]
| 对外二级报警信息2（Alarm） | External Alarm2 |  | bit5:动环报警汇总 | bit5:Run Alarm Summary | Run_alarm_summary | {0:正常;1:报警} | {0:Normal;1:Alarm} | [0~1]
| 对外二级报警信息2（Alarm） | External Alarm2 |  | bit6:铜排温度过高 | bit6:Busbar OT | Copper_OT | {0:正常;1:报警} | {0:Normal;1:Alarm} | [0~1]
| 对外二级报警信息2（Alarm） | External Alarm2 |  | bit7:充电单体压差过大 | bit7:Chg Cell Volt Diff | Chg_cell_volt_diff | {0:正常;1:报警} | {0:Normal;1:Alarm} | [0~1]
| 对外二级报警信息2（Alarm） | External Alarm2 |  | bit8:充电单体温差过大 | bit8:Chg Cell Temp Diff | Chg_cell_temp_diff | {0:正常;1:报警} | {0:Normal;1:Alarm} | [0~1]
| 对外二级报警信息2（Alarm） | External Alarm2 |  | bit9:充电Pack压差过大 | bit9:Chg Module Volt Diff | Chg_odule_volt_diff | {0:正常;1:报警} | {0:Normal;1:Alarm} | [0~1]
| 对外二级报警信息2（Alarm） | External Alarm2 |  | bit10:放电单体压差过大 | bit10:Dsg Cell Volt Diff | Dsg_cell_volt_diff | {0:正常;1:报警} | {0:Normal;1:Alarm} | [0~1]
| 对外二级报警信息2（Alarm） | External Alarm2 |  | bit11:放电单体温差过大 | bit11:Dsg Cell Temp Diff | Dsg_cell_temp_diff | {0:正常;1:报警} | {0:Normal;1:Alarm} | [0~1]
| 对外二级报警信息2（Alarm） | External Alarm2 |  | bit12:放电Pack压差过大 | bit12:Dsg Module Volt Diff | Dsg_module_volt_diff | {0:正常;1:报警} | {0:Normal;1:Alarm} | [0~1]
|  |  |  | bit13:预留 | bit13:Reserve1 | Reserved1
|  |  |  | bit14:Pack内温差过大 | bit14:Pack Temp Diff | Pack_temp_diff | {0:正常;1:报警} | {0:Normal;1:Alarm} | [0~1]
| 对外二级报警信息2（Alarm） | External Alarm2 |  | bit15:预留 | bit15:Reserve2 | Reserved2
0x0BC8 | 对外三级报警信息2（Warning） | External Warning2 | External_warn2 | bit0:簇总压校验差过大 | bit0:Total Over Voltage Differencen | Total_OV_diff | {0:正常;1:报警} | {0:Normal;1:Alarm} | [0~1] |  | Hex | R | U16 |  |  | BCU | 0x0017
| 对外三级报警信息2（Warning） | External Warning2 |  | bit1:Pack电压过高 | bit1:Module OverVoltage | Module_OV | {0:正常;1:报警} | {0:Normal;1:Alarm} | [0~1]
| 对外三级报警信息2（Warning） | External Warning2 |  | bit2:Pack电压过低 | bit2:Module UnderVoltage | Module_UV | {0:正常;1:报警} | {0:Normal;1:Alarm} | [0~1]
| 对外三级报警信息2（Warning） | External Warning2 |  | bit3:单体温升过高 | bit3:Cell Temperature Rise | Cell_temp_rise | {0:正常;1:报警} | {0:Normal;1:Alarm} | [0~1]
| 对外三级报警信息2（Warning） | External Warning2 |  | bit4:Pack压差过大 | bit4:Module Over Voltage Difference | Module_OV_diff | {0:正常;1:报警} | {0:Normal;1:Alarm} | [0~1]
| 对外三级报警信息2（Warning） | External Warning2 |  | bit5:动环预警汇总 | bit5:Run Warn Summary | Run_warn_summary | {0:正常;1:报警} | {0:Normal;1:Alarm} | [0~1]
| 对外三级报警信息2（Warning） | External Warning2 |  | bit6:铜排温度过高 | bit6:Busbar OT | Copper_OT | {0:正常;1:报警}
| 对外三级报警信息2（Warning） | External Warning2 |  | bit7:充电单体压差过大 | bit7:Chg Cell Volt Diff | Chg_cell_volt_diff | {0:正常;1:报警}
| 对外三级报警信息2（Warning） | External Warning2 |  | bit8:充电单体温差过大 | bit8:Chg Cell Temp Diff | Chg_cell_temp_diff | {0:正常;1:报警}
| 对外三级报警信息2（Warning） | External Warning2 |  | bit9:充电Pack压差过大 | bit9:Chg Module Volt Diff | Chg_odule_volt_diff | {0:正常;1:报警} | {0:Normal;1:Alarm} | [0~1]
| 对外三级报警信息2（Warning） | External Warning2 |  | bit10:放电单体压差过大 | bit10:Dsg Cell Volt Diff | Dsg_cell_volt_diff | {0:正常;1:报警} | {0:Normal;1:Alarm} | [0~1]
| 对外三级报警信息2（Warning） | External Warning2 |  | bit11:放电单体温差过大 | bit11:Dsg Cell Temp Diff | Dsg_cell_temp_diff | {0:正常;1:报警} | {0:Normal;1:Alarm} | [0~1]
| 对外三级报警信息2（Warning） | External Warning2 |  | bit12:放电Pack压差过大 | bit12:Dsg Module Volt Diff | Dsg_module_volt_diff | {0:正常;1:报警} | {0:Normal;1:Alarm} | [0~1]
|  |  |  | bit13:预留 | bit13:Reserve1 | Reserved1
|  |  |  | bit14:Pack内温差过大 | bit14:Pack Temp Diff | Pack_temp_diff | {0:正常;1:报警} | {0:Normal;1:Alarm} | [0~1]
| 对外三级报警信息2（Warning） | External Warning2 |  | bit15:预留 | bit15:Reserve2 | Reserved2
0x0080 | 预充状态 | Pre-chg_state | Pre_Charge_state |  |  |  | {0:待启动;1:预充中;2:预充中;3:预充成功;4:预充失败} | {0:Standy;1:Pre-Charging;2:Pre-Charging;3:Pre-Charge Success;4:Pre-Charge Fail} | [0~4] |  |  | R | U16 |  | 系统预充状态 | BCU | 0x0018
0x0081 | 运行状态 | Rack Run State | BCU_run_state |  |  |  | {0:正常;1:禁充;2:禁放;3:待机;4:停机} | {0:Normal;1:Full;2:Empty;3:Standby;4:Stop} | [0~4] |  |  | R | U16 |  | 当前系统状态 | BCU | 0x0019
0x0A84 | 总控配置的心跳帧 | BAU Synchronize Heart Beat | heart_beat_num | [5 empty] | [0~65535] |  |  | R/W | U16 |  |  | BCU | 0x001A
0x0082 | 接收配置信息状态 | Receive Config State | receive_cfg_state |  |  |  | {0:从控配置失败;1:从控配置成功} | {0:fail;1:success} | [0~1] |  |  | R | U16 |  | 主从can通信时，查看从控是否完成注册（预留） 枚举说明中1对应的内容为预留信息 | BCU | 0x001B
0x0085 | 预充失败原因 | Precharge Fail Reason | Pre_Charge_fail_reason | [8 empty] | R | U16 |  | 预留 | BCU | 0x001C
0x00A8 | 充放电状态(根据电流方向判断) | Chg/Dsg State | current_state |  |  |  | {0:静置;1:放电;2:充电} | {0:Rest;1:Discharge;2:Charge} | [0~2] |  |  | R | U16 |  |  | BCU | 0x001D
0x00AF | 充满放空标志 | Full Empty Flag | full_or_empty_flag | bit0:充满 | bit0:Full | Full | {0:无效;1:充满} | {0:Null;1:Full} | [0~1] |  |  | R | U16 |  |  | BCU | 0x001E
| 充满放空标志 | Full Empty Flag |  | bit1:放空 | bit1:Empty | Empty | {0:无效;1:放空} | {0:Null;1:Empty} | [0~1]
0x0104 | 接触器状态 | Contactor State | Contactor_state | bit0:正极接触器状态 | bit0:Positive Contactor State | Positive_contactor_state | {0:断开;1:闭合} | {0:Open;1:Close} | [0~1] |  | Hex | R | U16 |  |  | BCU | 0x001F
| 接触器状态 | Contactor State |  | bit1:预充接触器状态 | bit1:Pre-Charge Contactor State | Pre_Charge_contactor_state | {0:断开;1:闭合} | {0:Open;1:Close} | [0~1]
| 接触器状态 | Contactor State |  | bit2:负极接触器状态 | bit2:Negitive Contactor State | Negitive_contactor_state | {0:断开;1:闭合} | {0:Open;1:Close} | [0~1]
| 接触器状态 | Contactor State |  | bit3:隔离开关状态 | bit3:Disconnector State | Disconnector_state | {0:断开;1:闭合} | {0:Open;1:Close} | [0~1]
| 接触器状态 | Contactor State |  | bit4:正接触器2状态 | bit4:Positive Contactor2 State | Positive_contactor2_state | {0:断开;1:闭合} | {0:Open;1:Close} | [0~1]
| 接触器状态 | Contactor State |  | bit5:负接触器2状态 | bit5:Negitive Contactor2 State | Negitive_contactor2_state | {0:断开;1:闭合} | {0:Open;1:Close} | [0~1]
| 接触器状态 | Contactor State |  | bit6:光耦控制状态 | bit6:BoardIsolate Ctrl State | BoardIsolate_ctrl_state | {0:断开;1:闭合} | {0:Open;1:Close} | [0~1]
0x0115 | 从控故障状态 | BMU Fault State | BMU_fault_state | bit0:初始化故障 | bit0:Initialization Fault | Initialization_fault | {0:正常;1:故障} | {0:Normal;1:Fault} | [0~1] |  | Hex | R | U16 |  |  | BCU | 0x0020
| 从控故障状态 | BMU Fault State |  | bit1:采样线故障 | bit1:Sampling Line Fault | Sampling_line_fault | {0:正常;1:故障} | {0:Normal;1:Fault} | [0~1]
| 从控故障状态 | BMU Fault State |  | bit2:连接线故障 | bit2:Connection Line Fault | Connection_line_fault | {0:正常;1:故障} | {0:Normal;1:Fault} | [0~1]
| 从控故障状态 | BMU Fault State |  | bit3:采样芯片故障 | bit3:Sampling Chip Fault | Sampling_chip_fault | {0:正常;1:故障} | {0:Normal;1:Fault} | [0~1]
| 从控故障状态 | BMU Fault State |  | bit4:电压采样故障 | bit4:Voltage Sampling Fault | Voltage_sampling_fault | {0:正常;1:故障} | {0:Normal;1:Fault} | [0~1]
| 从控故障状态 | BMU Fault State |  | bit5:电池温度采样故障 | bit5:Cell Temperature Sampling Fault | Cell_temp_samp_fault | {0:正常;1:故障} | {0:Normal;1:Fault} | [0~1]
| 从控故障状态 | BMU Fault State |  | bit6:温度传感器故障 | bit6:Temperature sensor Fault | Temp_sensor_fault | {0:正常;1:故障} | {0:Normal;1:Fault} | [0~1]
| 从控故障状态 | BMU Fault State |  | bit7:接触器故障 | bit7:Contactor Fault | Contactor_fault | {0:正常;1:故障} | {0:Normal;1:Fault} | [0~1]
| 从控故障状态 | BMU Fault State |  | bit8:EEPROM故障 | bit8:EEPROM Fault | EEPROM_fault | {0:正常;1:故障} | {0:Normal;1:Fault} | [0~1]
| 从控故障状态 | BMU Fault State |  | bit9:被动均衡故障 | bit9:Passive Balance Fault | Passive_balance_fault | {0:正常;1:故障} | {0:Normal;1:Fault} | [0~1]
| 从控故障状态 | BMU Fault State |  | bit10:被动均衡温度故障 | bit10:Passive Balance Temperature Fault | Passive_balance_temp_fault | {0:正常;1:故障} | {0:Normal;1:Fault} | [0~1]
| 从控故障状态 | BMU Fault State |  | bit11:主动均衡故障 | bit11:Active Balance Fault | Active_balance_fault | {0:正常;1:故障} | {0:Normal;1:Fault} | [0~1]
| 从控故障状态 | BMU Fault State |  | bit12:主动均衡温度故障 | bit12:Active Balance Temperature Fault | Active_balance_temp_fault | {0:正常;1:故障} | {0:Normal;1:Fault} | [0~1]
| 从控故障状态 | BMU Fault State |  | bit13:极柱温度故障 | bit13:Terminal Temperature Fault | Terminal_temp_fault | {0:正常;1:故障} | {0:Normal;1:Fault} | [0~1]
| 从控故障状态 | BMU Fault State |  | bit14:组间均衡故障 | bit14:Pack Balance Fault | Pack_balance_fault | {0:正常;1:故障} | {0:Normal;1:Fault} | [0~1]
0x013F | 所有从控的通信故障信息高33-48位 | BMU Comm Fault State3 | BMU_comm_fault_state3 | bit(0~15):从控(33~48)通信故障 | bit(0~15):BMU(33~48) Comm Fault | BMU(33~48)_comm_fault | {0:正常;1:故障} | {0:Normal;1:Fault} | [0~1] |  | Hex | R | U16 |  |  | BCU | 0x0021
0x0133 | 所有从控的通信故障信息高16位 | BMU Comm Fault State H16B | BMU_comm_fault_state_h16b | bit(0~15):从控(17~32)通信故障 | bit(0~15):BMU(17~32) Comm Fault State | BMU(17~32)_comm_fault_state | {0:正常;1:故障} | {0:Normal;1:Fault} | [0~1] |  | Hex | R | U16 |  |  | BCU | 0x0022
0x0134 | 所有从控的通信故障信息低16位 | BMU Comm Fault State L16B | BMU_comm_fault_state_l16b | bit(0~15):从控(1~16)通信故障 | bit(0~15):BMU(1~16) Comm Fault State | BMU(1~16)_comm_fault_state | {0:正常;1:故障} | {0:Normal;1:Fault} | [0~1] |  | Hex | R | U16 |  |  | BCU | 0x0023
0x013C | 所有从控的概要故障信息33-48 | BMU Sum Fault State3 | BMU_sum_fault_state3 | bit(0~15):从控(33~48)概要故障 | bit(0~15):BMU(33~48) Sum Fault | BMU(33~48)_sum_fault | {0:正常;1:故障} | {0:Normal;1:Fault} | [0~1] |  | Hex | R | U16 |  |  | BCU | 0x0024
0x013D | 所有从控的概要故障信息17-32 | BMU Sum Fault State2 | BMU_sum_fault_state2 | bit(0~15):从控(17~32)概要故障 | bit(0~15):BMU(17~32) Sum Fault | BMU(17~32)_sum_fault | {0:正常;1:故障} | {0:Normal;1:Fault} | [0~1] |  | Hex | R | U16 |  |  | BCU | 0x0025
0x013E | 所有从控的概要故障信息1-16 | BMU Sum Fault State1 | BMU_sum_fault_state1 | bit(0~15):从控(1~16)概要故障 | bit(0~15):BMU(1~16) Sum Fault | BMU(1~16)_sum_fault | {0:正常;1:故障} | {0:Normal;1:Fault} | [0~1] |  | Hex | R | U16 |  |  | BCU | 0x0026
0x0A0E | 自动分配从控ID错误的从控编号 | auto_allocate_BMU_err_ID | auto_allocate_BMU_err_ID |  |  |  | {0:正常} | {0:normal} | [1~42] |  |  | R | U16 |  |  | BCU | 0x0027
0x0083 | 菊花链1第一片通信错误的芯片编号 | Chain1 First Communication Eerror Chip number | Chain1_1st_ comm_err_chip_num | (若只使用一条菊花链，即使使用的是菊花链2，也会在此处显示) | (If only one daisy chain is used, it will be shown here even if daisy chain 2 is used) |  |  |  | [0~21] |  |  | R | U16 |  | 菊花链1的第一片通信错误芯片编号 | BCU | 0x0028
0x0084 | 菊花链2第一片通信错误的芯片编号 | Chain2 First Communication Eerror Chip number | Chain2_1st_ comm_err_chip_num | [5 empty] | [0~21] |  |  | R | U16 |  | 菊花链2的第一片通信错误芯片编号 | BCU | 0x0029
0x01C0 | 主控软件项目编号 | BCU_software_project_num | BCU_software_project_num | [8 empty] | R | U16 |  |  | BCU | 0x002A
0x01C1 | 主控软件主版本号 | BCU_software_main_version_num | BCU_software_main_version_num | [5 empty] | [1~1000] |  |  | R | U16 |  |  | BCU | 0x002B
0x01C2 | 主控软件子版本号 | BCU_software_sub_version_num | BCU_software_sub_version_num | [5 empty] | [1~1000] |  |  | R | U16 |  |  | BCU | 0x002C
0x01C3 | 主控软件修正版本号 | BCU_software_main_revise_num | BCU_software_main_revise_num | [5 empty] | [1~1000] |  |  | R | U16 |  |  | BCU | 0x002D
0x01C5 | 主控硬件主版本号 | BCU_hardware_main_version_num | BCU_hardware_main_version_num | [8 empty] | R | U16 |  |  | BCU | 0x002E
0x01C6 | 主控硬件子版本号 | BCU_hardware_sub_version_num | BCU_hardware_sub_version_num | [8 empty] | R | U16 |  |  | BCU | 0x002F
0x0BD3 | 对外预提示 | External Warn TipI | External_warn_tipI | bit0:总压过高 | bit0:Total OV | Total_OV | {0:正常;1:故障} | {0:Normal;1:Alarm} | [0~1] |  | Hex | R | U16 |  |  | BCU | 0x0030
|  |  |  | bit1:总压过低 | bit1:Total UV | Total_UV | {0:正常;1:故障} | {0:Normal;1:Alarm} | [0~1]
|  |  |  | bit2:单体电压过高 | bit2:Cell OV | Cell_OV | {0:正常;1:故障} | {0:Normal;1:Alarm} | [0~1]
|  |  |  | bit3:单体电压过低 | bit3:Cell UV | Cell_UV | {0:正常;1:故障} | {0:Normal;1:Alarm} | [0~1]
|  |  |  | bit4:放电电流过大 | bit4:Dsg OC | Dsg_OC | {0:正常;1:故障} | {0:Normal;1:Alarm} | [0~1]
|  |  |  | bit5:充电电流过大 | bit5:Chg OC | Chg_OC | {0:正常;1:故障} | {0:Normal;1:Alarm} | [0~1]
|  |  |  | bit6:放电温度过高 | bit6:Dsg OT | Dsg_OT | {0:正常;1:故障} | {0:Normal;1:Alarm} | [0~1]
|  |  |  | bit7:放电温度过低 | bit7:Dsg UT | Dsg_UT | {0:正常;1:故障} | {0:Normal;1:Alarm} | [0~1]
|  |  |  | bit8:充电温度过高 | bit8:Chg OT | Chg_OT | {0:正常;1:故障} | {0:Normal;1:Alarm} | [0~1]
|  |  |  | bit9:充电温度过低 | bit9:Chg UT | Chg_UT | {0:正常;1:故障} | {0:Normal;1:Alarm} | [0~1]
|  |  |  | bit10:预留 | bit10:Reserved | Low_IR | {0:正常;1:故障} | {0:Normal;1:Alarm} | [0~1]
|  |  |  | bit11:预留 | bit11:Reserved | Term_OT | {0:正常;1:故障} | {0:Normal;1:Alarm} | [0~1]
|  |  |  | bit12:预留 | bit12:Reserved | PDU_OT | {0:正常;1:故障} | {0:Normal;1:Alarm} | [0~1]
|  |  |  | bit13:单体压差过大 | bit13:Cell OV Diff | Cell_OV_diff | {0:正常;1:故障} | {0:Normal;1:Alarm} | [0~1]
|  |  |  | bit14:单体温差过大 | bit14:Cell OT Diff | Cell_OT_diff | {0:正常;1:故障} | {0:Normal;1:Alarm} | [0~1]
|  |  |  | bit15:预留 | bit15:Reserved | Low_SOH | {0:正常;1:故障} | {0:Normal;1:Alarm} | [0~1]
0x0BD4 | 对外预提示II | External Warn TipII | External_warn_tipII | bit0:预留 | bit0:Reserved | Total_OV_diff | {0:正常;1:故障} | {0:Normal;1:Alarm} | [0~1] |  | Hex | R | U16 |  |  | BCU | 0x0031
|  |  |  | bit1:模组电压过高 | bit1:Module OverVoltage | Module_OV | {0:正常;1:故障} | {0:Normal;1:Alarm} | [0~1]
|  |  |  | bit2:模组电压过低 | bit2:Module UnderVoltage | Module_UV | {0:正常;1:故障} | {0:Normal;1:Alarm} | [0~1]
|  |  |  | bit3:预留 | bit3:Reserved | Cell_temp_rise | {0:正常;1:故障} | {0:Normal;1:Alarm} | [0~1]
|  |  |  | bit4:模组压差过大 | bit4:Module OverVoltage Difference | Module_OV_diff | {0:正常;1:故障} | {0:Normal;1:Alarm} | [0~1]
|  |  |  | bit5:预留 | bit5:Reserved | Run_warn_summary | {0:正常;1:故障} | {0:Normal;1:Alarm} | [0~1]
|  |  |  | bit6:预留 | bit6:Reserved | Copper_OT | {0:正常;1:报警} | {0:Normal;1:Alarm} | [0~1]
|  |  |  | bit7:充电单体压差过大 | bit7:Chg Cell Volt Diff | Chg_cell_volt_diff | {0:正常;1:报警} | {0:Normal;1:Alarm} | [0~1]
|  |  |  | bit8:充电单体温差过大 | bit8:Chg Cell Temp Diff | Chg_cell_temp_diff | {0:正常;1:报警} | {0:Normal;1:Alarm} | [0~1]
|  |  |  | bit9:充电模组压差过大 | bit9:Chg Moulde Volt Diff | Chg_module_volt_diff | {0:正常;1:报警} | {0:Normal;1:Alarm} | [0~1]
|  |  |  | bit10:放电单体压差过大 | bit10:Dsg Cell Volt Diff | Dsg_cell_volt_diff | {0:正常;1:报警} | {0:Normal;1:Alarm} | [0~1]
|  |  |  | bit11:放电单体温差过大 | bit11:Dsg Cell Temp Diff | Dsg_cell_temp_diff | {0:正常;1:报警} | {0:Normal;1:Alarm} | [0~1]
|  |  |  | bit12:放电模组压差过大 | bit12:Dsg Moulde Volt Diff | Dsg_module_volt_diff | {0:正常;1:报警} | {0:Normal;1:Alarm} | [0~1]
|  |  |  | bit13:预留 | bit13:Reserve1 | Reserved1
|  |  |  | bit14:Pack内温差过大 | bit14:Pack Temp Diff | Pack_temp_diff | {0:正常;1:报警} | {0:Normal;1:Alarm} | [0~1]
|  |  |  | bit15:预留 | bit15:Reserve2 | Reserved2
0xFFFF | 平台预留位置 | reserve60 | [9 empty] | R/W | U16 | 14 |  | BCU | 0x0032
0xFFFF | 项目部门预留位置 | reserve61 |  |  | 无 | [6 empty] | R/W | U16 | 32 | 特殊项目可以使用该空间 | BCU | 0x0040

## Rack Detail
Rack Detail -- EMS Read From BMS(BCU)
偏移地址 | 配置项中文名 | 配置项英文名 | 英文key | 中文使用说明 | 英文使用说明 | 英文子key | 说明(值/枚举说明) | 说明(值/枚举说明)(英文) | 范围 | 单位系数 | 单位 | 是否可写 | 数值格式 | 个数 | 备注 | 数据源 | Modbus地址
0x0400 | 单体电压 | Cell Voltege | Vcell | [5 empty] | [-5000~5000] | 1 | mV | R | S16 | 512 |  | BCU | 0x1401
| 预留 | reserve70 | reserve70 | [8 empty] | R | u16 | 512 |  | BCU | 0x1601
0x0200 | 单体温度 | Cell Temperature | Tcell | [5 empty] | [-400~1400] | 0.1 | ℃ | R | S16 | 512 |  | BCU | 0x1801
| 预留 | reserve71 | reserve71 | [8 empty] | R | u16 | 2048 |  | BCU | 0x1A01
0x0900 | 正极温度 | Tterm_pos | Tterm_pos | [5 empty] | [-400~1400] | 0.1 | ℃ | R | S16 | 128 |  | BCU | 0x2201
0x0980 | 负极温度 | Tterm_neg | Tterm_neg | [5 empty] | [-400~1400] | 0.1 | ℃ | R | S16 | 128 |  | BCU | 0x2281
0x1600 | 铜排温度 | Busbar Temp | Copper_temp | [5 empty] | [-400~1400] | 0.1 | ℃ | R | S16 | 128 |  | BCU | 0x2301
0x1680 | 冷却液温度 | Coolant Temp | Coolant_temp | [5 empty] | [-400~1400] | 0.1 | ℃ | R | S16 | 128 |  | BCU | 0x2381
| 预留 | reserve72 | [9 empty] | R | U16 | 4608 |  | BCU | 0x2401
| 平台预留位置 | reserve73 | [9 empty] | R | u16 | 256 |  | BCU | 0x3601
| 项目部门预留位置 | reserve74 |  | 无 | 无 | [6 empty] | R | u16 | 256 | 该部分不允许项目部自定义 | BCU | 0x3701

## Rack Measure
Rack Measure --EMS Read from BMS(BCU)
偏移地址 | 配置项中文名 | 配置项英文名 | 英文key | 中文使用说明 | 英文使用说明 | 英文子key | 说明(值/枚举说明) | 说明(值/枚举说明)(英文) | 范围 | 单位系数 | 单位 | 是否可写 | 数值格式 | 个数 | 备注 | 数据源 | Modbus地址
0x0089 | 最高单体电压 | Vcell_max | Vcell_max | [5 empty] | [-5000~5000] | 1 | mV | R | S16 |  |  | BCU | 0x0210
0x008A | 单体最高电压编号 | Num of Vcell_max | Vcell_max_num | [5 empty] | [0~300] |  |  | R | U16 |  | #编号 | BCU | 0x0211
0x008B | 最高单体所在模组编号 | Pack of Vcell_max | Vcell_max_pack | [5 empty] | [0~300] |  |  | R | U16 |  | #编号 | BCU | 0x0212
0x008C | 最高单体在模组中的单体编号 | Position of Vcell_max | Vcell_max_position | [5 empty] | [0~300] |  |  | R | U16 |  | #编号 | BCU | 0x0213
0x008D | 最低单体电压 | Vcell_min | Vcell_min | [5 empty] | [-5000~5000] | 1 | mV | R | S16 |  |  | BCU | 0x0214
0x008E | 单体最低电压编号 | Num of Vcell_min | Vcell_min_num | [5 empty] | [0~300] |  |  | R | U16 |  | #编号 | BCU | 0x0215
0x008F | 最低单体所在模组编号 | Pack of Vcell_min | Vcell_min_pack | [5 empty] | [0~300] |  |  | R | U16 |  | #编号 | BCU | 0x0216
0x0090 | 最低单体在模组中的单体编号 | Position of Vcell_min | Vcell_min_position | [5 empty] | [0~300] |  |  | R | U16 |  | #编号 | BCU | 0x0217
0x0091 | 单体压差 | Vcell_diff | Vcell_diff | [5 empty] | [0~5000] | 1 | mV | R | U16 |  |  | BCU | 0x0218
0x0092 | 平均单体电压 | Vcell_avg | Vcell_avg | [5 empty] | [-5000~5000] | 1 | mV | R | S16 |  |  | BCU | 0x0219
0x0093 | 最高单体温度 | Tcell_max | Tcell_max | [5 empty] | [-400~1400] | 0.1 | ℃ | R | S16 |  |  | BCU | 0x021A
0x0094 | 电池最高温度编号 | Num of Tcell_max | Tcell_max_num | [5 empty] | [0~300] |  |  | R | U16 |  | #编号 | BCU | 0x021B
0x0095 | 最高温度所在模组编号 | Pack of Tcell_max | Tcell_max_pack | [5 empty] | [0~300] |  |  | R | U16 |  | #编号 | BCU | 0x021C
0x0096 | 最高温度在模组中的温度编号 | Position of Tcell_max | Tcell_max_position | [5 empty] | [0~300] |  |  | R | U16 |  | #编号 | BCU | 0x021D
0x0097 | 最低单体温度 | Tcell_min | Tcell_min | [5 empty] | [-400~1400] | 0.1 | ℃ | R | S16 |  |  | BCU | 0x021E
0x0098 | 电池最低温度编号 | Num of Tcell_min | Tcell_min_num | [5 empty] | [0~300] |  |  | R | U16 |  | #编号 | BCU | 0x021F
0x0099 | 最低温度所在模组编号 | Pack of Tcell_min | Tcell_min_pack | [5 empty] | [0~300] |  |  | R | U16 |  | #编号 | BCU | 0x0220
0x009A | 最低温度在模组中的温度编号 | Position of Tcell_min | Tcell_min_position | [5 empty] | [0~300] |  |  | R | U16 |  | #编号 | BCU | 0x0221
0x009B | 平均单体温度 | Tcell_avg | Tcell_avg | [5 empty] | [-400~1400] | 0.1 | ℃ | R | S16 |  |  | BCU | 0x0222
0x009C | 最大极柱温度 | Tterm_max | Tterm_max | [5 empty] | [-400~1400] | 0.1 | ℃ | R | S16 |  |  | BCU | 0x0223
0x009D | 最大极柱温度位置 | Tterm_max_pos | Tterm_max_pos | [5 empty] | [0~200] |  |  | R | U16 |  |  | BCU | 0x0224
0x009E | 允许充电电流 | Irack_chg_limit | Irack_chg_limit | 限流模块输出，系统对外充电电流值 | Current limiting module output, system external charging current value |  |  |  | [0~6000] | 0.1 | A | R | U16 |  | 外部显示 | BCU | 0x0225
0x009F | 允许放电电流 | Irack_dsg_limit | Irack_dsg_limit | 限流模块输出，系统对外放电电流值 | Current limiting module output, system external discharge current value |  |  |  | [0~6000] | 0.1 | A | R | U16 |  | 外部显示 | BCU | 0x0226
0x00A0 | SOC | SOC | SOC | [5 empty] | [0~1000] |  | ‰ | R | U16 |  |  | BCU | 0x0227
0x00A1 | SOH | SOH | SOH | [5 empty] | [0~1000] |  | ‰ | R | U16 |  |  | BCU | 0x0228
0x00AE | 电池最大温差 | max_bat_temp_diff | max_bat_temp_diff | branch6.2之前该DB无效 | This DB is not valid before branch6.2 |  |  |  | [0~1800] | 0.1 | ℃ | R | U16 |  | 所有从控电池温度中，最大电池温度和最小电池温度的差值 | BCU | 0x0229
0x0A1C | 簇最高单体温升 | max_bat_temp_rise | max_bat_temp_rise | [5 empty] | [0~1400] |  | ℃ | R | U16 |  |  | BCU | 0x022A
0x0A1D | 簇最高单体温升电池包编号 | max_bat_temp_rise_bmu_num | max_bat_temp_rise_bmu_num | [5 empty] | [1~42] |  |  | R | U16 |  |  | BCU | 0x022B
0x0A1E | 簇最高单体温升电池包中单体温度编号 | max_bat_temp_rise _num_in_bmu | max_bat_temp_rise _num_in_bmu | [5 empty] | [1~512] |  |  | R | U16 |  |  | BCU | 0x022C
0x0A23 | 簇最高单体温升所有单体中的编号 | max_bat_temp_rise_num_in_bcu | max_bat_temp_rise_num_in_bcu | [5 empty] | [1~512] |  |  | R | U16 |  |  |  | 0x022D
0x00BF | 内部SOC | Inner SOC | Rack_Inner_SOC | [5 empty] | [0~1000] |  | ‰ | R | U16 |  | 内部SOC值（与db0x0040的值一致） | BCU | 0x022E
0x0088 | 预充总压 | Pre-Charge_volt | Pre_Charge_volt | [5 empty] | [-20000~20000] | 0.1 | V | R | S16 |  | 预充时，预充接触器总电压 | BCU | 0x022F
0x0086 | 从控电压累加和 | BMU_total_vol | BMU_total_vol | [5 empty] | [-20000~20000] | 0.1 | V | R | S16 |  | 查看所有从控电池电压累加和 | BCU | 0x0230
0x00C0 | 簇总压 | Rack Voltage | Vrack | [5 empty] | [-20000~20000] | 0.1 | V | R | S16 |  |  | BCU | 0x0231
0x00C8 | 簇电流 | Rack Current | Irack | [5 empty] | [-6000~6000] | 0.1 | A | R | S16 |  |  | BCU | 0x0232
0x00C3 | K_总电压 | Ncon Total Volt | ncon_total_vol | 菊花链无效 | Daisy chain invalid |  |  |  | [-20000~20000] | 0.1 | V | R | S16 |  |  | BCU | 0x0233
0x00D0 | 预留 | reserve118 | reserve118 | [8 empty] | R | U16 | 3 |  | BCU | 0x0234
0x00CB | 绝缘电阻 | IR | IR | [5 empty] | [0~20000] |  | kΩ | R | U16 |  |  | BCU | 0x0237
0x00CC | 正极绝缘 | IR_pos | IR_pos | [5 empty] | [0~20000] |  | kΩ | R | U16 |  |  | BCU | 0x0238
0x00CD | 负极绝缘 | IR_neg | IR_neg | [5 empty] | [0~20000] |  | kΩ | R | U16 |  |  | BCU | 0x0239
0x00CE | 供电采样电压 | Supply Sample Voltage | supply_sample_vol | [5 empty] | [9000~32000] |  | mV | R | U16 |  |  | BCU | 0x023A
0x00E9 | 高压箱最高温度 | PDU Maximum Temperature | PDU_max_temp | [5 empty] | [-400~1400] | 0.1 | ℃ | R | S16 |  |  | BCU | 0x023B
0x00F3 | 高压箱温度1 | PDU Temperature1 | PDU_temp1 | [5 empty] | [-400~1400] | 0.1 | ℃ | R | S16 |  |  | BCU | 0x023C
0x00F4 | 高压箱温度2 | PDU Temperature2 | PDU_temp2 | [5 empty] | [-400~1400] | 0.1 | ℃ | R | S16 |  |  | BCU | 0x023D
0x00F5 | 高压箱温度3 | PDU Temperature3 | PDU_temp3 | [5 empty] | [-400~1400] | 0.1 | ℃ | R | S16 |  |  | BCU | 0x023E
0x00F6 | 高压箱温度4 | PDU Temperature4 | PDU_temp4 | [5 empty] | [-400~1400] | 0.1 | ℃ | R | S16 |  |  | BCU | 0x023F
0xFFFF | 高压箱温度5,6,7,8 | reserve80 | reserve80 | 预留 | reserve |  |  |  |  | 0.1 | ℃ | R | s16 | 4 |  | BCU | 0x0240
0x00FB | 高压互锁采样 | Hvil In Sample | HVIL_in_sample | 预留 | Rreserve |  |  |  | [0~100] |  | % | R | U16 |  |  | BCU | 0x0244
0x0A0F | 电池簇内阻 | Rack Inner DCR | clu_resistance | [7 empty] | mΩ | R | U16 |  |  | BCU | 0x0245
0x0A19 | 当月累计充电能量 | Month Chg Energy | Month_Echg_curr | [5 empty] | [0~65535] |  | kWh | R | U16 |  |  | BCU | 0x0246
0x0A1A | 当月累计放电能量 | Month Dsg Energy | Month_Edsg_curr | [5 empty] | [0~65535] |  | kWh | R | U16 |  |  | BCU | 0x0247
0x0A2D | 当年累计充电能量 | Year Chg Energy | Year_Echg_cum | [5 empty] | [0~4294967295] |  | kWh | R | U32 |  |  | BCU | 0x0248
0x0A2F | 当年累计放电能量 | Year Dsg Energy | Year_Edsg_cum | [5 empty] | [0~4294967295] |  | kWh | R | U32 |  |  | BCU | 0x024A
0x0A31 | 总累计充电容量 | Chg Capacity All | Total_Echg_cum | [5 empty] | [0~4294967295] |  | Ah | R | U32 |  |  | BCU | 0x024C
0x0A33 | 总累计放电容量 | Dsg Capacity All | Total_Edsg_cum | [5 empty] | [0~4294967295] |  | Ah | R | U32 |  |  | BCU | 0x024E
0x01CD | 报警时最高单体电压位置 | Alarm Vcell Max Pos | Alarm_Vcell_max_pos | [5 empty] | [0~512] |  |  | R | U16 |  |  | BCU | 0x0250
0x01CE | 报警时最高单体电压值 | Alarm Vcell Max | Alarm_Vcell_max | [5 empty] | [-5000~5000] |  | mV | R | S16 |  |  | BCU | 0x0251
0x01CF | 停机时最高单体电压位置 | Stop Vcell Max Pos | Stop_Vcell_max_pos | [5 empty] | [0~512] |  |  | R | U16 |  |  | BCU | 0x0252
0x01D0 | 停机时最高单体电压值 | Stop Vcell Max | Stop_Vcell_max | [5 empty] | [-5000~5000] |  | mV | R | S16 |  |  | BCU | 0x0253
0x01D1 | 报警时最低单体电压位置 | Alarm Vcell Min Pos | Alarm_Vcell_min_pos | [5 empty] | [0~512] |  |  | R | U16 |  |  | BCU | 0x0254
0x01D2 | 报警时最低单体电压值 | Alarm Vcell Min | Alarm_Vcell_min | [5 empty] | [-5000~5000] |  | mV | R | S16 |  |  | BCU | 0x0255
0x01D3 | 停机时最低单体电压位置 | Stop Vcell Min Pos | Stop_Vcell_min_pos | [5 empty] | [0~512] |  |  | R | U16 |  |  | BCU | 0x0256
0x01D4 | 停机时最低单体电压值 | Stop Vcell Min | Stop_Vcell_min | [5 empty] | [-5000~5000] |  | mV | R | S16 |  |  | BCU | 0x0257
0x01D5 | 簇总压过高报警时电压值 | Rack OV Alarm Voltage | Pack_OV_alarm_voltage | [5 empty] | [-3000~3000] | 0.1 | V | R | S16 |  |  | BCU | 0x0258
0x01D6 | 簇总压过高停机时电压值 | Rack OV Stop Voltage | Pack_OV_stop_voltage | [5 empty] | [-3000~3000] | 0.1 | V | R | S16 |  |  | BCU | 0x0259
0x01D7 | 簇总压过低报警时电压值 | Rack UV Alarm Voltage | Pack_UV_alarm_voltage | [5 empty] | [-3000~3000] | 0.1 | V | R | S16 |  |  | BCU | 0x025A
0x01D8 | 簇总压过低停机时电压值 | Rack UV Stop Voltage | Pack_UV_stop_voltage | [5 empty] | [-3000~3000] | 0.1 | V | R | S16 |  |  | BCU | 0x025B
0x01D9 | 单体充电电流过大报警时电流值 | Cell Chg OC Alarm Current | Cell_chg_OC_alarm_current | [5 empty] | [-6000~6000] | 0.1 | A | R | S16 |  |  | BCU | 0x025C
0x01DA | 单体充电电流过大停机时电流值 | Cell Chg OC Stop Current | Cell_chg_OC_stop_current | [5 empty] | [-6000~6000] | 0.1 | A | R | S16 |  |  | BCU | 0x025D
0x01DB | 单体放电电流过大报警时电流值 | Cell Dsg OC Alarm Current | Cell_dsg_OC_alarm_current | [5 empty] | [-6000~6000] | 0.1 | A | R | S16 |  |  | BCU | 0x025E
0x01DC | 单体放电电流过大停机时电流值 | Cell Dsg OC Stop Current | Cell_dsg_OC_stop_current | [5 empty] | [-6000~6000] | 0.1 | A | R | S16 |  |  | BCU | 0x025F
0x01DD | 报警时最高单体温度位置 | Alarm Tcell Max Pos | Alarm_Tcell_max_pos | [5 empty] | [0~300] |  |  | R | U16 |  |  | BCU | 0x0260
0x01DE | 报警时最高单体温度值 | Alarm Tcell Max | Alarm_Tcell_max | [5 empty] | [-400~1400] | 0.1 | ℃ | R | S16 |  |  | BCU | 0x0261
0x01DF | 停机时最高单体温度位置 | Stop Tcell Max Pos | Stop_Tcell_max_pos | [5 empty] | [0~512] |  |  | R | U16 |  |  | BCU | 0x0262
0x01E0 | 停机时最高单体温度值 | Stop Tcell Max | Stop_Tcell_max | [5 empty] | [-400~1400] | 0.1 | ℃ | R | S16 |  |  | BCU | 0x0263
0x01E1 | 报警时最低单体温度位置 | Alarm Tcell Min Pos | Alarm_Tcell_min_pos | [5 empty] | [0~512] |  |  | R | U16 |  |  | BCU | 0x0264
0x01E2 | 报警时最低单体温度值 | Alarm Tcell Min | Alarm_Tcell_min | [5 empty] | [-400~1400] | 0.1 | ℃ | R | S16 |  |  | BCU | 0x0265
0x01E3 | 停机时最低单体温度位置 | Stop Tcell Min Pos | Stop_Tcell_min_pos | [5 empty] | [0~512] |  |  | R | U16 |  |  | BCU | 0x0266
0x01E4 | 停机时最低单体温度值 | Stop Tcell Min | Stop_Tcell_min | [5 empty] | [-400~1400] | 0.1 | ℃ | R | S16 |  |  | BCU | 0x0267
0x01E5 | 报警时高压箱最高温度值 | Alarm PDU Temp Max | Alarm_PDU_Temp_max | [5 empty] | [-400~1400] | 0.1 | ℃ | R | S16 |  |  | BCU | 0x0268
0x01E6 | 停机时高压箱最高温度值 | Stop PDU Temp Max | Stop_PDU_Temp_max | [5 empty] | [-400~1400] | 0.1 | ℃ | R | S16 |  |  | BCU | 0x0269
0x01E7 | 温升报警时电池编号 | Temp Rise Alm Bat Num | temp_rise_alm_bat_num | [5 empty] | [0~512] |  |  | R | U16 |  |  | BCU | 0x026A
0x01E8 | 温升报警时温升值 | Temp Rise Alm Value | temp_rise_alm_value | [5 empty] | [0~1400] | 0.1 | ℃/S | R | U16 |  |  | BCU | 0x026B
0x01E9 | 温升停机时电池编号 | Temp Rise Halt Bat Num | temp_rise_halt_bat_num | [5 empty] | [0~512] |  |  | R | U16 |  |  | BCU | 0x026C
0x01EA | 温升停机时温升值 | Temp Rise Halt Value | temp_rise_halt_value | [5 empty] | [0~1400] | 0.1 | ℃/S | R | U16 |  |  | BCU | 0x026D
0x01EB | 报警时最高极柱温度位置 | Alarm Tterm Max Pos | Alarm_Tterm_max_pos | [5 empty] | [0~512] |  |  | R | U16 |  |  | BCU | 0x026E
0x01EC | 报警时最高极柱温度 | Alarm Tterm Max | Alarm_Tterm_max | [5 empty] | [-400~1400] | 0.1 | ℃ | R | S16 |  |  | BCU | 0x026F
0x01ED | 停机时最高极柱温度位置 | Stop Tterm Max Pos | Stop_Tterm_max_pos | [5 empty] | [0~512] |  |  | R | U16 |  |  | BCU | 0x0270
0x01EE | 停机时最高极柱温度 | Stop Tterm Max | Stop_Tterm_max | [5 empty] | [-400~1400] | 0.1 | ℃ | R | S16 |  |  | BCU | 0x0271
0x01EF | 单体压差过大报警时压差值 | Cell Volt Diff Alarm Voltage | Cell_volt_diff_alarm_voltage | [5 empty] | [0~5000] |  | mV | R | U16 |  |  | BCU | 0x0272
0x01F0 | 单体压差过大停机时压差值 | Cell Volt Diff Stop Voltage | Cell_volt_diff_stop_voltage | [5 empty] | [0~5000] |  | mV | R | U16 |  |  | BCU | 0x0273
0x01F1 | 绝缘阻值过低报警时阻值 | Low IR Alarm Resistance | Low_IR_alarm_resistance | [5 empty] | [0~65535]] |  | Ω/V | R | U16 |  |  | BCU | 0x0274
0x01F2 | 绝缘阻值过低停机时阻值 | Low IR Stop Resistance | Low_IR_stop_resistance | [5 empty] | [0~65535]] |  | Ω/V | R | U16 |  |  | BCU | 0x0275
0x01F3 | 总电压和从控总电压压差过大告警时差值 | BCU BMU Vol Diff Hi Alm Value | BCU_BMU_vol_diff_hi_alm_value | [5 empty] | [0~20000] | 0.1 | V | R | U16 |  |  | BCU | 0x0276
0x01F4 | 总电压和从控总电压压差过大停机时差值 | BCU BMU Vol Diff Hi Halt Value | BCU_BMU_vol_diff_hi_halt_value | [5 empty] | [0~20000] | 0.1 | V | R | U16 |  |  | BCU | 0x0277
0x01F5 | 电池单体温度最高最低之间温差过大告警时压差值 | Cell Temp Diff Hi Alm Value | cell_temp_diff_hi_alm_value | [5 empty] | [0~1800] | 0.1 | ℃ | R | U16 |  |  | BCU | 0x0278
0x01F6 | 单体温差过大停机时温差值 | Cell Temp Diff Stop Temp | Cell_temp_diff_stop_Temp | [5 empty] | [0~1800] | 0.1 | ℃ | R | U16 |  |  | BCU | 0x0279
0x01F7 | 告警时最高Pack电压编号 | Alm Max Pack Vol Num | alm_max_module_vol_num | [5 empty] | [0~42] |  |  | R | U16 |  |  | BCU | 0x027A
0x01F8 | Pack电压过高告警时电压值 | Pack Vol Hi Alm Value | module_vol_hi_alm_value | [5 empty] | [0~600] | 0.1 | V | R | S16 |  |  | BCU | 0x027B
0x01F9 | 停机时最高Pack电压编号 | Halt Max Pack Vol Num | halt_max_module_vol_num | [5 empty] | [0~42] |  |  | R | U16 |  |  | BCU | 0x027C
0x01FA | Pack电压过高停机时电压值 | Pack Vol Hi Halt Value | module_vol_hi_halt_value | [5 empty] | [0~600] | 0.1 | V | R | S16 |  |  | BCU | 0x027D
0x01FB | 告警时最低Pack电压编号 | Alm Min Pack Vol Num | alm_min_module_vol_num | [5 empty] | [0~42] |  |  | R | U16 |  |  | BCU | 0x027E
0x01FC | Pack电压过低告警时电压值 | Pack Vol Low Alm Value | module_vol_low_alm_value | [5 empty] | [0~600] | 0.1 | V | R | S16 |  |  | BCU | 0x027F
0x01FD | 停机时最低Pack电压编号 | Halt Min Pack Vol Num | halt_min_module_vol_num | [5 empty] | [0~42] |  |  | R | U16 |  |  | BCU | 0x0280
0x01FE | Pack电压过低停机时电压值 | Pack Vol Low Halt Value | module_vol_low_halt_value | [5 empty] | [0~600] | 0.1 | V | R | S16 |  |  | BCU | 0x0281
0x00BB | 当天累计充电能量 | Today_Echg_cum | Today_Echg_cum | [5 empty] | [0~65535] |  | kWh | R | U16 |  |  | BCU | 0x0282
0x00BC | 当天累计放电能量 | Today_Edsg_cum | Today_Edsg_cum | [5 empty] | [0~65535] |  | kWh | R | U16 |  |  | BCU | 0x0283
0x0BF2 | 最大铜排温度 | Max Busbar Temp | Tcopper_max | [5 empty] | [-400~1400] | 0.1 | ℃ | R | S16 |  |  | BCU | 0x0284
0x0BF3 | 最大铜排温度位置 | Max Busbar Temp Position | Pos_of_Tcopper_max | [5 empty] | [0~200] |  |  | R | U16 |  |  | BCU | 0x0285
0x0BF4 | 最大冷却液温度 | Max Coolant Temp | TCoolant _max | [5 empty] | [-400~1400] | 0.1 | ℃ | R | S16 |  |  | BCU | 0x0286
0x0BF5 | 最大冷却液温度位置 | Max Coolant Temp Position | Pos_of_TCoolant_max | [5 empty] | [0~200] |  |  | R | U16 |  |  | BCU | 0x0287
| 平台预留位置 | reserve81 | [9 empty] | R | U16 | 122 |  | BCU | 0x0288
| 项目部门预留位置 | reserve82 |  | 无 | 无 | [6 empty] | R | u16 | 128 | 特殊项目可以使用该空间 | BCU | 0x0302

## Rack Control
Rack Control -- EMS Write into BMS(BCU)
偏移地址 | 配置项中文名 | 配置项英文名 | 英文key | 中文使用说明 | 英文使用说明 | 英文子key | 说明(值/枚举说明) | 说明(值/枚举说明)(英文) | 范围 | 单位系数 | 单位 | 是否可写 | 数值格式 | 个数 | 备注 | 数据源 | Modbus地址
0x0010 | 启动绝缘采样 | Start Insulation Sampling | start_insulation_sampleing | 绝缘采样开启之后，需过3S才能再次开启。 | After the insulation sampling is turned on, it takes 3S to turn it on again. |  | {0:关闭;1:开始} | {0:Stop;1:Start} | [0~1] |  |  | R/W | U16 |  |  | BCU/EMS | 0x0401
0x0011 | 预充控制 | Start Pre Chg Operate | start_pre_chg_operate |  |  |  | {1:开启预充;0:断开预充总正} | {1:start;0:Stop} | [0~1] |  |  | R/W | U16 |  |  | BCU/EMS | 0x0402
0x0000 | 主控复位 | BCU Reset | BCU_reset |  |  |  | {0x00:无效;0x01:复位} | {0x00:invalidity;0x01:Reset } | [0~1] |  | Hex | R/W | U16 |  |  | BCU/EMS | 0x0403
0x0009 | 重置从控ID | Reset BMU ID Operate | Reset_BMU_ID |  |  |  | {0x01:使能;0x02:不使能} | {0x01:Enable;0x02:Disable} | [1~2] |  | Hex | R/W | U16 |  |  | BCU/EMS | 0x0404
0x0012 | 设置主控地址 | Configure BCU ID | config_BCU_ID | 最小值为1^>=1 | The minimum value is 1^>=1 |  |  |  | [1~64] |  |  | R/W | U16 |  |  | BCU/EMS | 0x0405
0x001B | 风扇强控开关 | Fan Switch | Fan_forced_control_switch |  |  |  | {0:无;1:开启;2:关闭} | {0:None;1:ON;2:OFF} | [0~2] |  |  | R/W | U16 |  |  | BCU/EMS | 0x0406
| 平台预留位置 | reserve90 |  | 无 | 无 | [6 empty] | R/W | U16 | 94 |  | BCU | 0x0407
| 项目部门预留位置 | reserve91 |  | 无 | 无 | [6 empty] | R/W | U16 | 32 | 特殊项目可以使用该空间 | BCU | 0x0465
| 预留 | reserve92 |  | 预留 | 控制占空比0-128 | [6 empty] | R/W | U16 | 512 |  | BCU/EMS | 0x0601

## Rack_Parameter Set & Read
RACK Alarm Parameter Threshold Set & Read
Register type: Rack参数设置(保持寄存器, 每Rack Modbus地址独立,从2开始,功能码:0x10或0x06); Rack Parameter Settings (Holding Registers Modbus Addr:each rack independent,from 2 Function Code:0x10 or 0x06)
Modbus Addr: 2 to N+1 (N is rack number)
偏移地址 | 配置项中文名 | 配置项英文名 | 英文key | 中文使用说明 | 英文使用说明 | 英文子key | 说明(值/枚举说明) | 说明(值/枚举说明)(英文) | 范围 | 单位系数 | 单位 | 是否可写 | 数值格式 | 个数 | 备注 | 数据源 | Modbus地址
0x015A | 单体电压过高三级报警 | Cell OV Level 3 Alarm | Cell_OV_lvl3_alarm | [5 empty] | [-5000~5000] |  | mV | R/W | S16 |  |  | BAU, BCU[1] | 0x6001
0x019A | 单体电压过高三级报警恢复值 | Cell OV Level 3 Alarm Recovery | Cell_OV_lvl3_alarm_recovery | [5 empty] | [-5000~5000] |  | mV | R/W | S16 |  |  | BAU, BCU[1] | 0x6002
0x015E | 单体电压过低三级报警 | Cell UV Level 3 Alarm | Cell_UV_lvl3_alarm | [5 empty] | [-5000~5000] |  | mV | R/W | S16 |  |  | BAU, BCU[1] | 0x6003
0x019E | 单体电压过低三级报警恢复值 | Cell UV Level 3 Alarm Recovery | Cell_UV_lvl3_alarm_recovery | [5 empty] | [-5000~5000] |  | mV | R/W | S16 |  |  | BAU, BCU[1] | 0x6004
0x0142 | 簇总压过高三级报警 | Rack OV Level 3 Alarm | Rack_OV_lvl3_alarm | [5 empty] | [-32767~32767] | 0.1 | V | R/W | S16 |  |  | BAU, BCU[1] | 0x6005
0x0182 | 簇总压过高三级报警恢复值 | Rack OV Level 3 Alarm Recovery | Rack_OV_lvl3_alarm_recovery | [5 empty] | [-32767~32767] | 0.1 | V | R/W | S16 |  |  | BAU, BCU[1] | 0x6006
0x0145 | 簇总压过低三级报警 | Rack UV Level 3 Alarm | Rack_UV_lvl3_alarm | [5 empty] | [-32767~32767] | 0.1 | V | R/W | S16 |  |  | BAU, BCU[1] | 0x6007
0x0185 | 簇总压过低三级报警恢复值 | Rack UV Level 3 Alarm Recovery | Rack_UV_lvl3_alarm_recovery | [5 empty] | [-32767~32767] | 0.1 | V | R/W | S16 |  |  | BAU, BCU[1] | 0x6008
0x017D | 充电电流过大三级报警 | Chg OC Level 3 Alarm | Chg_OC_lvl3_alarm | [5 empty] | [-32767~32767] | 0.1 | A | R/W | S16 |  |  | BAU, BCU[1] | 0x6009
0x01BD | 充电电流过大三级报警恢复值 | Chg OC Level 3 Alarm Recovery | Chg_OC_lvl3_alarm_recovery | [5 empty] | [-32767~32767] | 0.1 | A | R/W | S16 |  |  | BAU, BCU[1] | 0x600A
0x017A | 放电电流过大三级报警 | Dsg OC Level 3 Alarm | Dsg_OC_lvl3_alarm | [5 empty] | [-32767~32767] | 0.1 | A | R/W | S16 |  |  | BAU, BCU[1] | 0x600B
0x01BA | 放电电流过大三级报警恢复值 | Dsg OC Level 3 Alarm Recovery | Dsg_OC_lvl3_alarm_recovery | [5 empty] | [-32767~32767] | 0.1 | A | R/W | S16 |  |  | BAU, BCU[1] | 0x600C
0x0171 | 充电温度过高三级报警 | Chg OT Level 3 Alarm | Chg_OT_lvl3_alarm | [5 empty] | [-400~1400] | 0.1 | ℃ | R/W | S16 |  |  | BAU, BCU[1] | 0x600D
0x01B1 | 充电温度过高三级报警恢复值 | Chg OT Level 3 Alarm Recovery | Chg_OT_lvl3_alarm_recovery | [5 empty] | [-400~1400] | 0.1 | ℃ | R/W | S16 |  |  | BAU, BCU[1] | 0x600E
0x0174 | 充电温度过低三级报警 | Chg UT Level 3 Alarm | Chg_UT_lvl3_alarm | [5 empty] | [-400~1400] | 0.1 | ℃ | R/W | S16 |  |  | BAU, BCU[1] | 0x600F
0x01B4 | 充电温度过低三级报警恢复值 | Chg UT Level 3 Alarm Recovery | Chg_UT_lvl3_alarm_recovery | [5 empty] | [-400~1400] | 0.1 | ℃ | R/W | S16 |  |  | BAU, BCU[1] | 0x6010
0x014E | SOC过低三级报警 | Low SOC Level 3 Alarm | Low_SOC_lvl3_alarm | [5 empty] | [0~100] |  | % | R/W | U16 |  |  | BAU, BCU[1] | 0x6011
0x018E | SOC过低三级报警恢复值 | Low SOC Level 3 Alarm Recovery | Low_SOC_lvl3_alarm_recovery | [5 empty] | [0~100] |  | % | R/W | U16 |  |  | BAU, BCU[1] | 0x6012
0x0177 | 极柱温度过高三级报警 | Term OT Level 3 Alarm | Term_OT_lvl3_alarm | [5 empty] | [-400~1400] | 0.1 | ℃ | R/W | S16 |  |  | BAU, BCU[1] | 0x6013
0x01B7 | 极柱温度过高三级报警恢复值 | Term OT Level 3 Alarm Recovery | Term_OT_lvl3_alarm_recovery | [5 empty] | [-400~1400] | 0.1 | ℃ | R/W | S16 |  |  | BAU, BCU[1] | 0x6014
0x014B | 绝缘阻值过低三级报警 | Low IR Level 3 Alarm | Low_IR_lvl3_alarm | [5 empty] | [0~65535] |  | Ω/V | R/W | U16 |  |  | BAU, BCU[1] | 0x6015
0x018B | 绝缘阻值过低三级报警恢复值 | Low IR Level 3 Alarm Recovery | Low_IR_lvl3_alarm_recovery | [5 empty] | [0~65535] |  | Ω/V | R/W | U16 |  |  | BAU, BCU[1] | 0x6016
0x0162 | 单体压差过大三级报警 | Cell Volt Diff Level 3 Alarm | Cell_volt_diff_lvl3_alarm | [5 empty] | [-5000~5000] |  | mV | R/W | S16 |  |  | BAU, BCU[1] | 0x6017
0x01A2 | 单体压差过大三级报警恢复值 | Cell Volt Diff Level 3 Alarm Recovery | Cell_volt_diff_lvl3_alarm_recovery | [5 empty] | [-5000~5000] |  | mV | R/W | S16 |  |  | BAU, BCU[1] | 0x6018
0x0148 | 簇总压校验差过大三级报警 | Rack Volt Calibration Level 3 Alarm | Vrack_cal_diff_lvl3_alarm | [5 empty] | [-32767~32767] | 0.1 | V | R/W | S16 |  |  | BAU, BCU[1] | 0x6019
0x0188 | 簇总压校验差过大三级报警恢复值 | Rack Volt Calibration Level 3 Alarm Recovery | Vrack_cal_diff_lvl3_alarm_recovery | [5 empty] | [-32767~32767] | 0.1 | V | R/W | S16 |  |  | BAU, BCU[1] | 0x601A
0x0165 | 单体温度过高三级报警 | Cell OT Level 3 Alarm | Cell_OT_lvl3_alarm | [5 empty] | [-400~1400] | 0.1 | ℃ | R/W | S16 |  |  | BAU, BCU[1] | 0x601B
0x01A5 | 单体温度过高三级报警恢复值 | Cell OT Level 3 Alarm Recovery | Cell_OT_lvl3_alarm_recovery | [5 empty] | [-400~1400] | 0.1 | ℃ | R/W | S16 |  |  | BAU, BCU[1] | 0x601C
0x0168 | 单体温度过低三级报警 | Cell UT Level 3 Alarm | Cell_UT_lvl3_alarm | [5 empty] | [-400~1400] | 0.1 | ℃ | R/W | S16 |  |  | BAU, BCU[1] | 0x601D
0x01A8 | 单体温度过低三级报警恢复值 | Cell UT Level 3 Alarm Recovery | Cell_UT_lvl3_alarm_recovery | [5 empty] | [-400~1400] | 0.1 | ℃ | R/W | S16 |  |  | BAU, BCU[1] | 0x601E
0x016B | 单体温差过大三级报警 | Cell Temp Diff Level 3 Alarm | Cell_temp_diff_lvl3_alarm | [5 empty] | [-400~1400] | 0.1 | ℃ | R/W | S16 |  |  | BAU, BCU[1] | 0x601F
0x01AB | 单体温差过大三级报警恢复值 | Cell Temp Diff Level 3 Alarm Recovery | Cell_temp_diff_lvl3_alarm_recovery | [5 empty] | [-400~1400] | 0.1 | ℃ | R/W | S16 |  |  | BAU, BCU[1] | 0x6020
0x0157 | 高压箱温度过高三级报警 | PDU OT Level 3 Alarm | PDU_OT_lvl3_alarm | [5 empty] | [-400~1400] | 0.1 | ℃ | R/W | S16 |  |  | BAU, BCU[1] | 0x6021
0x0197 | 高压箱温度过高三级报警恢复值 | PDU OT Level 3 Alarm Recovery | PDU_OT_lvl3_alarm_recovery | [5 empty] | [-400~1400] | 0.1 | ℃ | R/W | S16 |  |  | BAU, BCU[1] | 0x6022
0x0159 | 单体电压过高二级报警 | Cell OV Level 2 Alarm | Cell_OV_lvl2_alarm | [5 empty] | [-5000~5000] |  | mV | R/W | S16 |  |  | BAU, BCU[1] | 0x6023
0x0199 | 单体电压过高二级报警恢复值 | Cell OV Level 2 Alarm Recovery | Cell_OV_lvl2_alarm_recovery | [5 empty] | [-5000~5000] |  | mV | R/W | S16 |  |  | BAU, BCU[1] | 0x6024
0x015D | 单体电压过低二级报警 | Cell UV Level 2 Alarm | Cell_UV_lvl2_alarm | [5 empty] | [-5000~5000] |  | mV | R/W | S16 |  |  | BAU, BCU[1] | 0x6025
0x019D | 单体电压极高报警恢复值 | Cell Safety OV Alarm Recovery | Cell_UV_lvl2_alarm_recovery | [5 empty] | [-5000~5000] |  | mV | R/W | S16 |  |  | BAU, BCU[1] | 0x6026
0x0141 | 簇总压过高二级报警 | Rack OV Level 2 Alarm | Rack_OV_lvl2_alarm | [5 empty] | [-32767~32767] | 0.1 | V | R/W | S16 |  |  | BAU, BCU[1] | 0x6027
0x0181 | 簇总压过高二级报警恢复值 | Rack OV Level 2 Alarm Recovery | Rack_OV_lvl2_alarm_recovery | [5 empty] | [-32767~32767] | 0.1 | V | R/W | S16 |  |  | BAU, BCU[1] | 0x6028
0x0144 | 簇总压过低二级报警 | Rack UV Level 2 Alarm | Rack_UV_lvl2_alarm | [5 empty] | [-32767~32767] | 0.1 | V | R/W | S16 |  |  | BAU, BCU[1] | 0x6029
0x0184 | 簇总压过低二级报警恢复值 | Rack UV Level 2 Alarm Recovery | Rack_UV_lvl2_alarm_recovery | [5 empty] | [-32767~32767] | 0.1 | V | R/W | S16 |  |  | BAU, BCU[1] | 0x602A
0x017C | 充电电流过大二级报警 | Chg OC Level 2 Alarm | Chg_OC_lvl2_alarm | [5 empty] | [-32767~32767] | 0.1 | A | R/W | S16 |  |  | BAU, BCU[1] | 0x602B
0x01BC | 充电电流过大二级报警恢复值 | Chg OC Level 2 Alarm Recovery | Chg_OC_lvl2_alarm_recovery | [5 empty] | [-32767~32767] | 0.1 | A | R/W | S16 |  |  | BAU, BCU[1] | 0x602C
0x0179 | 放电电流过大二级报警 | Dsg OC Level 2 Alarm | Dsg_OC_lvl2_alarm | [5 empty] | [-32767~32767] | 0.1 | A | R/W | S16 |  |  | BAU, BCU[1] | 0x602D
0x01B9 | 放电电流过大二级报警恢复值 | Dsg OC Level 2 Alarm Recovery | Dsg_OC_lvl2_alarm_recovery | [5 empty] | [-32767~32767] | 0.1 | A | R/W | S16 |  |  | BAU, BCU[1] | 0x602E
0x0170 | 充电温度过高二级报警 | Chg OT Level 2 Alarm | Chg_OT_lvl2_alarm | [5 empty] | [-400~1400] | 0.1 | ℃ | R/W | S16 |  |  | BAU, BCU[1] | 0x602F
0x01B0 | 充电温度过高二级报警恢复值 | Chg OT Level 2 Alarm Recovery | Chg_OT_lvl2_alarm_recovery | [5 empty] | [-400~1400] | 0.1 | ℃ | R/W | S16 |  |  | BAU, BCU[1] | 0x6030
0x0173 | 充电温度过低二级报警 | Chg UT Level 2 Alarm | Chg_UT_lvl2_alarm | [5 empty] | [-400~1400] | 0.1 | ℃ | R/W | S16 |  |  | BAU, BCU[1] | 0x6031
0x01B3 | 充电温度过低二级报警恢复值 | Chg UT Level 2 Alarm Recovery | Chg_UT_lvl2_alarm_recovery | [5 empty] | [-400~1400] | 0.1 | ℃ | R/W | S16 |  |  | BAU, BCU[1] | 0x6032
0x014D | SOC过低二级报警 | Low SOC Level 2 Alarm | Low_SOC_lvl2_alarm | [5 empty] | [0~100] |  | % | R/W | U16 |  |  | BAU, BCU[1] | 0x6033
0x018D | SOC过低二级报警恢复值 | Low SOC Level 2 Alarm Recovery | Low_SOC_lvl2_alarm_recovery | [5 empty] | [0~100] |  | % | R/W | U16 |  |  | BAU, BCU[1] | 0x6034
0x0176 | 极柱温度过高二级报警 | Term OT Level 2 Alarm | Term_OT_lvl2_alarm | [5 empty] | [-400~1400] | 0.1 | ℃ | R/W | S16 |  |  | BAU, BCU[1] | 0x6035
0x01B6 | 极柱温度过高二级报警恢复值 | Term OT Level 2 Alarm Recovery | Term_OT_lvl2_alarm_recovery | [5 empty] | [-400~1400] | 0.1 | ℃ | R/W | S16 |  |  | BAU, BCU[1] | 0x6036
0x014A | 绝缘阻值过低二级报警 | Low IR Level 2 Alarm | Low_IR_lvl2_alarm | [5 empty] | [0~65535] |  | Ω/V | R/W | U16 |  |  | BAU, BCU[1] | 0x6037
0x018A | 绝缘阻值过低二级报警恢复值 | Low IR Level 2 Alarm Recovery | Low_IR_lvl2_alarm_recovery | [5 empty] | [0~65535] |  | Ω/V | R/W | U16 |  |  | BAU, BCU[1] | 0x6038
0x0161 | 单体压差过大二级报警 | Cell Volt Diff Level 2 Alarm | Cell_volt_diff_lvl2_alarm | [5 empty] | [-5000~5000] |  | mV | R/W | S16 |  |  | BAU, BCU[1] | 0x6039
0x01A1 | 单体电压过低二级报警恢复值 | Cell UV Level 2 Alarm Recovery | Cell_volt_diff_lvl2_alarm_recovery | [5 empty] | [-5000~5000] |  | mV | R/W | S16 |  |  | BAU, BCU[1] | 0x603A
0x0147 | 簇总压校验差过大二级报警 | Rack Volt Calibration Level 2 Alarm | Vrack_cal_diff_lvl2_alarm | [5 empty] | [-32767~32767] | 0.1 | V | R/W | S16 |  |  | BAU, BCU[1] | 0x603B
0x0187 | 簇总压校验差过大二级报警恢复值 | Rack Volt Calibration Level 2 Alarm Recovery | Vrack_cal_diff_lvl2_alarm_recovery | [5 empty] | [-32767~32767] | 0.1 | V | R/W | S16 |  |  | BAU, BCU[1] | 0x603C
0x0164 | 单体温度过高二级报警 | Cell OT Level 2 Alarm | Cell_OT_lvl2_alarm | [5 empty] | [-400~1400] | 0.1 | ℃ | R/W | S16 |  |  | BAU, BCU[1] | 0x603D
0x01A4 | 单体温度过高二级报警恢复值 | Cell OT Level 2 Alarm Recovery | Cell_OT_lvl2_alarm_recovery | [5 empty] | [-400~1400] | 0.1 | ℃ | R/W | S16 |  |  | BAU, BCU[1] | 0x603E
0x0167 | 单体温度过低二级报警 | Cell UT Level 2 Alarm | Cell_UT_lvl2_alarm | [5 empty] | [-400~1400] | 0.1 | ℃ | R/W | S16 |  |  | BAU, BCU[1] | 0x603F
0x01A7 | 单体温度过低二级报警恢复值 | Cell UT Level 2 Alarm Recovery | Cell_UT_lvl2_alarm_recovery | [5 empty] | [-400~1400] | 0.1 | ℃ | R/W | S16 |  |  | BAU, BCU[1] | 0x6040
0x016A | 单体温差过大二级报警 | Cell Temp Diff Level 2 Alarm | Cell_temp_diff_lvl2_alarm | [5 empty] | [-400~1400] | 0.1 | ℃ | R/W | S16 |  |  | BAU, BCU[1] | 0x6041
0x01AA | 单体温差过大二级报警恢复值 | Cell Temp Diff Level 2 Alarm Recovery | Cell_temp_diff_lvl2_alarm_recovery | [5 empty] | [-400~1400] | 0.1 | ℃ | R/W | S16 |  |  | BAU, BCU[1] | 0x6042
0x0156 | 高压箱温度过高二级报警 | PDU OT Level 2 Alarm | PDU_OT_lvl2_alarm | [5 empty] | [-400~1400] | 0.1 | ℃ | R/W | S16 |  |  | BAU, BCU[1] | 0x6043
0x0196 | 高压箱温度过高二级报警恢复值 | PDU OT Level 2 Alarm Recovery | PDU_OT_lvl2_alarm_recovery | [5 empty] | [-400~1400] | 0.1 | ℃ | R/W | S16 |  |  | BAU, BCU[1] | 0x6044
0x0158 | 单体电压过高一级报警 | Cell OV Level 1 Alarm | Cell_OV_lvl1_alarm | [5 empty] | [-5000~5000] |  | mV | R/W | S16 |  |  | BAU, BCU[1] | 0x6045
0x0198 | 单体电压过高一级报警恢复值 | Cell OV Level 1 Alarm Recovery | Cell_OV_lvl1_alarm_recovery | [5 empty] | [-5000~5000] |  | mV | R/W | S16 |  |  | BAU, BCU[1] | 0x6046
0x015C | 单体电压过低一级报警 | Cell UV Level 1 Alarm | Cell_UV_lvl1_alarm | [5 empty] | [-5000~5000] |  | mV | R/W | S16 |  |  | BAU, BCU[1] | 0x6047
0x019C | 单体电压过高三级报警恢复值 | Cell OV Level 3 Alarm Recovery | Cell_UV_lvl1_alarm_recovery | [5 empty] | [-5000~5000] |  | mV | R/W | S16 |  |  | BAU, BCU[1] | 0x6048
0x0140 | 簇总压过高一级报警 | Rack OV Level 1 Alarm | Rack_OV_lvl1_alarm | [5 empty] | [-32767~32767] | 0.1 | V | R/W | S16 |  |  | BAU, BCU[1] | 0x6049
0x0180 | 簇总压过高一级报警恢复值 | Rack OV Level 1 Alarm Recovery | Rack_OV_lvl1_alarm_recovery | [5 empty] | [-32767~32767] | 0.1 | V | R/W | S16 |  |  | BAU, BCU[1] | 0x604A
0x0143 | 簇总压过低一级报警 | Rack UV Level 1 Alarm | Rack_UV_lvl1_alarm | [5 empty] | [-32767~32767] | 0.1 | V | R/W | S16 |  |  | BAU, BCU[1] | 0x604B
0x0183 | 簇总压过低一级报警恢复值 | Rack UV Level 1 Alarm Recovery | Rack_UV_lvl1_alarm_recovery | [5 empty] | [-32767~32767] | 0.1 | V | R/W | S16 |  |  | BAU, BCU[1] | 0x604C
0x017B | 充电电流过大一级报警 | Chg OC Level 1 Alarm | Chg_OC_lvl1_alarm | [5 empty] | [-32767~32767] | 0.1 | A | R/W | S16 |  |  | BAU, BCU[1] | 0x604D
0x01BB | 充电电流过大一级报警恢复值 | Chg OC Level 1 Alarm Recovery | Chg_OC_lvl1_alarm_recovery | [5 empty] | [-32767~32767] | 0.1 | A | R/W | S16 |  |  | BAU, BCU[1] | 0x604E
0x0178 | 放电电流过大一级报警 | Dsg OC Level 1 Alarm | Dsg_OC_lvl1_alarm | [5 empty] | [-32767~32767] | 0.1 | A | R/W | S16 |  |  | BAU, BCU[1] | 0x604F
0x01B8 | 放电电流过大一级报警恢复值 | Dsg OC Level 1 Alarm Recovery | Dsg_OC_lvl1_alarm_recovery | [5 empty] | [-32767~32767] | 0.1 | A | R/W | S16 |  |  | BAU, BCU[1] | 0x6050
0x016F | 充电温度过高一级报警 | Chg OT Level 1 Alarm | Chg_OT_lvl1_alarm | [5 empty] | [-400~1400] | 0.1 | ℃ | R/W | S16 |  |  | BAU, BCU[1] | 0x6051
0x01AF | 充电温度过高一级报警恢复值 | Chg OT Level 1 Alarm Recovery | Chg_OT_lvl1_alarm_recovery | [5 empty] | [-400~1400] | 0.1 | ℃ | R/W | S16 |  |  | BAU, BCU[1] | 0x6052
0x0172 | 充电温度过低一级报警 | Chg UT Level 1 Alarm | Chg_UT_lvl1_alarm | [5 empty] | [-400~1400] | 0.1 | ℃ | R/W | S16 |  |  | BAU, BCU[1] | 0x6053
0x01B2 | 充电温度过低一级报警恢复值 | Chg UT Level 1 Alarm Recovery | Chg_UT_lvl1_alarm_recovery | [5 empty] | [-400~1400] | 0.1 | ℃ | R/W | S16 |  |  | BAU, BCU[1] | 0x6054
0x014C | SOC过低一级报警 | Low SOC Level 1 Alarm | Low_SOC_lvl1_alarm | [5 empty] | [0~100] |  | % | R/W | U16 |  |  | BAU, BCU[1] | 0x6055
0x018C | SOC过低一级报警恢复值 | Low SOC Level 1 Alarm Recovery | Low_SOC_lvl1_alarm_recovery | [5 empty] | [0~100] |  | % | R/W | U16 |  |  | BAU, BCU[1] | 0x6056
0x0175 | 极柱温度过高一级报警 | Term OT Level 1 Alarm | Term_OT_lvl1_alarm | [5 empty] | [-400~1400] | 0.1 | ℃ | R/W | S16 |  |  | BAU, BCU[1] | 0x6057
0x01B5 | 极柱温度过高一级报警恢复值 | Term OT Level 1 Alarm Recovery | Term_OT_lvl1_alarm_recovery | [5 empty] | [-400~1400] | 0.1 | ℃ | R/W | S16 |  |  | BAU, BCU[1] | 0x6058
0x0149 | 绝缘阻值过低一级报警 | Low IR Level 1 Alarm | Low_IR_lvl1_alarm | [5 empty] | [0~65535] |  | Ω/V | R/W | U16 |  |  | BAU, BCU[1] | 0x6059
0x0189 | 绝缘阻值过低一级报警恢复值 | Low IR Level 1 Alarm Recovery | Low_IR_lvl1_alarm_recovery | [5 empty] | [0~65535] |  | Ω/V | R/W | U16 |  |  | BAU, BCU[1] | 0x605A
0x0160 | 单体压差过大一级报警 | Cell Volt Diff Level 1 Alarm | Cell_volt_diff_lvl1_alarm | [5 empty] | [-5000~5000] |  | mV | R/W | S16 |  |  | BAU, BCU[1] | 0x605B
0x01A0 | 单体电压过低一级报警恢复值 | Cell UV Level 1 Alarm Recovery | Cell_volt_diff_lvl1_alarm_recovery | [5 empty] | [-5000~5000] |  | mV | R/W | S16 |  |  | BAU, BCU[1] | 0x605C
0x0146 | 簇总压校验差过大一级报警 | Rack Volt Calibration Level 1 Alarm | Vrack_cal_diff_lvl1_alarm | [5 empty] | [-32767~32767] | 0.1 | V | R/W | S16 |  |  | BAU, BCU[1] | 0x605D
0x0186 | 簇总压校验差过大一级报警恢复值 | Rack Volt Calibration Level 1 Alarm Recovery | Vrack_cal_diff_lvl1_alarm_recovery | [5 empty] | [-32767~32767] | 0.1 | V | R/W | S16 |  |  | BAU, BCU[1] | 0x605E
0x0163 | 单体温度过高一级报警 | Cell OT Level 1 Alarm | Cell_OT_lvl1_alarm | [5 empty] | [-400~1400] | 0.1 | ℃ | R/W | S16 |  |  | BAU, BCU[1] | 0x605F
0x01A3 | 单体温度过高一级报警恢复值 | Cell OT Level 1 Alarm Recovery | Cell_OT_lvl1_alarm_recovery | [5 empty] | [-400~1400] | 0.1 | ℃ | R/W | S16 |  |  | BAU, BCU[1] | 0x6060
0x0166 | 单体温度过低一级报警 | Cell UT Level 1 Alarm | Cell_UT_lvl1_alarm | [5 empty] | [-400~1400] | 0.1 | ℃ | R/W | S16 |  |  | BAU, BCU[1] | 0x6061
0x01A6 | 单体温度过低一级报警恢复值 | Cell UT Level 1 Alarm Recovery | Cell_UT_lvl1_alarm_recovery | [5 empty] | [-400~1400] | 0.1 | ℃ | R/W | S16 |  |  | BAU, BCU[1] | 0x6062
0x0169 | 单体温差过大一级报警 | Cell Temp Diff Level 1 Alarm | Cell_temp_diff_lvl1_alarm | [5 empty] | [-400~1400] | 0.1 | ℃ | R/W | S16 |  |  | BAU, BCU[1] | 0x6063
0x01A9 | 单体温差过大一级报警恢复值 | Cell Temp Diff Level 1 Alarm Recovery | Cell_temp_diff_lvl1_alarm_recovery | [5 empty] | [-400~1400] | 0.1 | ℃ | R/W | S16 |  |  | BAU, BCU[1] | 0x6064
0x0155 | 高压箱温度过高一级报警 | PDU OT Level 1 Alarm | PDU_OT_lvl1_alarm | [5 empty] | [-400~1400] | 0.1 | ℃ | R/W | S16 |  |  | BAU, BCU[1] | 0x6065
0x0195 | 高压箱温度过高一级报警恢复值 | PDU OT Level 1 Alarm Recovery | PDU_OT_lvl1_alarm_recovery | [5 empty] | [-400~1400] | 0.1 | ℃ | R/W | S16 |  |  | BAU, BCU[1] | 0x6066
0x0A89 | Pack压差过大一级报警 | Pack Voltage Difference Level 1 Alarm | lv1_module_vol_differ_hi_alm_throld | [5 empty] | [-32768~32768] | 0.1 | V | R | S16 |  |  | BAU, BCU[1] | 0x6067
0x0A8A | Pack压差过大二级报警 | Pack Voltage Difference Level 2 Alarm | lv2_module_vol_differ_hi_alm_throld | [5 empty] | [-32768~32768] | 0.1 | V | R | S16 |  |  | BAU, BCU[1] | 0x6068
0x0A8B | Pack压差过大三级报警 | Pack Voltage Difference Level 3 Alarm | lv3_module_vol_differ_hi_alm_throld | [5 empty] | [0~600] | 0.1 | V | R | S16 |  |  | BAU, BCU[1] | 0x6069
0x0A8C | Pack压差过大报警一级恢复值 | Pack Voltage Difference Level 1 Alarm Recovery | lv1_module_vol_differ_hi_alm_reco | [5 empty] | [-32768~32768] | 0.1 | V | R | S16 |  |  | BAU, BCU[1] | 0x606A
0x0A8D | Pack压差过大报警二级恢复值 | Pack Voltage Difference Level 2 Alarm Recovery | lv2_module_vol_differ_hi_alm_reco | [5 empty] | [-32768~32768] | 0.1 | V | R | S16 |  |  | BAU, BCU[1] | 0x606B
0x0A8E | Pack压差过大报警三级恢复值 | Pack Voltage Difference Level 3 Alarm Recovery | lv3_module_vol_differ_hi_alm_reco | [5 empty] | [-32768~32768] | 0.1 | V | R | S16 |  |  | BAU, BCU[1] | 0x606C
0x1110 | 铜排温度过高一级报警 | Busbar OT Level 1 Alarm | Copper_OT_lvl1_Alarm_Trigger | [5 empty] | [-400~1400] | 0.1 | ℃ | R/W | S16 |  |  | BAU, BCU[1] | 0x606D
0x1111 | 铜排温度过高二级报警 | Busbar OT Level 2 Alarm | Copper_OT_lvl2_Alarm_Trigger | [5 empty] | [-400~1400] | 0.1 | ℃ | R/W | S16 |  |  | BAU, BCU[1] | 0x606E
0x1112 | 铜排温度过高三级报警 | Busbar OT Level 3 Alarm | Copper_OT_lvl3_Alarm_Trigger | [5 empty] | [-400~1400] | 0.1 | ℃ | R/W | S16 |  |  | BAU, BCU[1] | 0x606F
0x1190 | 铜排温度过高一级恢复值 | Busbar OT Level 1 Alarm Recovery | Copper_OT_lvl1_Alarm_Recovery | [5 empty] | [-400~1400] | 0.1 | ℃ | R/W | S16 |  |  | BAU, BCU[1] | 0x6070
0x1191 | 铜排温度过高二级恢复值 | Busbar OT Level 2 Alarm Recovery | Copper_OT_lvl2_Alarm_Recovery | [5 empty] | [-400~1400] | 0.1 | ℃ | R/W | S16 |  |  | BAU, BCU[1] | 0x6071
0x1192 | 铜排温度过高三级恢复值 | Busbar OT Level 3 Alarm Recovery | Copper_OT_lvl3_Alarm_Recovery | [5 empty] | [-400~1400] | 0.1 | ℃ | R/W | S16 |  |  | BAU, BCU[1] | 0x6072
0x1113 | 充电单体压差过大一级报警 | Chg Cell Volt Diff Level 1 Alarm | Chg_cell_volt_lvl1_alarm_trigger | [5 empty] | [-5000~5000] | 1 | mV | R/W | S16 |  |  | BAU, BCU[1] | 0x6073
0x1114 | 充电单体压差过大二级报警 | Chg Cell Volt Diff Level 2 Alarm | Chg_cell_volt_lvl2_alarm_trigger | [5 empty] | [-5000~5000] | 1 | mV | R/W | S16 |  |  | BAU, BCU[1] | 0x6074
0x1115 | 充电单体压差过大三级报警 | Chg Cell Volt Diff Level 3 Alarm | Chg_cell_volt_lvl3_alarm_trigger | [5 empty] | [-5000~5000] | 1 | mV | R/W | S16 |  |  | BAU, BCU[1] | 0x6075
0x1193 | 充电单体压差过大一级恢复值 | Chg Cell Volt Diff Level 1 Alarm Recovery | Chg_cell_volt_lvl1_alarm_recovery | [5 empty] | [-5000~5000] | 1 | mV | R/W | S16 |  |  | BAU, BCU[1] | 0x6076
0x1194 | 充电单体压差过大二级恢复值 | Chg Cell Volt Diff Level 2 Alarm Recovery | Chg_cell_volt_lvl2_alarm_recovery | [5 empty] | [-5000~5000] | 1 | mV | R/W | S16 |  |  | BAU, BCU[1] | 0x6077
0x1195 | 充电单体压差过大三级恢复值 | Chg Cell Volt Diff Level 3 Alarm Recovery | Chg_cell_volt_lvl3_alarm_recovery | [5 empty] | [-5000~5000] | 1 | mV | R/W | S16 |  |  | BAU, BCU[1] | 0x6078
0x1117 | 充电单体温差过大一级报警 | Chg Cell Temp Diff Level 1 Alarm | Chg_cell_temp_lvl1_alarm_trigger | [5 empty] | [-400~1400] | 1 | mV | R/W | S16 |  |  | BAU, BCU[1] | 0x6079
0x1118 | 充电单体温差过大二级报警 | Chg Cell Temp Diff Level 2 Alarm | Chg_cell_temp_lvl2_alarm_trigger | [5 empty] | [-400~1400] | 1 | mV | R/W | S16 |  |  | BAU, BCU[1] | 0x607A
0x1119 | 充电单体温差过大三级报警 | Chg Cell Temp Diff Level 3 Alarm | Chg_cell_temp_lvl3_alarm_trigger | [5 empty] | [-400~1400] | 1 | mV | R/W | S16 |  |  | BAU, BCU[1] | 0x607B
0x1197 | 充电单体温差过大一级恢复值 | Chg Cell Temp Diff Level 1 Alarm Recovery | Chg_cell_temp_lvl1_alarm_recovery | [5 empty] | [-400~1400] | 1 | mV | R/W | S16 |  |  | BAU, BCU[1] | 0x607C
0x1198 | 充电单体温差过大二级恢复值 | Chg Cell Temp Diff Level 2 Alarm Recovery | Chg_cell_temp_lvl2_alarm_recovery | [5 empty] | [-400~1400] | 1 | mV | R/W | S16 |  |  | BAU, BCU[1] | 0x607D
0x1199 | 充电单体温差过大三级恢复值 | Chg Cell Temp Diff Level 3 Alarm Recovery | Chg_cell_temp_lvl3_alarm_recovery | [5 empty] | [-400~1400] | 1 | mV | R/W | S16 |  |  | BAU, BCU[1] | 0x607E
| 预留 | reserve100 | reserve100 | [8 empty] | R | U16 |  |  | BAU, BCU[1] | 0x607F
0x0023 | 总控时间 | BAU Sync Time | BAU_sync_time_h16b | [5 empty] | [0~65535] | 100 | ms | R/W | U32 |  |  | BCU/EMS | 0x6080
0x0067 | 预充结束压差 | Pre-Charge End Volt Diff | Pre_Chg_end_volt_diff | [5 empty] | [-32767~32767] | 0.1 | V | R/W | S16 |  |  | BCU/EMS | 0x6082
0x007D | 风扇开启温度 | Pack Fan ON Temp | IO1_auto_distribute_wrong_ID | [5 empty] | [-400~1400] | 0.1 | ℃ | R/W | S16 |  |  | BCU/EMS | 0x6083
0x007E | 风扇关闭温度 | Pack Fan OFF Temp | fan_stop_temp | [5 empty] | [-400~1400] | 0.1 | ℃ | R/W | S16 |  |  | BCU/EMS | 0x6084
0x0A5F | IP第四个字节 | Last Byte of IP | last_byte_of_IP | [5 empty] | [0~255] |  |  | R/W | S16 |  | 由于与堆编号和IP偏移机制冲突，默认不开启该功能，软件中开启配置后，堆编号与IP偏移的配置不生效 | BCU/EMS | 0x6085
0x0A6E | IP第三个字节 | 3rd Byte of IP | 3rd_byte_of_IP | [5 empty] | [0~255] |  |  | R/W | U16 |  |  | BCU/EMS | 0x6086
0x0A6F | IP第二个字节 | 2nd Byte of IP | 2nd_byte_of_IP | [5 empty] | [0~255] |  |  | R/W | U16 |  |  | BCU/EMS | 0x6087
0x0A70 | IP第一个字节 | 1st Byte of IP | 1st_byte_of_IP | [5 empty] | [0~255] |  |  | R/W | U16 |  |  | BCU/EMS | 0x6088
0x0A71 | 网关第一个字节 | 1st Byte of Gateway | 1st_byte_of_gateway | [5 empty] | [0~255] |  |  | R/W | U16 |  |  | BCU/EMS | 0x6089
0x0A72 | 网关第二个字节 | 2nd Byte of Gateway | 2nd_byte_of_gateway | [5 empty] | [0~255] |  |  | R/W | U16 |  |  | BCU/EMS | 0x608A
0x0A73 | 网关第三个字节 | 3rd Byte of Gateway | 3rd_byte_of_gateway | [5 empty] | [0~255] |  |  | R/W | U16 |  |  | BCU/EMS | 0x608B
0x0A74 | 网关第四个字节 | 4th Byte of Gateway | 4th_byte_of_gateway | [5 empty] | [0~255] |  |  | R/W | U16 |  |  | BCU/EMS | 0x608C
0x0A75 | 子网掩码第一个字节 | 1st Byte of Subnetmask | 1st_byte_of_subnetmask | [5 empty] | [0~255] |  |  | R/W | U16 |  |  | BCU/EMS | 0x608D
0x0A76 | 子网掩码第二个字节 | 2nd Byte of Subnetmask | 2nd_byte_of_subnetmask | [5 empty] | [0~255] |  |  | R/W | U16 |  |  | BCU/EMS | 0x608E
0x0A77 | 子网掩码第三个字节 | 3rd Byte of Subnetmask | 3rd_byte_of_subnetmask | [5 empty] | [0~255] |  |  | R/W | U16 |  |  | BCU/EMS | 0x608F
0x0A78 | 子网掩码第四个字节 | 4th Byte of Subnetmask | 4th_byte_of_subnetmask | [5 empty] | [0~255] |  |  | R/W | U16 |  |  | BCU/EMS | 0x6090
0x111B | 充电Pack压差过大一级报警 | Chg Module Volt Diff Level 1 Alarm | Chg_module_volt_lvl1_alarm_tigger | [5 empty] | [-32767~32767] | 0.1 | V | R/W | S16 |  |  | BAU, BCU[1] | 0x6091
0x111C | 充电Pack压差过大二级报警 | Chg Module Volt Diff Level 2 Alarm | Chg_module_volt_lvl2_alarm_tigger | [5 empty] | [-32767~32767] | 0.1 | V | R/W | S16 |  |  | BAU, BCU[1] | 0x6092
0x111D | 充电Pack压差过大三级报警 | Chg Module Volt Diff Level 3 Alarm | Chg_module_volt_lvl3_alarm_tigger | [5 empty] | [-32767~32767] | 0.1 | V | R/W | S16 |  |  | BAU, BCU[1] | 0x6093
0x119B | 充电Pack压差过大一级恢复值 | Chg Module Volt Diff Level 1 Alarm Recovery | Chg_module_volt_lvl1_alarm_recovery | [5 empty] | [-32767~32767] | 0.1 | V | R/W | S16 |  |  | BAU, BCU[1] | 0x6094
0x119C | 充电Pack压差过大二级恢复值 | Chg Module Volt Diff Level 2 Alarm Recovery | Chg_module_volt_lvl2_alarm_recovery | [5 empty] | [-32767~32767] | 0.1 | V | R/W | S16 |  |  | BAU, BCU[1] | 0x6095
0x119D | 充电Pack压差过大三级恢复值 | Chg Module Volt Diff Level 3 Alarm Recovery | Chg_module_volt_lvl3_alarm_recovery | [5 empty] | [-32767~32767] | 0.1 | V | R/W | S16 |  |  | BAU, BCU[1] | 0x6096
0x111F | 放电单体压差过大一级报警 | Dsg Cell Volt Diff Level 1 Alarm | Dsg_cell_volt_lvl1_alarm_trigger | [5 empty] | [-5000~5000] | 1 | mV | R/W | S16 |  |  | BAU, BCU[1] | 0x6097
0x1120 | 放电单体压差过大二级报警 | Dsg Cell Volt Diff Level 2 Alarm | Dsg_cell_volt_lvl2_alarm_trigger | [5 empty] | [-5000~5000] | 1 | mV | R/W | S16 |  |  | BAU, BCU[1] | 0x6098
0x1121 | 放电单体压差过大三级报警 | Dsg Cell Volt Diff Level 3 Alarm | Dsg_cell_volt_lvl3_alarm_trigger | [5 empty] | [-5000~5000] | 1 | mV | R/W | S16 |  |  | BAU, BCU[1] | 0x6099
0x119F | 放电单体压差过大一级恢复值 | Dsg Cell Volt Diff Level 1 Alarm Recovery | Dsg_cell_volt_lvl1_alarm_recovery | [5 empty] | [-5000~5000] | 1 | mV | R/W | S16 |  |  | BAU, BCU[1] | 0x609A
0x11A0 | 放电单体压差过大二级恢复值 | Dsg Cell Volt Diff Level 2 Alarm Recovery | Dsg_cell_volt_lvl2_alarm_recovery | [5 empty] | [-5000~5000] | 1 | mV | R/W | S16 |  |  | BAU, BCU[1] | 0x609B
0x11A1 | 放电单体压差过大三级恢复值 | Dsg Cell Volt Diff Level 3 Alarm Recovery | Dsg_cell_volt_lvl3_alarm_recovery | [5 empty] | [-5000~5000] | 1 | mV | R/W | S16 |  |  | BAU, BCU[1] | 0x609C
0x1123 | 放电单体温差过大一级报警 | Dsg Cell Temp Diff Level 1 Alarm | Dsg_cell_temp_lvl1_alarm_trigger | [5 empty] | [-400~1400] | 1 | mV | R/W | S16 |  |  | BAU, BCU[1] | 0x609D
0x1124 | 放电单体温差过大二级报警 | Dsg Cell Temp Diff Level 2 Alarm | Dsg_cell_temp_lvl2_alarm_trigger | [5 empty] | [-400~1400] | 1 | mV | R/W | S16 |  |  | BAU, BCU[1] | 0x609E
0x1125 | 放电单体温差过大三级报警 | Dsg Cell Temp Diff Level 3 Alarm | Dsg_cell_temp_lvl3_alarm_trigger | [5 empty] | [-400~1400] | 1 | mV | R/W | S16 |  |  | BAU, BCU[1] | 0x609F
0x11A3 | 放电单体温差过大一级恢复值 | Dsg Cell Temp Diff Level 1 Alarm Recovery | Dsg_cell_temp_lvl1_alarm_recovery | [5 empty] | [-400~1400] | 1 | mV | R/W | S16 |  |  | BAU, BCU[1] | 0x60A0
0x11A4 | 放电单体温差过大二级恢复值 | Dsg Cell Temp Diff Level 2 Alarm Recovery | Dsg_cell_temp_lvl2_alarm_recovery | [5 empty] | [-400~1400] | 1 | mV | R/W | S16 |  |  | BAU, BCU[1] | 0x60A1
0x11A5 | 放电单体温差过大三级恢复值 | Dsg Cell Temp Diff Level 3 Alarm Recovery | Dsg_cell_temp_lvl3_alarm_recovery | [5 empty] | [-400~1400] | 1 | mV | R/W | S16 |  |  | BAU, BCU[1] | 0x60A2
0x1127 | 放电Pack压差过大一级报警 | Dsg Module Volt Diff Level 1 Alarm | Dsg_module_volt_lvl1_alarm_tigger | [5 empty] | [-32767~32767] | 0.1 | V | R/W | S16 |  |  | BAU, BCU[1] | 0x60A3
0x1128 | 放电Pack压差过大二级报警 | Dsg Module Volt Diff Level 2 Alarm | Dsg_module_volt_lvl2_alarm_tigger | [5 empty] | [-32767~32767] | 0.1 | V | R/W | S16 |  |  | BAU, BCU[1] | 0x60A4
0x1129 | 放电Pack压差过大三级报警 | Dsg Module Volt Diff Level 3 Alarm | Dsg_module_volt_lvl3_alarm_tigger | [5 empty] | [-32767~32767] | 0.1 | V | R/W | S16 |  |  | BAU, BCU[1] | 0x60A5
0x11A7 | 放电Pack压差过大一级恢复值 | Dsg Module Volt Diff Level 1 Alarm Recovery | Dsg_module_volt_lvl1_alarm_recovery | [5 empty] | [-32767~32767] | 0.1 | V | R/W | S16 |  |  | BAU, BCU[1] | 0x60A6
0x11A8 | 放电Pack压差过大二级恢复值 | Dsg Module Volt Diff Level 2 Alarm Recovery | Dsg_module_volt_lvl2_alarm_recovery | [5 empty] | [-32767~32767] | 0.1 | V | R/W | S16 |  |  | BAU, BCU[1] | 0x60A7
0x11A9 | 放电Pack压差过大三级恢复值 | Dsg Module Volt Diff Level 3 Alarm Recovery | Dsg_module_volt_lvl3_alarm_recovery | [5 empty] | [-32767~32767] | 0.1 | V | R/W | S16 |  |  | BAU, BCU[1] | 0x60A8
0x112B | Pack内温差过大一级报警 | Pack Temp Diff Level 1 Alarm | Pack_temp_diff_lv1_alarm_tigger | [5 empty] | [-400~1400] | 0.1 | ℃ | R/W | S16 |  |  | BAU, BCU[1] | 0x60A9
0x112C | Pack内温差过大二级报警 | Pack Temp Diff Level 2 Alarm | Pack_temp_diff_lv2_alarm_tigger | [5 empty] | [-400~1400] | 0.1 | ℃ | R/W | S16 |  |  | BAU, BCU[1] | 0x60AA
0x112D | Pack内温差过大三级报警 | Pack Temp Diff Level 3 Alarm | Pack_temp_diff_lv3_alarm_tigger | [5 empty] | [-400~1400] | 0.1 | ℃ | R/W | S16 |  |  | BAU, BCU[1] | 0x60AB
0x11AB | Pack内温差过大一级恢复值 | Pack Temp Diff Level 1 Alarm Recovery | Pack_temp_diff_lv1_alarm_recovery | [5 empty] | [-400~1400] | 0.1 | ℃ | R/W | S16 |  |  | BAU, BCU[1] | 0x60AC
0x11AC | Pack内温差过大二级恢复值 | Pack Temp Diff Level 2 Alarm Recovery | Pack_temp_diff_lv2_alarm_recovery | [5 empty] | [-400~1400] | 0.1 | ℃ | R/W | S16 |  |  | BAU, BCU[1] | 0x60AD
0x11AD | Pack内温差过大三级恢复值 | Pack Temp Diff Level 3 Alarm Recovery | Pack_temp_diff_lv3_alarm_recovery | [5 empty] | [-400~1400] | 0.1 | ℃ | R/W | S16 |  |  | BAU, BCU[1] | 0x60AE
0x11AD | Pack内温差过大三级恢复值 | Pack Temp Diff Level 3 Alarm Recovery | Pack_temp_diff_lv3_alarm_recovery | [5 empty] | [-400~1400] | 0.1 | ℃ | R/W | S16 |  |  | BAU, BCU[1] | 0x60AE

## Rack_Alarm_lv4_Para Set& Read
RACK Alarm Parameter Threshold Set & Read
Register type: Rack参数设置(保持寄存器, 每Rack Modbus地址独立,从2开始,功能码:0x10或0x06); Rack Parameter Settings (Holding Registers Modbus Addr:each rack independent,from 2 Function Code:0x10 or 0x06)
Modbus Addr: 2 to N+1 (N is rack number)
偏移地址 | 配置项中文名 | 配置项英文名 | 英文key | 中文使用说明 | 英文使用说明 | 英文子key | 说明(值/枚举说明) | 说明(值/枚举说明)(英文) | 范围 | 单位系数 | 单位 | 是否可写 | 数值格式 | 个数 | 备注 | 数据源 | Modbus地址
0x1100 | 簇总压过高截止 | Rack OV Tip Trigger | Rack_OV_Tip_Trigger | [5 empty] | [-32767~32767] | 0.1 | V | R/W | S16 |  |  | BAU, BCU[1] | 0x6101
0x1101 | 簇总压过低截止 | Rack UV Tip Trigger | Rack_UV_Tip_Trigger | [5 empty] | [-32767~32767] | 0.1 | V | R/W | S16 |  |  | BAU, BCU[1] | 0x6102
| 预留 | reserve110 | reserve110 | [8 empty] | R/W | S16 |  |  | BAU, BCU[1] | 0x6103
0x1103 | 单体电压过高截止 | Cell OV Tip Trigger | Cell_OV_Tip_Trigger | [5 empty] | [-5000~5000] | 1 | mV | R/W | S16 |  |  | BAU, BCU[1] | 0x6104
0x1104 | 单体电压过低截止 | Cell UV Tip Trigger | Cell_UV_Tip_Trigger | [5 empty] | [-5000~5000] | 1 | mV | R/W | S16 |  |  | BAU, BCU[1] | 0x6105
0x1105 | 单体压差过大截止 | Cell Volt Diff Tip Trigger | Cell_Volt_Diff_Tip_Trigger | [5 empty] | [-5000~5000] | 1 | mV | R/W | S16 |  |  | BAU, BCU[1] | 0x6106
0x1106 | 放电温度过高截止 | Dsg OT Tip Trigger | Dsg_OT_Tip_Trigger | [5 empty] | [-400~1400] | 0.1 | ℃ | R/W | S16 |  |  | BAU, BCU[1] | 0x6107
0x1107 | 放电温度过低截止 | Dsg UT Tip Trigger | Dsg_UT_Tip_Trigger | [5 empty] | [-400~1400] | 0.1 | ℃ | R/W | S16 |  |  | BAU, BCU[1] | 0x6108
0x1108 | 温差过大截止 | Cell Temp Diff Tip Trigger | Cell_Temp_Diff_Tip_Trigger | [5 empty] | [-400~1400] | 0.1 | ℃ | R/W | S16 |  |  | BAU, BCU[1] | 0x6109
0x1109 | 充电温度过高截止 | Chg OT Tip Trigger | Chg_OT_Tip_Trigger | [5 empty] | [-400~1400] | 0.1 | ℃ | R/W | S16 |  |  | BAU, BCU[1] | 0x610A
0x110A | 充电温度过低截止 | Chg UT Tip Trigger | Chg_UT_Tip_Trigger | [5 empty] | [-400~1400] | 0.1 | ℃ | R/W | S16 |  |  | BAU, BCU[1] | 0x610B
0x110B | 放电电流过大截止 | Chg OC Tip Trigger | Chg_OC_Tip_Trigger | [5 empty] | [-32767~32767] | 0.1 | A | R/W | S16 |  |  | BAU, BCU[1] | 0x610C
0x110C | 充电电流过大截止 | Dsg OC Tip Trigger | Dsg_OC_Tip_Trigger | [5 empty] | [-32767~32767] | 0.1 | A | R/W | S16 |  |  | BAU, BCU[1] | 0x610D
0x110D | Pack电压过高截止 | Pack OV Tip Trigger | Pack_OV_Tip_Trigger | [5 empty] | [-32767~32767] | 0.1 | V | R/W | S16 |  |  | BAU, BCU[1] | 0x610E
0x110E | Pack电压过低截止 | Pack UV Tip Trigger | Pack_UV_Tip_Trigger | [5 empty] | [-32767~32767] | 0.1 | V | R/W | S16 |  |  | BAU, BCU[1] | 0x610F
0x110F | Pack压差过大截止 | Pack Volt Diff Tip Trigger | Pack_Volt_Diff_Tip_Trigger | [5 empty] | [-32767~32767] | 0.1 | V | R/W | S16 |  |  | BAU, BCU[1] | 0x6110
0x1116 | 充电单体压差过大截止 | Chg Cell Volt Diff Tip Trigger | Chg_cell_volt_tip_trigger | [5 empty] | [-5000~5000] | 1 | mV | R/W | S16 |  |  | BAU, BCU[1] | 0x6111
0x111A | 充电单体温差过大截止 | Chg Cell Temp Diff Tip Trigger | Chg_cell_temp_tip_trigger | [5 empty] | [-400~1400] | 0.1 | ℃ | R/W | S16 |  |  | BAU, BCU[1] | 0x6112
0x111E | 充电Pack压差过大截止 | Chg Module Volt Diff Tip Trigger | Chg_module_volt_tip_trigger | [5 empty] | [-32767~32767] | 0.1 | V | R/W | S16 |  |  | BAU, BCU[1] | 0x6113
0x1180 | 簇总压过高截止恢复值 | Rack OV Notify Recovery | Rack_OV_Tip_Recovery | [5 empty] | [-32767~32767] | 0.1 | V | R/W | S16 |  |  | BAU, BCU[1] | 0x6114
0x1181 | 簇总压过低截止恢复值 | Rack UV Notify Recovery | Rack_UV_Tip_Recovery | [5 empty] | [-32767~32767] | 0.1 | V | R/W | S16 |  |  | BAU, BCU[1] | 0x6115
| 预留 | Reserved114 | reserve114 | [8 empty] | R/W | S16 |  |  | BAU, BCU[1] | 0x6116
0x1183 | 单体电压过高截止恢复值 | Cell OV Notify Recovery | Cell_OV_Tip_Recovery | [5 empty] | [-5000~5000] | 1 | mV | R/W | S16 |  |  | BAU, BCU[1] | 0x6117
0x1184 | 单体电压过低截止恢复值 | Cell UV Notify Recovery | Cell_UV_Tip_Recovery | [5 empty] | [-5000~5000] | 1 | mV | R/W | S16 |  |  | BAU, BCU[1] | 0x6118
0x1185 | 单体压差过大截止恢复值 | Cell Volt Diff Notify Recovery | Cell_Volt_Diff_Tip_Recovery | [8 empty] | R/W | S16 |  |  | BAU, BCU[1] | 0x6119
0x1186 | 放电温度过高截止恢复值 | Dsg OT Notify Recovery | Dsg_OT_Tip_Recovery | [5 empty] | [-400~1400] | 0.1 | ℃ | R/W | S16 |  |  | BAU, BCU[1] | 0x611A
0x1187 | 放电温度过低截止恢复值 | Dsg UT Notify Recovery | Dsg_UT_Tip_Recovery | [5 empty] | [-400~1400] | 0.1 | ℃ | R/W | S16 |  |  | BAU, BCU[1] | 0x611B
0x1188 | 温差过大截止恢复值 | Cell Temp Diff Notify Recovery | Cell_Temp_Diff_Tip_Recovery | [5 empty] | [-400~1400] | 0.1 | ℃ | R/W | S16 |  |  | BAU, BCU[1] | 0x611C
0x1189 | 充电温度过高截止恢复值 | Chg OT Notify Recovery | Chg_OT_Tip_Recovery | [5 empty] | [-400~1400] | 0.1 | ℃ | R/W | S16 |  |  | BAU, BCU[1] | 0x611D
0x118A | 充电温度过低截止恢复值 | Chg UT Notify Recovery | Chg_UT_Tip_Recovery | [5 empty] | [-400~1400] | 0.1 | ℃ | R/W | S16 |  |  | BAU, BCU[1] | 0x611E
0x118B | 放电电流过大截止恢复值 | Dsg OC Notify Recovery | Chg_OC_Tip_Recovery | [5 empty] | [-32767~32767] | 0.1 | A | R/W | S16 |  |  | BAU, BCU[1] | 0x611F
0x118C | 充电电流过大截止恢复值 | Chg OC Notify Recovery | Dsg_OC_Tip_Recovery | [5 empty] | [-32767~32767] | 0.1 | A | R/W | S16 |  |  | BAU, BCU[1] | 0x6120
0x118D | Pack电压过高截止恢复值 | Pack OV Notify Recovery | Pack_OV_Tip_Recovery | [5 empty] | [-32767~32767] | 0.1 | V | R/W | S16 |  |  | BAU, BCU[1] | 0x6121
0x118E | Pack电压过低截止恢复值 | Pack UV Notify Recovery | Pack_UV_Tip_Recovery | [5 empty] | [-32767~32767] | 0.1 | V | R/W | S16 |  |  | BAU, BCU[1] | 0x6122
0x118F | Pack压差过大截止恢复值 | Pack Volt Diff Notify Recovery | Pack_Volt_Diff_Tip_Recovery | [5 empty] | [-32767~32767] | 0.1 | V | R/W | S16 |  |  | BAU, BCU[1] | 0x6123
0x1196 | 充电单体压差过大截止恢复值 | Chg Cell Volt Diff Notify Recovery | Chg_cell_volt_tip_recovery | [5 empty] | [-5000~5000] | 1 | mV | R/W | S16 |  |  | BAU, BCU[1] | 0x6124
0x119A | 充电单体温差过大截止恢复值 | Chg Cell Temp Diff Notify Recovery | Chg_cell_temp_tip_recovery | [5 empty] | [-400~1400] | 0.1 | ℃ | R/W | S16 |  |  | BAU, BCU[1] | 0x6125
0x119E | 充电Pack压差过大截止恢复值 | Chg Module Volt Diff Notify Recovery | Chg_module_volt_tip_recovery | [5 empty] | [-32767~32767] | 0.1 | V | R/W | S16 |  |  | BAU, BCU[1] | 0x6126
0x1122 | 放电单体压差过大截止 | Dsg Cell Volt Diff Notify | Dsg_cell_volt_tip_trigger | [5 empty] | [-5000~5000] | 1 | mV | R/W | S16 |  |  | BAU, BCU[1] | 0x6127
0x1126 | 放电单体温差过大截止 | Dsg Cell Temp Diff Notify | Dsg_cell_temp_tip_trigger | [5 empty] | [-400~1400] | 0.1 | ℃ | R/W | S16 |  |  | BAU, BCU[1] | 0x6128
0x112A | 放电Pack压差过大截止 | Dsg Module Volt Diff Notify | Dsg_module_volt_tip_trigger | [5 empty] | [-32767~32767] | 0.1 | V | R/W | S16 |  |  | BAU, BCU[1] | 0x6129
0x112E | Pack内温差过大截止 | Pack Temp Diff Notify | Pack_temp_diff_tip_trigger | [5 empty] | [-400~1400] | 0.1 | ℃ | R/W | S16 |  |  | BAU, BCU[1] | 0x612A
| 预留 | Reserved110 | Reserved110 | [8 empty] | R/W | U16 | 79 |  | BAU, BCU[1] | 0x612B
0x11A2 | 放电单体压差过大截止-恢复值 | Dsg Cell Volt Diff Notify Recovery | Dsg_cell_volt_tip_recovery | [5 empty] | [-5000~5000] | 1 | mV | R/W | S16 |  |  | BAU, BCU[1] | 0x617A
0x11A6 | 放电单体温差过大截止恢复值 | Dsg Cell Temp Diff Notify Recovery | Dsg_cell_temp_tip_recovery | [5 empty] | [-400~1400] | 0.1 | ℃ | R/W | S16 |  |  | BAU, BCU[1] | 0x617B
0x11AA | 放电Pack压差过大截止恢复值 | Dsg Module Volt Diff Notify Recovery | Dsg_module_volt_tip_recovery | [5 empty] | [-32767~32767] | 0.1 | V | R/W | S16 |  |  | BAU, BCU[1] | 0x617C
0x11AE | Pack内温差过大截止恢复值 | Pack Temp Diff Notify Recovery | Pack_temp_diff_tip_recovery | [5 empty] | [-400~1400] | 0.1 | ℃ | R/W | S16 |  |  | BAU, BCU[1] | 0x617D